## Slide 1
ERCOT Frequency Control Report
November 2018
ERCOT
Operations Planning
PDCWG | December 17th, 2018

## Slide 2: Summary of November 2018
CPS1: 173.73%
Current CPS1 12-Month Rolling Average: 175.87%
2 BAAL Exceedance
3 hourly CPS1 scores below 100%
BAAL-003 Events have updated through August
2018 BAAL-003 FRM Performance: -895.19
2018 RMS1 Statistics
  Mean: 15.31 mHz
  Min: 12.66 mHz
  Max: 19.18 mHz
Energy Statistics
  Total Energy: 27,042,180 MWh
  Wind Energy: 5,577,203 MWh
  Percent Energy from Wind Generation: 20.62%
Minimum System Inertia
  Mean: 178,025
  Max: 266,848 on November 14th
  Min: 128,759 on November 3rd

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
November-18 CPS1 (%): 173.73
Notes: Outliers:
11/3/18 18:00: 8.9%
Wind ramp down of >500 MW over 15 mins. Frequency was dragging due large expected generation deviation. Reg Up exhausted from 18:01 until 18:39.
11/3/18 21:00: 83.4%
Wind ramp down of >2,500 MW throughout the hour. Frequency was dragging due to wind ramp and large expected generation deviation. Reg Up exhausted from 21:20 until 21:55.
11/14/18 10:00: 90.9%
Small Wind ramp up, load declining through mid day. Frequency was above upper deadband 10:09 to 10:23. Reg Down exhausted from 10:18 until 11:00.

## Slide 5: BAAL Exceedances & Violations
There was 2 BAAL exceedance
  November 3, 2018
    Wind was ramping down quickly
    Unit loss when there was already a large expected generation deviation
    Less than 59.91 Hz for 1 minute

## Slide 6: 15-Minute Average CPS1%
November-18 CPS1 (%): 173.73

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 175.87%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes: Mean is 14.73 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 15.31 mHz
Min: 12.66 mHz
Max: 19.18 mHz

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Frequency Profile Comparison

## Slide 15: Time Error Correction

## Slide 16: ERCOT Daily Time Error

## Slide 17: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 18: BAL-003 Performance

## Slide 19: Op. Year 2018 BAL-003 Selected Events
Maybe. Will be valuated at the end of the year.

## Slide 20: Op. Year 2018 BAL-003 FRM Performance

## Slide 21: ERCOT Energy Statistics

## Slide 22: Total Energy
Notes: 27,042,180 MWh

## Slide 23: Total Energy from Wind Generation
Notes: 5,577,203 MWh

## Slide 24: % Energy from Wind Generation
Notes: 20.62%

## Slide 25: ERCOT System Inertia

## Slide 26: Daily Minimum System Inertia
Notes: Minimum Inertia = 128,759 MW*s on 11/3/2018. Need details here.
Previous Minimum was 130,014 MW*s on 10/27/2017. This was also our record wind day.
November:
Mean: 178,025
Max: 266,848 on November 14th
Min: 128,759 on November 3rd

## Slide 27: Questions?
Thank you!

## Slide 28: Op. Year 2017 BAL-003 Selected Events
Notes: Frequency Bias updated from 764 to 759 in April

## Slide 29: Op. Year 2017 BAL-003 FRM Performance