## Slide 1: System Protection Working Group (SPWG) Update to ROS
January 10, 2019
Genardo T. Corpuz
2018 SPWG Chair

## Slide 2: SPWG Meeting
Meeting held on November 15, 2018
Short Circuit Case building will start in January 18, 2019
  Current Year 2019
  Future Years 2020-2024
Reviewed ERCOT SPWG Procedures
  Revise verbiage to reflect misoperation submittal to NERC

## Slide 3: SPWG Meeting
2019 SPWG Chair:
  Micheal A. Davis, Jr, P.E.
  CenterPoint Energy | Supervising Engineer | Transmission Planning - System Modeling
2019 SPWG Vice-Chair:
  Keith Calle, P.E.
  CPS Energy | Manager | System Protection Engineering

## Slide 4: NERC SPCS Updates
NERC SPCS representatives from ERCOT SPWG attended the meeting on November 13, 2018 in Atlanta, GA
  Glenn Hargrave, CPS
  Armin Klusman, CNP
Implementation Guidance Documents
  PRC-019: Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection)
    Draft in progress, expected completion 1st quarter of 2019
  PRC-024: Generator Frequency and Voltage Protective Relay Settings
    Approved and posted in NERC website

## Slide 5: NERC SPCS Updates
New Standard Authorization Requests (SARs) Being Proposed
  PRC-019
    Update to separate requirements for asynchronous/inverter based generation and synchronous generation
  PRC-023
    Update to remove Requirement R2, “Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability”
  PRC-024-2
    Draft SAR being proposed by Inverter-Based Resource Performance Task Force to address problems with Inverter-Based protection

## Slide 6: Transmission Operator Protection System Misoperations 2018 Q2
ERCOT Protection System Misoperations Data – 138kV and 345kV Combined

## Slide 8: Protection System Misoperations – 2018 Q2
 |  | Q2 | YTD
# of Misoperations | Total | 53 | 96
 | 345 kV | 18 | 32
 | 138 kV | 34 | 62
 | < 100 kV | 1 | 2
By Category | Failure to Trip | 2 | 5
 | Slow Trip | 4 | 4
 | Unnecessary Trip during Fault | 28 | 50
 | Unnecessary Trip – Non Fault | 19 | 37
 | SPS | 0 | 0
By Relay System Type | Electromechanical | 5 | 10
 | Solid State | 2 | 3
 | Microprocessor | 41 | 71
 | Other/ N/A | 5 | 12
By Equipment Protected | Line | 24 | 42
 | Transformer | 5 | 15
 | Generator | 1 | 9
 | Shunt/Series Capacitor | 0 | 0
 | Shunt/Series Reactor | 4 | 5
 | Dynamic VAR system | 0 | 0
 | Bus | 4 | 4
 | Breaker | 14 | 20

## Slide 9: Protection System Misoperations – 2018 Q2

## Slide 10: Protection System Misoperations – 2018 Q2

## Slide 11: Protection System Misoperations – 2018 Q2

## Slide 12: Protection System Misoperations – 2018 Q2

## Slide 13: Protection System Misoperations – 2018 Q2

## Slide 14
Summary of Human Performance Issues in 2018 Q2:
  Generator tripped during start-up. CT shorting screws were left in the CT shorting block after maintenance.
  138kV line overtripped during a fault due to CCVT grounding switch left in the grounded position.
  138kV line overtripped during a fault due to communication fiber pair terminated in the wrong location.
  345kV line overtripped due to miscoordination of settings. Setting changes on the line terminal were not communicated to the remote end owner.
  138kV line overtripped during a fault. Pending relay settings had not been implemented.
  345kV DTT misoperation due to communication cards with different version model numbers installed.
  138kV generator line misoperated due to mismatched L90 firmware versions on the ends of the line.
  138kV line overtriped due to reversed polarity in the current polarizing circuit.
  Capacitor bank fault caused the 138kV bus to trip due to incorrect capacitor bank breaker failure design.
Protection System Misoperations

## Slide 15: Protection System Misoperations
Failure to Trip/Slow Trip Misoperations in 2018 Q2:
  138kV generator breaker slow to trip while taking unit off line. DC ground prevented full DC voltage from being applied to breaker trip coils.
  34.5kV wind plant breaker failed to trip during a fault because 125V DC was not applied to its trip coils.

## Slide 16: Questions ?