## Slide 1
NERC Alert
Momentary Cessation Assessment for Existing Solar Generation Resources
John Schmall
ERCOT Transmission Planning
ROS Meeting
January 10, 2019

## Slide 2: NERC Alert
NERC Alert issued in May 2018 to recommend assessment of potential reliability risks due to adverse characteristics of solar PV resources
  Assess the use and impact of momentary cessation
  Assess model updates to eliminate/reduce momentary cessation
Momentary Cessation
  Inverter does not inject current under voltage conditions where the resource is not allowed to trip (e.g. “no trip” zone specified in Nodal Operating Guide, Section 2.9.1)

## Slide 3: TRE Recommendations
In order to efficiently address NERC Alert (with recommendations addressed to Transmission Planners, Planning Coordinators, Transmission Operators, and Reliability Coordinators):
  ERCOT survey solar resources
  ERCOT assess models and perform studies
  Share results with Transmission Planners and Transmission Operators
    Minimum 5-day comment period (November 16-28, 2018)
  Address all comments and finalize report by December 7, 2018

## Slide 4: NERC Alert Survey Response
ERCOT sent out the survey to 16 solar resources (~1400 MW total) and all 16 resources responded to survey
  Three resources (~200 MW total) indicated the use of momentary cessation
  One resource does not have plans to eliminate momentary cessation
ERCOT staff reviewed models for all 16 solar resources
  Worked with Resource Entities to confirm appropriate model response

## Slide 5: Model Review
Individual model performance tested
  Voltage profiles per ERCOT Nodal Operating Guide, Section 2.9.1
Model adjustments confirmed with Resource Entities as necessary
  Expected response with respect to momentary cessation
  Protection relay model settings
  Specific model parameter tuning
All reviewed models required some adjustment
  Most updates reflect data corrections
  Most updates not directly associated with momentary cessation

## Slide 6: Grid Impact
ERCOT DWG 2020 HWLL case
  All sixteen solar generation projects were modeled at full output
  Applied a nine cycle 3-phase fault at each POI
Simulation results did not indicate instability, cascading, or uncontrolled separation associated with the use of momentary cessation
Updated models for two solar resources exhibited suspect behavior contributing to over-voltage conditions and subsequent resource tripping (~300 MW)
  ERCOT will work further with the Resource Entities to improve this undesirable response

## Slide 7: Questions?