## Data
[12 empty] | 20 to 52 actual | 20 to 52 expected
NMMSUnitClass | Fuel_Type | Gen_Type | Delta_Frequency | PI_HSL | PI_LSL | PACapacity | Headroom | PI_MW_pre | PI_MW_post | MW_Change | RampMagnitude | APFR_adj | EPFR_final | PUPFR | Droop | PI_MW_MaxResponse | RampMWSustained | ASPFR_adj | ESPFR_final | sMW_Change | sDelta_Frequency | PUSPFR | sDroop | Sdroop_Calc | MaxDeadband | MaxDroop | H1 | H2
CombinedCycle | CC | COGN | -0.131 | 549.1 | 275 | 12 | 97.2 | 439.9 | 449.2 | 9.3 | -0.89 | 10.204 | 13.472 | 0.757 | 12.89% | 454.8 | -1.2 | 16.124 | 12.87 | 14.9 | -0.127 | 1.253 | 7.802% | -6.44 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.131 | 606 | 270 | 0 | 224.8 | 381.2 | 404.6 | 23.4 | 7.19 | 16.124 | 19.777 | 0.815 | 5.655% | 404.9 | 10 | 13.665 | 18.908 | 23.7 | -0.127 | 0.723 | 5.413% | -3.51 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.131 | 585 | 235 | 0 | 240.3 | 344.7 | 365.9 | 21.2 | 5.88 | 15.308 | 19.092 | 0.802 | 6.026% | 363.9 | 8.2 | 10.943 | 18.253 | 19.2 | -0.127 | 0.6 | 6.451% | -3.92 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.131 | 230 | 150 | 0 | 6.3 | 223.7 | 241.5 | 17.8 | 0.76 | 17.037 | 5.769 | 2 | 2.823% | 241.5 | 1.1 | 16.751 | 5.511 | 17.8 | -0.127 | 2 | 2.737% | -2.74 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.131 | 560 | 135 | 0 | 247.7 | 312.3 | 320.4 | 8.1 | -3.56 | 11.657 | 13.707 | 0.85 | 15.1% | 319.8 | -5 | 12.437 | 13.104 | 7.5 | -0.127 | 0.949 | 15.81% | -9.09 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.131 | 413 | 125 | 0 | 185.3 | 227.7 | 236.2 | 8.5 | -1.58 | 10.123 | 11.887 | 0.852 | 10.61% | 233.9 | -2.2 | 8.432 | 11.364 | 6.2 | -0.127 | 0.742 | 14.1% | -8.01 | 0.017 | 0.05 | 6.284% | 5.784%
Wind | WND | WIND | -0.131 | 139.3 | 0 | 0 | 13.2 | 126.1 | 131 | 4.9 | 0.35 | 4.524 | 4.546 | 0.995 | 6.213% | 132.3 | 0.5 | 5.729 | 4.346 | 6.2 | -0.127 | 1.318 | 4.76% | -4.44 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.131 | 257 | 150 | 18 | 46.1 | 192.9 | 198.6 | 5.7 | -0.83 | 6.494 | 5.995 | 1.083 | 9.849% | 199.4 | -1.1 | 7.642 | 5.727 | 6.5 | -0.127 | 1.334 | 8.373% | -6.48 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.131 | 358 | 270 | 0 | 58.4 | 299.6 | 312.1 | 12.5 | -0.22 | 12.762 | 8.98 | 1.421 | 6.255% | 316.3 | -0.3 | 17.003 | 8.578 | 16.7 | -0.127 | 1.982 | 4.539% | -3.92 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.131 | 105 | 12 | 0 | 92.1 | 12.9 | 16 | 3.1 | 0.34 | 2.72 | 3.39 | 0.802 | 7.404% | 15.6 | 0.5 | 2.241 | 3.241 | 2.7 | -0.127 | 0.691 | 8.242% | -1.03 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.131 | 345 | 185 | 11 | 65.9 | 268.1 | 280.8 | 12.7 | -0.42 | 13.113 | 8.378 | 1.565 | 5.933% | 281.8 | -0.6 | 14.249 | 8.003 | 13.7 | -0.127 | 1.78 | 5.332% | -4.27 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.131 | 560.8 | 343.3 | 0 | 44.5 | 516.3 | 535 | 18.7 | -0.41 | 19.172 | 14.067 | 1.363 | 6.549% | 538.9 | -0.6 | 23.231 | 13.438 | 22.6 | -0.127 | 1.729 | 5.254% | -4.99 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.131 | 593.6 | 152.7 | 0 | 111.2 | 482.4 | 508.3 | 25.9 | 1.49 | 24.455 | 13.888 | 1.761 | 5.005% | 506.3 | 2.1 | 21.912 | 13.278 | 23.9 | -0.127 | 1.65 | 5.258% | -4.41 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.131 | 593.6 | 152.7 | 0 | 111.2 | 482.4 | 508.3 | 25.9 | 1.49 | 24.455 | 13.888 | 1.761 | 5.005% | 506.3 | 2.1 | 21.912 | 13.278 | 23.9 | -0.127 | 1.65 | 5.258% | -4.41 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.131 | 588.2 | 150.2 | 0 | 45.4 | 542.8 | 567.8 | 25 | 1.49 | 23.541 | 13.463 | 1.749 | 5.138% | 564.8 | 2.1 | 20 | 12.871 | 22 | -0.127 | 1.554 | 5.66% | -5.39 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.131 | 588.2 | 150.2 | 0 | 45.4 | 542.8 | 567.8 | 25 | 1.49 | 23.541 | 13.463 | 1.749 | 5.138% | 564.8 | 2.1 | 20 | 12.871 | 22 | -0.127 | 1.554 | 5.66% | -5.39 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.131 | 428.6 | 180.3 | 0 | 96.7 | 331.9 | 348.9 | 17 | 1.43 | 15.578 | 13.987 | 1.114 | 5.506% | 350.1 | 2 | 16.227 | 13.372 | 18.2 | -0.127 | 1.214 | 4.986% | -3.98 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.131 | 964.9 | 461 | 18.1 | 110.3 | 836.5 | 852.4 | 15.9 | -2.95 | 18.888 | 23.749 | 0.795 | 13.25% | 870 | -4.1 | 37.605 | 22.687 | 33.5 | -0.127 | 1.658 | 6.097% | -5.45 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.131 | 727.9 | 378 | 119.9 | 124.2 | 483.8 | 501 | 17.2 | -1.2 | 18.334 | 15.251 | 1.202 | 9.241% | 506 | -1.7 | 23.803 | 14.569 | 22.2 | -0.127 | 1.634 | 6.941% | -4.76 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.131 | 470 | 180 | 0 | 289 | 181 | 187.5 | 6.5 | -0.2 | 6.715 | 7.985 | 0.841 | 15.8% | 186.5 | -0.3 | 5.75 | 7.553 | 5.5 | -0.127 | 0.761 | 18.1% | -7.17 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.131 | 470 | 180 | 0 | 289 | 181 | 187.5 | 6.5 | -0.2 | 6.715 | 7.985 | 0.841 | 15.8% | 186.5 | -0.3 | 5.75 | 7.553 | 5.5 | -0.127 | 0.761 | 18.1% | -7.17 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.131 | 470 | 180 | 0 | 289 | 181 | 187.5 | 6.5 | -0.2 | 6.715 | 7.985 | 0.841 | 15.8% | 186.5 | -0.3 | 5.75 | 7.553 | 5.5 | -0.127 | 0.761 | 18.1% | -7.17 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.131 | 470 | 180 | 0 | 289 | 181 | 187.5 | 6.5 | -0.2 | 6.715 | 7.985 | 0.841 | 15.8% | 186.5 | -0.3 | 5.75 | 7.553 | 5.5 | -0.127 | 0.761 | 18.1% | -7.17 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.131 | 232 | 150 | 5 | 43.4 | 183.6 | 190.8 | 7.2 | -1.19 | 8.461 | 6.425 | 1.317 | 7.039% | 190.8 | -1.7 | 8.914 | 6.143 | 7.2 | -0.127 | 1.451 | 6.824% | -5.56 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.131 | 203.9 | 0 | 32 | 36.5 | 135.4 | 160.9 | 25.5 | -1.34 | 26.793 | 4.312 | 2 | 1.747% | 162.1 | -1.9 | 28.504 | 4.119 | 26.7 | -0.127 | 2 | 1.617% | -1.11 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.131 | 622 | 304 | 120 | 93.8 | 408.2 | 425.1 | 16.9 | -0.01 | 16.889 | 12.592 | 1.341 | 8.037% | 429.3 | 0 | 21.089 | 12.029 | 21.1 | -0.127 | 1.753 | 6.241% | -4.22 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.131 | 285 | 164 | 55 | 31 | 199 | 207.3 | 8.3 | -1.39 | 9.707 | 5.769 | 1.683 | 7.5% | 207.3 | -1.9 | 10.318 | 5.511 | 8.3 | -0.127 | 1.872 | 7.271% | -5.23 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.131 | 831 | 358 | 0 | 203.5 | 627.5 | 641.6 | 14.1 | -1.55 | 15.693 | 20.606 | 0.762 | 12.87% | 641.4 | -2.2 | 16.101 | 19.7 | 13.9 | -0.127 | 0.817 | 12.66% | -9.85 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.131 | 847 | 452 | 0 | 313.2 | 533.8 | 545.5 | 11.7 | -0.44 | 12.17 | 21.229 | 0.573 | 15.81% | 546.3 | -0.6 | 13.17 | 20.296 | 12.5 | -0.127 | 0.649 | 14.34% | -9.32 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.131 | 118 | 72 | 0 | 21.8 | 96.2 | 104 | 7.8 | 0 | 7.809 | 3.482 | 2 | 3.307% | 104 | 0 | 7.823 | 3.313 | 7.8 | -0.127 | 2 | 3.206% | -2.69 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.131 | 550 | 360 | 0 | 69.5 | 480.5 | 498.9 | 18.4 | -0.3 | 18.638 | 13.796 | 1.351 | 6.528% | 503 | -0.4 | 22.903 | 13.179 | 22.5 | -0.127 | 1.738 | 5.175% | -4.66 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.131 | 553.8 | 316.6 | 45.8 | 14 | 494 | 507.7 | 13.7 | 1.18 | 12.476 | 12.745 | 0.979 | 8.828% | 510 | 1.6 | 14.358 | 12.174 | 16 | -0.127 | 1.179 | 7.328% | -6.74 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.131 | 252 | 150 | 5 | 44.7 | 202.3 | 209 | 6.7 | -0.7 | 7.394 | 6.165 | 1.199 | 8.216% | 209.3 | -1 | 8.022 | 5.894 | 7 | -0.127 | 1.361 | 7.624% | -6.31 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.131 | 750 | 350 | 0 | 398.7 | 351.3 | 369.2 | 17.9 | -4.11 | 22.074 | 24.477 | 0.902 | 9.15% | 368.9 | -5.7 | 23.334 | 23.401 | 17.6 | -0.127 | 0.997 | 9.021% | -4.36 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.131 | 710 | 350 | 0 | 256 | 454 | 464.6 | 10.6 | -3.1 | 13.728 | 23.172 | 0.592 | 14.63% | 464.8 | -4.3 | 15.116 | 22.153 | 10.8 | -0.127 | 0.682 | 13.92% | -9.18 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.131 | 735 | 400 | 0 | 330.7 | 404.3 | 405.9 | 1.6 | -0.12 | 1.668 | 23.987 | 0.07 | 100.3% | 401.7 | -0.2 | -2.445 | 22.933 | -2.6 | -0.127 | 0 | -59.85% | 33.94 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.131 | 758.9 | 473.7 | 55.3 | 131.8 | 571.8 | 606 | 34.2 | -0.65 | 34.827 | 17.649 | 1.973 | 4.846% | 609.6 | -0.9 | 38.703 | 16.859 | 37.8 | -0.127 | 2 | 4.25% | -3.3 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.131 | 532 | 235 | 0 | 85.8 | 446.2 | 456.5 | 10.3 | -0.71 | 11.051 | 13.344 | 0.828 | 11.28% | 463.3 | -1 | 18.107 | 12.747 | 17.1 | -0.127 | 1.42 | 6.587% | -5.7 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.131 | 392 | 220 | 0 | 23.1 | 368.9 | 375.5 | 6.6 | 0.24 | 6.342 | 12.381 | 0.512 | 12.97% | 376.1 | 0.3 | 6.872 | 11.836 | 7.2 | -0.127 | 0.581 | 11.53% | -11.18 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.131 | 392 | 220 | 0 | 23.1 | 368.9 | 375.5 | 6.6 | 0.24 | 6.342 | 12.381 | 0.512 | 12.97% | 376.1 | 0.3 | 6.872 | 11.836 | 7.2 | -0.127 | 0.581 | 11.53% | -11.18 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.131 | 79 | 55 | 0 | 21.8 | 57.2 | 60.4 | 3.2 | -0.64 | 3.854 | 2.331 | 1.653 | 5.399% | 60.4 | -0.9 | 4.08 | 2.218 | 3.2 | -0.127 | 1.839 | 5.234% | -3.89 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.131 | 84 | 55 | 0 | 26.7 | 57.3 | 60.2 | 2.9 | -0.54 | 3.444 | 2.479 | 1.389 | 6.334% | 60.1 | -0.8 | 3.523 | 2.358 | 2.8 | -0.127 | 1.494 | 6.36% | -4.46 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.131 | 895 | 465 | 122.7 | 30.7 | 741.6 | 762.5 | 20.9 | -4.16 | 25.102 | 19.372 | 1.296 | 9.351% | 768.2 | -5.8 | 32.446 | 18.506 | 26.6 | -0.127 | 1.753 | 7.123% | -6.09 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.131 | 659 | 155 | 0 | 34.6 | 624.4 | 642.2 | 17.8 | -2.74 | 20.612 | 16.338 | 1.262 | 8.085% | 642.4 | -3.8 | 21.878 | 15.62 | 18 | -0.127 | 1.401 | 7.751% | -7.57 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.131 | 390 | 185 | 35 | 73.8 | 281.2 | 293.6 | 12.4 | 0.1 | 12.288 | 8.905 | 1.38 | 6.869% | 294.8 | 0.1 | 13.435 | 8.506 | 13.6 | -0.127 | 1.579 | 6.072% | -4.51 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 552.8 | 275 | 12 | 126.1 | 414.7 | 420.5 | 5.8 | -2.54 | 8.327 | 15.447 | 0.539 | 23.04% | 423.7 | -3.5 | 12.54 | 15.234 | 9 | -0.143 | 0.823 | 14.64% | -11.13 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.145 | 606 | 220 | 0 | 121 | 485 | 495.2 | 10.2 | -7.37 | 17.617 | 22.492 | 0.783 | 14.36% | 488.9 | -10.3 | 14.196 | 22.187 | 3.9 | -0.143 | 0.64 | 37.04% | -30.05 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.145 | 602 | 235 | 0 | 240.4 | 361.6 | 380.4 | 18.8 | -1.66 | 20.453 | 22.343 | 0.915 | 7.74% | 374 | -2.3 | 14.73 | 22.04 | 12.4 | -0.143 | 0.668 | 11.57% | -7.05 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.145 | 459 | 300 | 0 | 61.6 | 397.4 | 421.9 | 24.5 | -0.19 | 24.704 | 13.11 | 1.884 | 4.529% | 420.3 | -0.3 | 23.246 | 12.93 | 22.9 | -0.143 | 1.798 | 4.778% | -4.19 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.145 | 413 | 280 | 0 | 115 | 298 | 309 | 11 | -3.18 | 14.108 | 12.96 | 1.089 | 9.076% | 306.7 | -4.4 | 13.091 | 12.785 | 8.7 | -0.143 | 1.024 | 11.32% | -8.27 | 0.017 | 0.05 | 6.284% | 5.784%
Wind | WND | WIND | -0.145 | 153.3 | 0 | 0 | 28.4 | 124.9 | 127.2 | 2.3 | -1.12 | 3.477 | 5.69 | 0.611 | 16.12% | 124.6 | -1.6 | 1.31 | 5.613 | -0.3 | -0.143 | 0.233 | -121.9% | 100.52 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.145 | 254 | 168 | 12 | 61.4 | 180.6 | 189.8 | 9.2 | -0.71 | 9.983 | 6.912 | 1.444 | 6.675% | 191.2 | -1 | 11.614 | 6.817 | 10.6 | -0.143 | 1.704 | 5.714% | -4.11 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 178 | 87 | 65 | 11.3 | 101.7 | 102.4 | 0.7 | 0.71 | 0.017 | 3.228 | 0.005 | 61.49% | 99.7 | 1 | -2.935 | 3.183 | -2 | -0.143 | 0 | -21.23% | 12.27 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 492 | 350 | 54 | 59.1 | 378.9 | 394.8 | 15.9 | 0.2 | 15.765 | 12.51 | 1.26 | 7.48% | 398.7 | 0.3 | 19.57 | 12.338 | 19.8 | -0.143 | 1.586 | 5.924% | -4.62 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 275 | 255 | 0 | 17.7 | 257.3 | 270.8 | 13.5 | 0.12 | 13.427 | 7.855 | 1.709 | 4.925% | 267.9 | 0.2 | 10.443 | 7.747 | 10.6 | -0.143 | 1.348 | 6.186% | -5.86 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.145 | 596 | 153 | 0 | 142.2 | 453.8 | 477.1 | 23.3 | -3.07 | 26.415 | 16.037 | 1.647 | 6.183% | 473 | -4.3 | 23.515 | 15.82 | 19.2 | -0.143 | 1.486 | 7.4% | -5.71 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.145 | 596 | 153 | 0 | 142.2 | 453.8 | 477.1 | 23.3 | -3.07 | 26.415 | 16.037 | 1.647 | 6.183% | 473 | -4.3 | 23.515 | 15.82 | 19.2 | -0.143 | 1.486 | 7.4% | -5.71 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.145 | 589.1 | 153.1 | 0 | 79.5 | 509.6 | 537.4 | 27.8 | -1.91 | 29.763 | 15.503 | 1.92 | 5.122% | 532.4 | -2.7 | 25.542 | 15.293 | 22.8 | -0.143 | 1.67 | 6.159% | -5.4 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.145 | 589.1 | 153.1 | 0 | 79.5 | 509.6 | 537.4 | 27.8 | -1.91 | 29.763 | 15.503 | 1.92 | 5.122% | 532.4 | -2.7 | 25.542 | 15.293 | 22.8 | -0.143 | 1.67 | 6.159% | -5.4 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.145 | 426.6 | 180.3 | 0 | 96.7 | 329.9 | 348.8 | 18.9 | -0.7 | 19.516 | 15.835 | 1.232 | 5.456% | 348.4 | -1 | 19.399 | 15.62 | 18.5 | -0.143 | 1.242 | 5.497% | -4.31 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.145 | 957.2 | 461 | 20.7 | 121.6 | 814.9 | 828.1 | 13.2 | -3.54 | 16.705 | 26.751 | 0.624 | 17.53% | 852 | -4.9 | 41.997 | 26.382 | 37.1 | -0.143 | 1.592 | 6.15% | -5.31 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 970.3 | 461 | 39.2 | 119.1 | 812 | 835 | 23 | 0 | 22.969 | 26.594 | 0.864 | 10.2% | 856 | 0 | 44 | 26.228 | 44 | -0.143 | 1.678 | 5.256% | -4.46 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 724 | 390 | 119.9 | 119.4 | 484.7 | 503.1 | 18.4 | -0.6 | 19.052 | 17.255 | 1.104 | 9.511% | 510 | -0.8 | 26.155 | 17.018 | 25.3 | -0.143 | 1.537 | 6.821% | -4.63 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.145 | 470 | 180 | 0 | 289.3 | 180.7 | 188.2 | 7.5 | -0.37 | 7.868 | 9.409 | 0.836 | 15.15% | 187.1 | -0.5 | 6.907 | 9.258 | 6.4 | -0.143 | 0.746 | 17.51% | -6.81 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.145 | 470 | 180 | 0 | 289.3 | 180.7 | 188.2 | 7.5 | -0.37 | 7.868 | 9.409 | 0.836 | 15.15% | 187.1 | -0.5 | 6.907 | 9.258 | 6.4 | -0.143 | 0.746 | 17.51% | -6.81 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.145 | 470 | 180 | 0 | 289.3 | 180.7 | 188.2 | 7.5 | -0.37 | 7.868 | 9.409 | 0.836 | 15.15% | 187.1 | -0.5 | 6.907 | 9.258 | 6.4 | -0.143 | 0.746 | 17.51% | -6.81 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.145 | 470 | 180 | 0 | 289.3 | 180.7 | 188.2 | 7.5 | -0.37 | 7.868 | 9.409 | 0.836 | 15.15% | 187.1 | -0.5 | 6.907 | 9.258 | 6.4 | -0.143 | 0.746 | 17.51% | -6.81 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.145 | 238 | 150 | 12 | 45.5 | 180.5 | 190.5 | 10 | -0.09 | 10.122 | 7.206 | 1.405 | 5.755% | 189 | -0.1 | 8.697 | 7.108 | 8.5 | -0.143 | 1.224 | 6.677% | -5.13 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 218.1 | 0 | 40 | 146.8 | 31.3 | 49.4 | 18.1 | 0.17 | 17.87 | 5.087 | 2 | 2.914% | 53.2 | 0.2 | 21.634 | 5.017 | 21.9 | -0.143 | 2 | 2.375% | -0.34 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 615 | 304 | 120 | 111.9 | 383.1 | 399.8 | 16.7 | -1.53 | 18.315 | 14.138 | 1.295 | 8.901% | 403.7 | -2.1 | 22.759 | 13.944 | 20.6 | -0.143 | 1.632 | 7.117% | -4.49 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 634 | 305 | 120 | 137.6 | 376.4 | 386.4 | 10 | -0.74 | 10.715 | 14.681 | 0.73 | 15.32% | 383.7 | -1 | 8.384 | 14.479 | 7.3 | -0.143 | 0.579 | 20.7% | -12.46 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 625 | 260 | 117.8 | 49.9 | 457.3 | 470.7 | 13.4 | 0.28 | 13.101 | 14.486 | 0.904 | 11.27% | 470.4 | 0.4 | 12.699 | 14.287 | 13.1 | -0.143 | 0.889 | 11.37% | -8.43 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 625 | 260 | 124.9 | 43.1 | 457 | 470.9 | 13.9 | 0.27 | 13.549 | 14.285 | 0.948 | 10.87% | 470.7 | 0.4 | 13.301 | 14.088 | 13.7 | -0.143 | 0.944 | 10.87% | -8.06 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.145 | 831 | 358 | 0 | 472.2 | 358.8 | 393.3 | 34.5 | -2 | 36.522 | 23.415 | 1.56 | 5.822% | 397.7 | -2.8 | 41.684 | 23.098 | 38.9 | -0.143 | 1.805 | 5.092% | -2.23 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.145 | 847 | 452 | 0 | 389.8 | 457.2 | 473.7 | 16.5 | -0.57 | 17.038 | 24.22 | 0.703 | 12.41% | 474.1 | -0.8 | 17.737 | 23.892 | 16.9 | -0.143 | 0.742 | 11.95% | -6.54 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.145 | 393 | 234 | 7 | 150.7 | 235.3 | 258.5 | 23.2 | -0.3 | 23.476 | 11.025 | 2 | 4.095% | 253.5 | -0.4 | 18.561 | 10.873 | 18.2 | -0.143 | 1.707 | 5.148% | -3.12 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.145 | 118 | 72 | 0 | 22 | 96 | 103.8 | 7.8 | 0 | 7.859 | 3.964 | 1.982 | 3.66% | 99.3 | 0 | 3.292 | 3.905 | 3.3 | -0.143 | 0.843 | 8.531% | -7.02 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 550 | 360 | 0 | 60.3 | 489.7 | 508.1 | 18.4 | -0.35 | 18.754 | 15.709 | 1.194 | 7.225% | 512.7 | -0.5 | 23.514 | 15.493 | 23 | -0.143 | 1.518 | 5.701% | -5.14 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.145 | 243 | 150 | 12 | 71.1 | 159.9 | 168.8 | 8.9 | -2.37 | 11.293 | 6.21 | 1.819 | 6.601% | 169.7 | -3.3 | 13.087 | 6.125 | 9.8 | -0.143 | 2 | 5.913% | -3.94 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.145 | 244 | 150 | 12 | 72.3 | 159.7 | 168.6 | 8.9 | -2.67 | 11.565 | 6.238 | 1.854 | 6.629% | 169.6 | -3.7 | 13.607 | 6.153 | 9.9 | -0.143 | 2 | 5.877% | -3.9 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.145 | 252 | 150 | 5 | 49.5 | 197.5 | 207.2 | 9.7 | -0.54 | 10.261 | 6.913 | 1.484 | 6.281% | 206.2 | -0.8 | 9.471 | 6.819 | 8.7 | -0.143 | 1.389 | 6.907% | -5.48 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.145 | 252 | 150 | 5 | 48.6 | 198.4 | 207.6 | 9.2 | -0.17 | 9.304 | 6.932 | 1.342 | 6.623% | 207.3 | -0.2 | 9.115 | 6.838 | 8.9 | -0.143 | 1.333 | 6.751% | -5.38 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.145 | 690 | 350 | 0 | 336.6 | 353.4 | 377.6 | 24.2 | -0.39 | 24.619 | 25.609 | 0.961 | 6.892% | 374.4 | -0.5 | 21.602 | 25.262 | 21 | -0.143 | 0.855 | 7.832% | -4.07 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.145 | 670 | 350 | 0 | 307.4 | 362.6 | 380.1 | 17.5 | -4.86 | 22.291 | 24.867 | 0.896 | 9.254% | 376.3 | -6.8 | 20.415 | 24.53 | 13.7 | -0.143 | 0.832 | 11.66% | -6.39 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.145 | 775 | 400 | 0 | 372.7 | 402.3 | 402.7 | 0.4 | -0.02 | 0.456 | 28.764 | 0.016 | 468.3% | 397 | 0 | -5.327 | 28.374 | -5.3 | -0.143 | 0 | -34.86% | 18.34 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.145 | 525 | 336 | 27 | 141.9 | 356.1 | 369.6 | 13.5 | -2.73 | 16.256 | 14.224 | 1.143 | 9.4% | 377.7 | -3.8 | 25.418 | 14.028 | 21.6 | -0.143 | 1.812 | 5.794% | -3.98 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 525 | 336 | 27 | 121.4 | 376.6 | 389.3 | 12.7 | -1.94 | 14.681 | 14.224 | 1.032 | 9.992% | 396.5 | -2.7 | 22.653 | 14.028 | 19.9 | -0.143 | 1.615 | 6.289% | -4.57 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 759.4 | 476.9 | 55.2 | 145.9 | 558.3 | 593.2 | 34.9 | 1.06 | 33.793 | 20.114 | 1.68 | 5.259% | 596.6 | 1.5 | 36.786 | 19.837 | 38.3 | -0.143 | 1.854 | 4.726% | -3.52 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 751.7 | 463 | 93 | 173.1 | 485.6 | 515 | 29.4 | -1.53 | 31 | 18.814 | 1.648 | 6.18% | 523.2 | -2.1 | 39.763 | 18.555 | 37.6 | -0.143 | 2 | 4.766% | -3.12 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 428 | 205 | 9.4 | 194.6 | 224 | 243.5 | 19.5 | -0.12 | 19.596 | 11.956 | 1.639 | 5.306% | 246.6 | -0.2 | 22.736 | 11.792 | 22.6 | -0.143 | 1.928 | 4.515% | -2.39 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 480 | 275 | 0 | 88.1 | 391.9 | 409.2 | 17.3 | 0 | 17.29 | 13.71 | 1.261 | 6.707% | 409 | 0 | 17.071 | 13.521 | 17.1 | -0.143 | 1.263 | 6.692% | -5.54 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.145 | 540 | 310 | 0 | 44.3 | 495.7 | 506.6 | 10.9 | 0.61 | 10.295 | 20.042 | 0.514 | 11.98% | 506.9 | 0.9 | 10.307 | 19.77 | 11.2 | -0.143 | 0.521 | 11.49% | -10.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.145 | 84 | 55 | 0 | 26.8 | 57.2 | 61 | 3.8 | -0.21 | 4.055 | 2.822 | 1.437 | 5.35% | 60.7 | -0.3 | 3.846 | 2.78 | 3.5 | -0.143 | 1.383 | 5.728% | -3.94 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.145 | 84 | 55 | 0 | 25.9 | 58.1 | 61.8 | 3.7 | -0.13 | 3.796 | 2.822 | 1.345 | 5.494% | 61.3 | -0.2 | 3.399 | 2.78 | 3.2 | -0.143 | 1.223 | 6.265% | -4.38 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.145 | 895 | 460 | 112.7 | 30.7 | 751.6 | 776.8 | 25.2 | 2.22 | 22.911 | 22.346 | 1.025 | 8.584% | 780.6 | 3.1 | 25.906 | 22.038 | 29 | -0.143 | 1.175 | 7.356% | -6.26 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.145 | 155 | 80 | 0 | 15.3 | 139.7 | 143.7 | 4 | 1.62 | 2.348 | 5.214 | 0.45 | 9.372% | 145.4 | 2.3 | 3.447 | 5.143 | 5.7 | -0.143 | 0.67 | 6.486% | -5.92 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.145 | 659 | 155 | 0 | 503.9 | 155.1 | 187.9 | 32.8 | -0.4 | 33.131 | 22.739 | 1.457 | 4.856% | 187.4 | -0.6 | 32.832 | 22.431 | 32.3 | -0.143 | 1.464 | 4.863% | -1.16 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.086 | 531.7 | 275 | 0 | 117.5 | 414.2 | 422.5 | 8.3 | -1.36 | 9.644 | 7.927 | 1.217 | 9.185% | 434 | -1.9 | 21.687 | 5.884 | 19.8 | -0.071 | 2 | 3.179% | -3 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.086 | 570 | 235 | 0 | 331.2 | 238.8 | 247.7 | 8.9 | -0.68 | 9.643 | 11.208 | 0.86 | 9.183% | 247 | -0.9 | 9.191 | 8.408 | 8.2 | -0.071 | 1.093 | 8.229% | -4.17 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.086 | 237 | 155 | 0 | 79.2 | 157.8 | 162.5 | 4.7 | 0.47 | 4.239 | 3.533 | 1.2 | 7.234% | 160.1 | 0.7 | 1.629 | 2.623 | 2.3 | -0.071 | 0.621 | 12.21% | -9.82 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.086 | 530 | 361 | 63.5 | 41 | 425.5 | 438.1 | 12.6 | 0.35 | 12.223 | 6.955 | 1.757 | 6.031% | 437.9 | 0.5 | 11.922 | 5.163 | 12.4 | -0.071 | 2 | 5.06% | -4.92 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.086 | 450 | 300 | 0 | 67.4 | 382.6 | 400.2 | 17.6 | -0.42 | 18 | 6.709 | 2 | 3.666% | 399.3 | -0.6 | 17.329 | 4.98 | 16.7 | -0.071 | 2 | 3.19% | -3.28 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.086 | 410 | 70 | 0 | 311.7 | 98.3 | 105.5 | 7.2 | -0.54 | 7.77 | 4.621 | 1.682 | 8.17% | 106.1 | -0.8 | 8.53 | 2.995 | 7.8 | -0.071 | 2 | 6.227% | -1.8 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.086 | 295 | 149 | 0 | 51.1 | 243.9 | 259.8 | 15.9 | 2.3 | 13.545 | 4.398 | 2 | 2.661% | 264.4 | 3.2 | 17.27 | 3.265 | 20.5 | -0.071 | 2 | 1.704% | -1.7 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.086 | 213 | 140 | 12 | 46.3 | 154.7 | 157.4 | 2.7 | 0.65 | 2.026 | 2.997 | 0.676 | 11.32% | 158.6 | 0.9 | 2.997 | 2.224 | 3.9 | -0.071 | 1.347 | 6.47% | -5.68 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.086 | 560 | 390 | 0 | 154.9 | 405.1 | 411.5 | 6.4 | -1.6 | 7.963 | 9.087 | 0.876 | 12.55% | 417.1 | -2.2 | 14.149 | 6.817 | 12 | -0.071 | 2 | 5.525% | -4.84 | 0.017 | 0.05 | 6.284% | 5.784%
Wind | WND | WIND | -0.086 | 65.3 | 0 | 0 | 11.4 | 53.9 | 53.9 | 0 | -4.48 | 4.484 | 1.284 | 2 | 0% | 53.9 | -6.2 | 6.24 | 0.963 | 0 | -0.071 | 2 | 0% |  | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.086 | 616 | 381 | 61 | 16.9 | 538.1 | 540.8 | 2.7 | 0.65 | 2.038 | 8.274 | 0.246 | 32.71% | 541.3 | 0.9 | 2.323 | 6.142 | 3.2 | -0.071 | 0.378 | 22.79% | -24.09 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.086 | 340 | 254 | 0 | 65.5 | 274.5 | 286.5 | 12 | 0.04 | 11.979 | 5.069 | 2 | 4.063% | 286.7 | 0.1 | 12.146 | 3.763 | 12.2 | -0.071 | 2 | 3.3% | -3.22 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.086 | 329 | 150 | 11 | 61.2 | 256.8 | 268.9 | 12.1 | 0.93 | 11.129 | 4.741 | 2 | 3.9% | 268.6 | 1.3 | 10.481 | 3.519 | 11.8 | -0.071 | 2 | 3.302% | -3.12 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.086 | 534.4 | 352.5 | 0 | 104.2 | 430.2 | 443.4 | 13.2 | -3.18 | 16.3 | 7.967 | 2 | 5.805% | 454.1 | -4.4 | 28.294 | 5.913 | 23.9 | -0.071 | 2 | 2.647% | -2.58 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.086 | 591.8 | 150.9 | 0 | 180.1 | 411.7 | 425.6 | 13.9 | -0.61 | 14.504 | 8.603 | 1.686 | 6.105% | 424.1 | -0.8 | 13.253 | 6.453 | 12.4 | -0.071 | 2 | 5.65% | -4.76 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.086 | 591.8 | 150.9 | 0 | 180.1 | 411.7 | 425.6 | 13.9 | -0.61 | 14.504 | 8.603 | 1.686 | 6.105% | 424.1 | -0.8 | 13.253 | 6.453 | 12.4 | -0.071 | 2 | 5.65% | -4.76 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.086 | 589.1 | 151.2 | 0 | 171.7 | 417.4 | 429.8 | 12.4 | -0.74 | 13.175 | 8.556 | 1.54 | 6.812% | 428.6 | -1 | 12.205 | 6.418 | 11.2 | -0.071 | 1.902 | 6.227% | -5.34 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.086 | 589.1 | 151.2 | 0 | 171.7 | 417.4 | 429.8 | 12.4 | -0.74 | 13.175 | 8.556 | 1.54 | 6.812% | 428.6 | -1 | 12.205 | 6.418 | 11.2 | -0.071 | 1.902 | 6.227% | -5.34 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.086 | 433.4 | 180.3 | 0 | 18.5 | 414.9 | 421.9 | 7 | -1.04 | 8.044 | 8.522 | 0.944 | 8.878% | 421.3 | -1.4 | 7.832 | 6.393 | 6.4 | -0.071 | 1.225 | 8.018% | -9.29 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.086 | 927.5 | 460.9 | 77.3 | 39.6 | 810.6 | 833.6 | 23 | 0.59 | 22.401 | 12.676 | 1.767 | 5.781% | 842 | 0.8 | 30.608 | 9.409 | 31.4 | -0.071 | 2 | 3.496% | -3.7 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.086 | 261.9 | 175 | 39.9 | 46.3 | 175.7 | 180.7 | 5 | 0 | 5.001 | 3.309 | 1.511 | 7.513% | 180.8 | 0 | 5.065 | 2.456 | 5.1 | -0.071 | 2 | 6.082% | -4.93 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.086 | 481 | 345 | 34 | 72.7 | 374.3 | 391.2 | 16.9 | 0.38 | 16.47 | 6.664 | 2 | 4.081% | 390.8 | 0.5 | 16.007 | 4.947 | 16.5 | -0.071 | 2 | 3.451% | -3.25 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.086 | 480 | 345 | 35 | 61 | 384 | 399.9 | 15.9 | 0.35 | 15.506 | 6.634 | 2 | 4.329% | 400.3 | 0.5 | 15.776 | 4.925 | 16.3 | -0.071 | 2 | 3.486% | -3.37 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.086 | 225 | 155 | 12 | 41 | 172 | 178.3 | 6.3 | 0.43 | 5.903 | 3.505 | 1.684 | 5.124% | 178.2 | 0.6 | 5.629 | 2.629 | 6.2 | -0.071 | 2 | 4.299% | -3.97 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.086 | 226 | 150 | 12 | 41.3 | 172.7 | 179.6 | 6.9 | 0.79 | 6.114 | 3.529 | 1.732 | 4.699% | 178.8 | 1.1 | 4.97 | 2.648 | 6.1 | -0.071 | 1.877 | 4.389% | -4.05 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.086 | 223 | 150 | 5 | 41.9 | 176.1 | 182.6 | 6.5 | 0.89 | 5.682 | 3.633 | 1.564 | 4.922% | 182.1 | 1.2 | 4.784 | 2.725 | 6 | -0.071 | 1.755 | 4.403% | -4.2 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.086 | 568 | 304 | 120 | 100.1 | 347.9 | 361.4 | 13.5 | 0.76 | 12.662 | 6.679 | 1.896 | 6.033% | 361.9 | 1.1 | 12.911 | 4.958 | 14 | -0.071 | 2 | 4.803% | -3.56 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.086 | 583 | 358 | 0 | 120 | 463 | 473.4 | 10.4 | -2.14 | 12.506 | 8.492 | 1.473 | 8.038% | 474.4 | -3 | 14.392 | 6.37 | 11.4 | -0.071 | 2 | 6.054% | -5.82 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.086 | 105 | 62 | 0 | 21.4 | 83.6 | 89.3 | 5.7 | 0 | 5.65 | 1.845 | 2 | 2.645% | 87.5 | 0 | 3.828 | 1.33 | 3.9 | -0.071 | 2 | 3.193% | -3.07 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | GT | -0.086 | 233 | 150 | 12 | 41.4 | 179.6 | 186.2 | 6.6 | 0.37 | 6.226 | 3.262 | 1.909 | 5.064% | 185.6 | 0.5 | 5.446 | 2.447 | 6 | -0.071 | 2 | 4.6% | -4.29 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.086 | 190 | 40 | 0 | 102 | 88 | 94.1 | 6.1 | 3.58 | 2.553 | 3.502 | 0.729 | 4.469% | 94.1 | 5 | 1.171 | 2.627 | 6.1 | -0.071 | 0.446 | 3.69% | -2.06 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.086 | 245 | 144 | 28.2 | 68.2 | 148.6 | 150.5 | 1.9 | -2.61 | 4.523 | 3.233 | 1.399 | 18.5% | 153.2 | -3.6 | 8.25 | 2.4 | 4.6 | -0.071 | 2 | 6.309% | -4.62 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.086 | 239 | 144 | 28.2 | 48.2 | 162.6 | 166.9 | 4.3 | -2.58 | 6.909 | 3.143 | 2 | 7.973% | 169.8 | -3.6 | 10.823 | 2.333 | 7.2 | -0.071 | 2 | 3.932% | -3.23 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.086 | 725 | 427.2 | 0 | 205 | 520 | 540.7 | 20.7 | -2.36 | 23.093 | 10.809 | 2 | 5.021% | 545.5 | -3.3 | 28.798 | 8.023 | 25.5 | -0.071 | 2 | 3.365% | -2.92 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.086 | 484.4 | 235 | 0 | 164.5 | 319.9 | 336.6 | 16.7 | -5.96 | 22.705 | 7.222 | 2 | 4.159% | 349.6 | -8.3 | 38.006 | 5.361 | 29.7 | -0.071 | 2 | 1.931% | -1.54 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.086 | 512 | 350 | 12 | 20.4 | 479.6 | 485.9 | 6.3 | 1.47 | 4.874 | 7.454 | 0.654 | 11.65% | 488.5 | 2.1 | 6.89 | 5.533 | 8.9 | -0.071 | 1.245 | 6.811% | -7.72 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.086 | 392 | 220 | 0 | 69.2 | 322.8 | 333.3 | 10.5 | -1.18 | 11.687 | 7.459 | 1.567 | 5.354% | 333.1 | -1.6 | 11.899 | 5.596 | 10.3 | -0.071 | 2 | 4.506% | -4.49 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.086 | 84 | 55 | 0 | 27.5 | 56.5 | 58.9 | 2.4 | 0.02 | 2.436 | 1.476 | 1.65 | 5.028% | 58.6 | 0 | 2.087 | 1.064 | 2.1 | -0.071 | 1.962 | 4.747% | -3.84 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.086 | 84 | 55 | 0 | 26.7 | 57.3 | 59.7 | 2.4 | 0.15 | 2.202 | 1.476 | 1.491 | 5.028% | 59.2 | 0.2 | 1.694 | 1.064 | 1.9 | -0.071 | 1.593 | 5.246% | -4.31 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.086 | 610 | 158 | 0 | 355 | 255 | 270.2 | 15.2 | -3.37 | 18.585 | 10.613 | 1.751 | 5.754% | 269.7 | -4.7 | 19.432 | 7.962 | 14.7 | -0.071 | 2 | 4.912% | -2.48 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.086 | 711 | 340 | 40 | 184 | 487 | 504.5 | 17.5 | -6.92 | 24.433 | 10.005 | 2 | 5.825% | 498.9 | -9.6 | 21.554 | 7.426 | 11.9 | -0.071 | 2 | 7.073% | -5.86 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.075 | 544.1 | 275 | 0 | 206.1 | 338 | 340.8 | 2.8 | -6.07 | 8.88 | 5.669 | 1.566 | 24.3% | 342.5 | -8.5 | 12.95 | 5.593 | 4.5 | -0.075 | 2 | 15.12% | -9.38 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.075 | 562 | 235 | 0 | 326.1 | 235.9 | 239.4 | 3.5 | -0.44 | 3.888 | 7.824 | 0.497 | 20.08% | 238.2 | -0.6 | 2.877 | 7.724 | 2.3 | -0.075 | 0.372 | 30.56% | -12.81 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.075 | 544 | 381 | 49 | 99.6 | 395.4 | 401.5 | 6.1 | -0.18 | 6.283 | 5.157 | 1.218 | 11.15% | 400.4 | -0.2 | 5.246 | 5.088 | 5 | -0.075 | 1.031 | 13.61% | -9.88 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.075 | 459 | 300 | 0 | 150.3 | 308.7 | 315.6 | 6.9 | -0.69 | 7.549 | 4.782 | 1.578 | 8.319% | 319.3 | -1 | 11.534 | 4.718 | 10.6 | -0.075 | 2 | 5.415% | -3.64 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.075 | 230 | 60 | 0 | 163.8 | 66.2 | 69 | 2.8 | -0.82 | 3.678 | 1.815 | 2 | 10.29% | 71.5 | -1.1 | 6.499 | 1.775 | 5.3 | -0.075 | 2 | 5.435% | -1.55 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.075 | 323 | 177 | 5 | 139.6 | 178.4 | 186.6 | 8.2 | 0.65 | 7.568 | 3.313 | 2 | 4.927% | 187.8 | 0.9 | 8.483 | 3.269 | 9.4 | -0.075 | 2 | 4.298% | -2.37 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.075 | 207 | 135 | 13 | 53.2 | 140.8 | 143.1 | 2.3 | -0.18 | 2.48 | 2.021 | 1.227 | 11.26% | 144.9 | -0.2 | 4.318 | 1.994 | 4.1 | -0.075 | 2 | 6.318% | -4.29 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.075 | 560 | 400 | 0 | 132.4 | 427.6 | 435.5 | 7.9 | -0.83 | 8.707 | 6.726 | 1.295 | 8.864% | 437.4 | -1.2 | 10.914 | 6.64 | 9.8 | -0.075 | 1.644 | 7.146% | -5.45 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.075 | 65 | 22 | 0 | 36.6 | 28.4 | 30 | 1.6 | 0.12 | 1.395 | 0.677 | 2 | 5.096% | 28.5 | 0.2 | -0.107 | 0.668 | 0.1 | -0.075 | 0 | 81.53% | -35.22 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.075 | 491 | 334 | 52 | 100.7 | 338.3 | 349.5 | 11.2 | 0.14 | 11.072 | 4.574 | 2 | 5.482% | 348.8 | 0.2 | 10.308 | 4.513 | 10.5 | -0.075 | 2 | 5.848% | -4.02 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.075 | 235 | 144 | 0 | 86.9 | 148.1 | 149.8 | 1.7 | 0.24 | 1.475 | 2.448 | 0.602 | 17.3% | 149.3 | 0.3 | 0.857 | 2.416 | 1.2 | -0.075 | 0.355 | 24.5% | -15.4 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.075 | 351 | 153 | 11 | 186.3 | 153.7 | 158.3 | 4.6 | 0.09 | 4.523 | 3.542 | 1.277 | 9.544% | 159 | 0.1 | 5.146 | 3.495 | 5.3 | -0.075 | 1.472 | 8.284% | -3.62 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.075 | 535.9 | 343 | 0 | 106 | 429.9 | 439.2 | 9.3 | -0.78 | 10.167 | 5.584 | 1.821 | 7.206% | 444.6 | -1.1 | 15.833 | 5.509 | 14.7 | -0.075 | 2 | 4.559% | -3.65 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.075 | 590.9 | 152.5 | 0 | 326.3 | 264.6 | 271.6 | 7 | -2.66 | 9.624 | 6.162 | 1.562 | 10.56% | 271.6 | -3.7 | 10.733 | 6.083 | 7 | -0.075 | 1.764 | 10.56% | -4.72 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.075 | 590.9 | 152.5 | 0 | 326.3 | 264.6 | 271.6 | 7 | -2.66 | 9.624 | 6.162 | 1.562 | 10.56% | 271.6 | -3.7 | 10.733 | 6.083 | 7 | -0.075 | 1.764 | 10.56% | -4.72 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.075 | 590.2 | 152.3 | 0 | 291.5 | 298.7 | 304.6 | 5.9 | -3.49 | 9.389 | 6.288 | 1.493 | 12.51% | 304.6 | -4.9 | 10.68 | 6.207 | 5.9 | -0.075 | 1.721 | 12.51% | -6.32 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.075 | 590.2 | 152.3 | 0 | 291.5 | 298.7 | 304.6 | 5.9 | -3.49 | 9.389 | 6.288 | 1.493 | 12.51% | 304.6 | -4.9 | 10.68 | 6.207 | 5.9 | -0.075 | 1.721 | 12.51% | -6.32 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.075 | 428.6 | 180.3 | 0 | 152.5 | 276.1 | 281.4 | 5.3 | -1.1 | 6.436 | 5.58 | 1.153 | 10.11% | 280.9 | -1.5 | 6.346 | 5.508 | 4.8 | -0.075 | 1.152 | 11.17% | -7.18 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.075 | 497 | 272 | 0 | 170.9 | 326.1 | 329.5 | 3.4 | 0.47 | 2.868 | 5.178 | 0.554 | 18.28% | 325.1 | 0.7 | -1.685 | 5.109 | -1 | -0.075 | 0 | -62.15% | 40.73 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.075 | 491 | 264 | 0 | 198.6 | 292.4 | 298.1 | 5.7 | 0.65 | 5.004 | 5.116 | 0.978 | 10.77% | 295.4 | 0.9 | 2.068 | 5.047 | 3 | -0.075 | 0.41 | 20.47% | -12.17 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.075 | 360.1 | 215 | 39.9 | 98.9 | 221.3 | 223.9 | 2.6 | -0.6 | 3.13 | 3.336 | 0.938 | 17.32% | 225.4 | -0.8 | 4.883 | 3.291 | 4.1 | -0.075 | 1.484 | 10.99% | -6.74 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.075 | 500 | 352 | 37 | 107.6 | 355.4 | 363.7 | 8.3 | -0.22 | 8.58 | 4.824 | 1.779 | 7.534% | 365.3 | -0.3 | 10.28 | 4.759 | 9.9 | -0.075 | 2 | 6.316% | -4.48 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.075 | 222 | 148.7 | 5 | 67.1 | 149.9 | 154.1 | 4.2 | -0.16 | 4.336 | 2.465 | 1.759 | 6.614% | 154.3 | -0.2 | 4.619 | 2.433 | 4.4 | -0.075 | 1.898 | 6.313% | -4.25 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.075 | 228 | 153.6 | 12 | 61.5 | 154.5 | 158.1 | 3.6 | 0.11 | 3.505 | 2.453 | 1.429 | 7.925% | 158.6 | 0.2 | 3.988 | 2.422 | 4.1 | -0.075 | 1.647 | 6.958% | -4.7 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.075 | 230 | 148.6 | 12 | 68.4 | 149.6 | 153.5 | 3.9 | -0.5 | 4.349 | 2.476 | 1.757 | 7.379% | 154 | -0.7 | 5.028 | 2.444 | 4.4 | -0.075 | 2 | 6.541% | -4.24 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.075 | 226 | 148.4 | 5 | 71.3 | 149.7 | 153.4 | 3.7 | 0 | 3.73 | 2.51 | 1.486 | 7.643% | 154 | 0 | 4.288 | 2.478 | 4.3 | -0.075 | 1.731 | 6.576% | -4.35 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.075 | 172.3 | 0 | 20 | 149.4 | 2.9 | 10 | 7.1 | -1.21 | 8.281 | 1.587 | 2 | 3.037% | 7.2 | -1.7 | 5.961 | 1.566 | 4.3 | -0.075 | 2 | 5.015% | -0.08 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.075 | 604 | 305 | 120 | 177.3 | 306.7 | 311.2 | 4.5 | -1.15 | 5.699 | 5.043 | 1.13 | 16.78% | 320.2 | -1.6 | 15.097 | 4.975 | 13.5 | -0.075 | 2 | 5.595% | -2.84 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.075 | 831 | 358 | 0 | 465.7 | 365.3 | 383 | 17.7 | -0.67 | 18.364 | 8.822 | 2 | 5.87% | 386.1 | -0.9 | 21.764 | 8.709 | 20.8 | -0.075 | 2 | 4.995% | -2.19 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.075 | 844 | 451 | 0 | 386.4 | 457.6 | 463 | 5.4 | -0.59 | 5.912 | 9.096 | 0.65 | 19.54% | 463.8 | -0.8 | 6.998 | 8.979 | 6.2 | -0.075 | 0.779 | 17.02% | -9.22 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.075 | 378 | 120 | 7 | 54.9 | 316.1 | 325.1 | 9 | -0.35 | 9.308 | 3.865 | 2 | 5.253% | 326.4 | -0.5 | 10.778 | 3.814 | 10.3 | -0.075 | 2 | 4.59% | -3.83 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.075 | 237 | 150 | 12 | 74.4 | 150.6 | 154.2 | 3.6 | 0.02 | 3.577 | 2.293 | 1.56 | 8.237% | 154.6 | 0 | 4.004 | 2.264 | 4 | -0.075 | 1.769 | 7.413% | -4.7 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.075 | 235 | 150 | 12 | 72.5 | 150.5 | 154.4 | 3.9 | -0.13 | 4.002 | 2.273 | 1.761 | 7.539% | 154.8 | -0.2 | 4.508 | 2.243 | 4.3 | -0.075 | 2 | 6.838% | -4.37 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.075 | 238 | 150 | 12 | 75.5 | 150.5 | 154.2 | 3.7 | 0.13 | 3.563 | 2.304 | 1.547 | 8.048% | 154.6 | 0.2 | 3.979 | 2.274 | 4.1 | -0.075 | 1.75 | 7.263% | -4.58 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.075 | 665 | 449 | 22 | 66.9 | 576.1 | 582.3 | 6.2 | 0.18 | 6.037 | 6.699 | 0.901 | 13.41% | 589.3 | 0.2 | 12.968 | 6.61 | 13.2 | -0.075 | 1.962 | 6.299% | -5.45 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.075 | 493 | 235 | 0 | 240.6 | 252.4 | 261.9 | 9.5 | -2.6 | 12.099 | 5.137 | 2 | 6.49% | 269.6 | -3.6 | 20.784 | 5.068 | 17.2 | -0.075 | 2 | 3.584% | -1.83 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.075 | 232.2 | 118 | 0 | 100.3 | 131.9 | 133.3 | 1.4 | 0.39 | 1.029 | 2.419 | 0.426 | 20.75% | 132.9 | 0.5 | 0.525 | 2.387 | 1 | -0.075 | 0.22 | 29.05% | -16.46 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.075 | 392 | 220 | 0 | 166.7 | 225.3 | 231.1 | 5.8 | -0.53 | 6.36 | 4.522 | 1.407 | 8.453% | 232 | -0.7 | 7.425 | 4.464 | 6.7 | -0.075 | 1.663 | 7.318% | -4.2 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.075 | 84 | 57 | 0 | 26.3 | 57.7 | 59.2 | 1.5 | -0.09 | 1.585 | 1.034 | 1.534 | 7.019% | 59.3 | -0.1 | 1.684 | 1.019 | 1.6 | -0.075 | 1.653 | 6.58% | -4.49 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.075 | 84 | 57 | 0 | 26.7 | 57.3 | 58.8 | 1.5 | -0.07 | 1.575 | 1.034 | 1.524 | 7.019% | 58.7 | -0.1 | 1.441 | 1.019 | 1.4 | -0.075 | 1.414 | 7.52% | -5.1 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.075 | 400 | 156 | 0 | 237.8 | 162.2 | 171.4 | 9.2 | -0.27 | 9.492 | 5.216 | 1.82 | 5.438% | 171.9 | -0.4 | 10.108 | 5.149 | 9.7 | -0.075 | 1.963 | 5.158% | -2.09 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.075 | 577 | 155 | 0 | 419 | 158 | 169.5 | 11.5 | -1.04 | 12.532 | 7.443 | 1.684 | 6.274% | 169.2 | -1.4 | 12.612 | 7.348 | 11.2 | -0.075 | 1.716 | 6.442% | -1.76 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.075 | 610 | 159 | 0 | 450.4 | 159.6 | 173.8 | 14.2 | 0.26 | 13.963 | 7.863 | 1.776 | 5.372% | 172.9 | 0.4 | 12.912 | 7.763 | 13.3 | -0.075 | 1.663 | 5.735% | -1.5 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.075 | 765 | 332.3 | 70 | 360.7 | 334.3 | 343.4 | 9.1 | -0.05 | 9.175 | 7.241 | 1.267 | 10.51% | 344.4 | -0.1 | 10.241 | 7.144 | 10.1 | -0.075 | 1.433 | 9.471% | -4.13 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 530.1 | 275 | 0 | 126.1 | 404 | 410.8 | 6.8 | 1.6 | 5.219 | 7.66 | 0.681 | 9.879% | 421.2 | 2.2 | 14.977 | 6.7 | 17.2 | -0.069 | 2 | 3.546% | -2.97 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.076 | 582 | 235 | 0 | 344.9 | 237.1 | 241.1 | 4 | -1.91 | 5.977 | 11.103 | 0.538 | 18.44% | 240.7 | -2.7 | 6.262 | 9.756 | 3.6 | -0.069 | 0.642 | 18.6% | -8.33 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 238 | 175 | 0 | 25.9 | 212.1 | 217.8 | 5.7 | 0.12 | 5.502 | 3.439 | 1.6 | 5.294% | 217.6 | 0.2 | 5.293 | 3.008 | 5.5 | -0.069 | 1.759 | 4.982% | -4.88 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 459 | 300 | 0 | 104.5 | 354.5 | 365.6 | 11.1 | 0.49 | 10.556 | 6.633 | 1.592 | 5.24% | 365.3 | 0.7 | 10.087 | 5.802 | 10.8 | -0.069 | 1.739 | 4.89% | -4.16 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 293 | 145 | 24 | 31.3 | 237.7 | 243.1 | 5.4 | 0.18 | 5.171 | 3.887 | 1.33 | 6.878% | 245 | 0.2 | 7.039 | 3.4 | 7.3 | -0.069 | 2 | 4.62% | -4.12 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.076 | 455 | 330 | 0 | 113.1 | 341.9 | 349.5 | 7.6 | -0.83 | 8.431 | 6.51 | 1.295 | 7.587% | 352.8 | -1.2 | 12.025 | 5.72 | 10.9 | -0.069 | 2 | 4.803% | -3.97 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 270 | 185 | 0 | 84.7 | 185.3 | 192.7 | 7.4 | 0.55 | 6.823 | 3.544 | 1.925 | 4.625% | 191.1 | 0.8 | 5.087 | 3.114 | 5.8 | -0.069 | 1.634 | 5.358% | -4.04 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 244 | 150 | 18 | 67.2 | 158.8 | 162.3 | 3.5 | -0.83 | 4.307 | 3.266 | 1.319 | 8.839% | 167.2 | -1.1 | 9.549 | 2.857 | 8.4 | -0.069 | 2 | 3.344% | -2.39 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 168 | 54 | 39 | 28.3 | 100.7 | 100.7 | 0 | -0.24 | 0.316 | 1.864 | 0.17 | 0% | 99.8 | -0.3 | -0.529 | 1.631 | -0.9 | -0.069 | 0 | -21.5% | 14.14 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.076 | 625 | 300 | 0 | 108.6 | 516.4 | 537.3 | 20.9 | 1.06 | 19.774 | 10.297 | 1.92 | 3.789% | 538.1 | 1.5 | 20.208 | 9.047 | 21.7 | -0.069 | 2 | 3.314% | -3.01 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 629 | 463 | 42 | 113.2 | 473.8 | 489.2 | 15.4 | -0.23 | 15.651 | 8.482 | 1.845 | 5.175% | 489.1 | -0.3 | 15.626 | 7.42 | 15.3 | -0.069 | 2 | 4.73% | -3.92 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 508.1 | 342.1 | 0 | 89.4 | 418.7 | 429.5 | 10.8 | 0 | 10.81 | 7.342 | 1.472 | 5.962% | 430.3 | 0 | 11.599 | 6.422 | 11.6 | -0.069 | 1.806 | 5.04% | -4.57 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.076 | 577.4 | 150.4 | 0 | 98.7 | 478.7 | 490.4 | 11.7 | -0.32 | 12.078 | 7.985 | 1.513 | 6.253% | 489.6 | -0.4 | 11.393 | 7.016 | 10.9 | -0.069 | 1.624 | 6.094% | -5.56 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 577.4 | 150.4 | 0 | 98.7 | 478.7 | 490.4 | 11.7 | -0.32 | 12.078 | 7.985 | 1.513 | 6.253% | 489.6 | -0.4 | 11.393 | 7.016 | 10.9 | -0.069 | 1.624 | 6.094% | -5.56 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 578.4 | 150.5 | 0 | 89.1 | 489.3 | 501.6 | 12.3 | -0.75 | 13.018 | 7.968 | 1.634 | 5.959% | 500.4 | -1 | 12.107 | 7.001 | 11.1 | -0.069 | 1.729 | 5.995% | -5.58 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 578.4 | 150.5 | 0 | 89.1 | 489.3 | 501.6 | 12.3 | -0.75 | 13.018 | 7.968 | 1.634 | 5.959% | 500.4 | -1 | 12.107 | 7.001 | 11.1 | -0.069 | 1.729 | 5.995% | -5.58 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 903.7 | 460 | 47.5 | 39.5 | 816.7 | 837.8 | 21.1 | 1.77 | 19.328 | 12.372 | 1.562 | 5.426% | 844 | 2.5 | 24.823 | 10.822 | 27.3 | -0.069 | 2 | 3.808% | -3.79 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 903.6 | 461 | 53.2 | 47.7 | 802.7 | 823.8 | 21.1 | 1.77 | 19.328 | 12.29 | 1.573 | 5.426% | 831 | 2.5 | 25.823 | 10.75 | 28.3 | -0.069 | 2 | 3.673% | -3.59 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.076 | 218 | 150 | 5 | 42.7 | 170.3 | 175.8 | 5.5 | 0.38 | 5.125 | 3.382 | 1.515 | 5.026% | 175.6 | 0.5 | 4.774 | 2.972 | 5.3 | -0.069 | 1.607 | 4.736% | -4.06 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.076 | 224 | 155 | 12 | 42.6 | 169.4 | 174.8 | 5.4 | 0.3 | 5.166 | 3.356 | 1.539 | 5.26% | 174.9 | 0.4 | 5.109 | 2.949 | 5.5 | -0.069 | 1.733 | 4.689% | -3.9 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.076 | 226 | 150 | 12 | 42.8 | 171.2 | 176.8 | 5.6 | 0.14 | 5.532 | 3.407 | 1.624 | 5.117% | 176.4 | 0.2 | 5.077 | 2.994 | 5.2 | -0.069 | 1.696 | 5.004% | -4.16 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.076 | 222 | 150 | 5 | 43.7 | 173.3 | 178.7 | 5.4 | 0.35 | 5.031 | 3.479 | 1.446 | 5.213% | 178.7 | 0.5 | 4.885 | 3.057 | 5.4 | -0.069 | 1.598 | 4.733% | -4.06 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 188.1 | 0 | 40 | 85.6 | 62.5 | 62 | -0.5 | -7.79 | 7.288 | 2.14 | 2 | -47.71% | 58.6 | -10.8 | 6.975 | 1.872 | -3.9 | -0.069 | 2 | -5.554% | 2.02 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 271 | 164 | 55 | 39.5 | 176.5 | 180 | 3.5 | -0.86 | 4.428 | 3.121 | 1.419 | 9.816% | 184.8 | -1.2 | 9.475 | 2.73 | 8.3 | -0.069 | 2 | 3.758% | -2.69 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.076 | 650 | 358 | 0 | 150.9 | 499.1 | 506.9 | 7.8 | -4.18 | 11.977 | 9.296 | 1.288 | 10.56% | 508.6 | -5.8 | 15.315 | 8.168 | 9.5 | -0.069 | 1.875 | 7.871% | -6.65 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 270 | 190 | 7 | 30.5 | 232.5 | 240.4 | 7.9 | 0.59 | 7.273 | 3.8 | 1.914 | 4.333% | 237.2 | 0.8 | 3.836 | 3.324 | 4.7 | -0.069 | 1.154 | 6.612% | -6.26 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 254 | 182 | 0 | 49.8 | 204.2 | 209.6 | 5.4 | 0.41 | 4.982 | 3.67 | 1.357 | 5.963% | 210.3 | 0.6 | 5.482 | 3.21 | 6.1 | -0.069 | 1.708 | 4.793% | -4.24 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 540 | 319.5 | 30.2 | 18.8 | 491 | 499.3 | 8.3 | 0.59 | 7.723 | 7.367 | 1.048 | 8.244% | 499 | 0.8 | 7.179 | 6.444 | 8 | -0.069 | 1.114 | 7.766% | -7.77 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 522.5 | 305.2 | 22 | 10.5 | 490 | 500.3 | 10.3 | 0 | 10.25 | 7.232 | 1.417 | 6.428% | 500 | 0 | 10 | 6.326 | 10 | -0.069 | 1.581 | 6.012% | -6.2 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.076 | 233 | 150 | 12 | 43.6 | 177.4 | 182.3 | 4.9 | 0.32 | 4.601 | 3.151 | 1.46 | 6.029% | 182.7 | 0.5 | 4.906 | 2.769 | 5.3 | -0.069 | 1.772 | 5.061% | -4.23 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.076 | 230 | 150 | 12 | 55.2 | 162.8 | 167.2 | 4.4 | -0.21 | 4.621 | 3.015 | 1.533 | 6.628% | 169.9 | -0.3 | 7.415 | 2.649 | 7.1 | -0.069 | 2 | 3.729% | -2.9 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.076 | 233 | 150 | 12 | 43.7 | 177.3 | 182.7 | 5.4 | 0.35 | 5.089 | 3.149 | 1.616 | 5.471% | 182.4 | 0.5 | 4.654 | 2.767 | 5.1 | -0.069 | 1.682 | 5.259% | -4.4 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.076 | 371 | 225 | 0 | 75.1 | 295.9 | 306 | 10.1 | 1.12 | 8.907 | 5.361 | 1.661 | 4.656% | 308.8 | 1.6 | 11.312 | 4.689 | 12.9 | -0.069 | 2 | 3.31% | -2.9 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 690 | 420 | 0 | 26 | 664 | 680.6 | 16.6 | -0.47 | 17.151 | 9.971 | 1.72 | 5.267% | 680.8 | -0.7 | 17.542 | 8.721 | 16.8 | -0.069 | 2 | 4.725% | -5 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.076 | 395 | 220 | 0 | 64.1 | 330.9 | 340.6 | 9.7 | 0.12 | 9.569 | 7.292 | 1.312 | 5.161% | 339.6 | 0.2 | 8.536 | 6.407 | 8.7 | -0.069 | 1.332 | 5.225% | -4.81 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.076 | 78 | 57 | 0 | 20.6 | 57.4 | 59.3 | 1.9 | -0.01 | 1.967 | 1.329 | 1.48 | 5.215% | 59.2 | 0 | 1.832 | 1.148 | 1.8 | -0.069 | 1.595 | 4.999% | -4.02 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.076 | 590 | 155 | 0 | 309.5 | 280.5 | 293.1 | 12.6 | 1.11 | 11.496 | 10.021 | 1.147 | 5.933% | 292.6 | 1.5 | 10.628 | 8.805 | 12.1 | -0.069 | 1.207 | 5.61% | -2.93 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.076 | 577 | 155 | 0 | 250.6 | 326.4 | 337.3 | 10.9 | 0.66 | 10.334 | 9.398 | 1.1 | 6.708% | 337.6 | 0.9 | 10.362 | 8.258 | 11.2 | -0.069 | 1.255 | 5.927% | -3.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.076 | 610 | 159 | 0 | 212.2 | 397.8 | 408.6 | 10.8 | 0.55 | 10.243 | 9.61 | 1.066 | 7.157% | 409.4 | 0.8 | 10.834 | 8.444 | 11.6 | -0.069 | 1.283 | 6.05% | -4.34 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 707 | 300 | 40 | 65.7 | 601.3 | 619.1 | 17.8 | 1.73 | 16.154 | 9.639 | 1.676 | 5.033% | 619 | 2.4 | 15.386 | 8.431 | 17.7 | -0.069 | 1.825 | 4.595% | -4.3 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.078 | 522 | 275 | 0 | 120.8 | 401.2 | 405.7 | 4.5 | -0.24 | 4.735 | 5.969 | 0.793 | 15.09% | 413.4 | -0.3 | 12.515 | 5.914 | 12.2 | -0.078 | 2 | 5.565% | -4.27 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.078 | 552 | 235 | 0 | 313.4 | 238.6 | 244.4 | 5.8 | -0.37 | 6.162 | 8.402 | 0.733 | 12.38% | 242.4 | -0.5 | 4.328 | 8.327 | 3.8 | -0.078 | 0.52 | 18.89% | -8.16 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.078 | 459 | 300 | 0 | 95 | 364 | 377.7 | 13.7 | -0.57 | 14.225 | 5.249 | 2 | 4.358% | 377.1 | -0.8 | 13.846 | 5.2 | 13.1 | -0.078 | 2 | 4.557% | -3.61 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.078 | 565 | 135 | 0 | 415.5 | 149.5 | 153.9 | 4.4 | -0.32 | 4.732 | 6.45 | 0.734 | 16.7% | 159.1 | -0.4 | 10.066 | 6.393 | 9.6 | -0.078 | 1.575 | 7.654% | -2.02 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.078 | 500 | 300 | 0 | 195.3 | 304.7 | 318.3 | 13.6 | 1.25 | 12.435 | 5.48 | 2 | 4.781% | 319.1 | 1.7 | 12.747 | 5.431 | 14.4 | -0.078 | 2 | 4.516% | -2.75 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.078 | 231 | 168 | 12 | 43.3 | 175.7 | 179.8 | 4.1 | -0.18 | 4.281 | 2.504 | 1.71 | 7.331% | 179.1 | -0.2 | 3.632 | 2.481 | 3.4 | -0.078 | 1.464 | 8.841% | -6.71 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.078 | 239 | 150 | 18 | 21 | 200 | 204.9 | 4.9 | 0 | 4.938 | 2.527 | 1.954 | 6.347% | 204.8 | 0 | 4.8 | 2.504 | 4.8 | -0.078 | 1.917 | 6.479% | -5.41 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.078 | 245 | 172 | 0 | 66 | 179 | 182.8 | 3.8 | 0.1 | 3.711 | 2.802 | 1.325 | 8.389% | 183 | 0.1 | 3.856 | 2.775 | 4 | -0.078 | 1.389 | 7.97% | -5.81 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.078 | 626 | 450 | 49 | 95.4 | 481.6 | 492.9 | 11.3 | -1.37 | 12.702 | 6.598 | 1.925 | 7.204% | 493.6 | -1.9 | 13.912 | 6.537 | 12 | -0.078 | 2 | 6.784% | -5.21 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.078 | 320 | 50 | 0 | 268 | 52 | 67.9 | 15.9 | -0.16 | 16.101 | 3.471 | 2 | 2.618% | 68.1 | -0.2 | 16.401 | 3.44 | 16.1 | -0.078 | 2 | 2.586% | -0.42 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.078 | 327 | 150 | 11 | 43.2 | 272.8 | 280 | 7.2 | 0.49 | 6.728 | 3.614 | 1.862 | 5.908% | 279.8 | 0.7 | 6.4 | 3.58 | 7 | -0.078 | 1.788 | 6.077% | -5.06 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.078 | 532.8 | 352.1 | 0 | 45.8 | 487 | 498.7 | 11.7 | 0.04 | 11.677 | 6.092 | 1.917 | 5.922% | 500.1 | 0.1 | 13.044 | 6.036 | 13.1 | -0.078 | 2 | 5.289% | -4.83 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.078 | 578.1 | 176.1 | 0 | 187.9 | 390.2 | 400.8 | 10.6 | -0.21 | 10.737 | 6.56 | 1.637 | 7.093% | 399.4 | -0.3 | 9.476 | 6.501 | 9.2 | -0.078 | 1.458 | 8.172% | -5.51 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.078 | 578.1 | 176.1 | 0 | 187.9 | 390.2 | 400.8 | 10.6 | -0.21 | 10.737 | 6.56 | 1.637 | 7.093% | 399.4 | -0.3 | 9.476 | 6.501 | 9.2 | -0.078 | 1.458 | 8.172% | -5.51 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.078 | 579.2 | 176.2 | 0 | 188.9 | 390.3 | 401.1 | 10.8 | -0.42 | 11.258 | 6.57 | 1.713 | 6.974% | 400.1 | -0.6 | 10.44 | 6.512 | 9.8 | -0.078 | 1.603 | 7.686% | -5.17 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.078 | 579.2 | 176.2 | 0 | 188.9 | 390.3 | 401.1 | 10.8 | -0.42 | 11.258 | 6.57 | 1.713 | 6.974% | 400.1 | -0.6 | 10.44 | 6.512 | 9.8 | -0.078 | 1.603 | 7.686% | -5.17 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.078 | 428.6 | 180.3 | 0 | 21 | 407.6 | 414.4 | 6.8 | -0.04 | 6.884 | 6.524 | 1.055 | 8.198% | 414.9 | -0.1 | 7.41 | 6.465 | 7.3 | -0.078 | 1.146 | 7.636% | -7.25 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.078 | 231 | 150 | 22 | 41.8 | 167.2 | 172.3 | 5.1 | 0.29 | 4.803 | 2.622 | 1.832 | 5.894% | 172 | 0.4 | 4.429 | 2.598 | 4.8 | -0.078 | 1.704 | 6.262% | -4.52 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.078 | 237 | 155 | 29 | 40.9 | 167.1 | 172.4 | 5.3 | 0.3 | 5.035 | 2.609 | 1.93 | 5.819% | 171.9 | 0.4 | 4.365 | 2.585 | 4.8 | -0.078 | 1.689 | 6.425% | -4.52 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.078 | 239 | 150 | 29 | 42 | 168 | 173.4 | 5.4 | 0.01 | 5.423 | 2.641 | 2 | 5.759% | 173.2 | 0 | 5.206 | 2.618 | 5.2 | -0.078 | 1.989 | 5.98% | -4.19 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.078 | 235 | 150 | 21 | 41.9 | 172.1 | 177.3 | 5.2 | 0.05 | 5.173 | 2.727 | 1.897 | 5.88% | 177.1 | 0.1 | 4.884 | 2.702 | 5 | -0.078 | 1.807 | 6.116% | -4.47 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.078 | 181.9 | 0 | 40 | 11.8 | 130.1 | 134.3 | 4.2 | -0.09 | 4.226 | 1.623 | 2 | 5.637% | 132.3 | -0.1 | 2.263 | 1.608 | 2.2 | -0.078 | 1.408 | 10.76% | -7.67 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.078 | 273 | 164 | 55 | 41.7 | 176.3 | 179.5 | 3.2 | 0.09 | 3.122 | 2.493 | 1.253 | 11.1% | 179.7 | 0.1 | 3.239 | 2.47 | 3.4 | -0.078 | 1.311 | 10.45% | -6.73 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.078 | 831 | 358 | 0 | 470.5 | 360.5 | 382.3 | 21.8 | 0.92 | 20.816 | 9.648 | 2 | 4.957% | 383.8 | 1.3 | 21.974 | 9.562 | 23.3 | -0.078 | 2 | 4.638% | -2.01 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.078 | 844 | 451 | 0 | 390 | 454 | 460.4 | 6.4 | 0.49 | 5.877 | 9.956 | 0.59 | 17.15% | 461.4 | 0.7 | 6.709 | 9.867 | 7.4 | -0.078 | 0.68 | 14.83% | -7.97 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.078 | 542 | 319.5 | 35.1 | 44.9 | 462 | 472.2 | 10.2 | 0.59 | 9.598 | 5.796 | 1.656 | 6.911% | 471 | 0.8 | 8.179 | 5.742 | 9 | -0.078 | 1.424 | 7.832% | -6.67 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.078 | 541.4 | 305.2 | 37.5 | 41.9 | 462 | 472.7 | 10.7 | 0.59 | 10.098 | 5.762 | 1.752 | 6.58% | 471 | 0.8 | 8.179 | 5.708 | 9 | -0.078 | 1.433 | 7.823% | -6.67 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.078 | 247 | 150 | 32 | 42.8 | 172.2 | 177.1 | 4.9 | 0.13 | 4.754 | 2.381 | 1.997 | 6.559% | 177 | 0.2 | 4.591 | 2.36 | 4.8 | -0.078 | 1.946 | 6.695% | -4.66 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.078 | 247 | 150 | 33 | 42 | 172 | 177.2 | 5.2 | 0.12 | 5.096 | 2.366 | 2 | 6.18% | 177.2 | 0.2 | 5.018 | 2.345 | 5.2 | -0.078 | 2 | 6.18% | -4.29 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.078 | 247 | 150 | 33 | 53.4 | 160.6 | 168.3 | 7.7 | 2.38 | 5.304 | 2.331 | 2 | 4.174% | 169.3 | 3.3 | 5.384 | 2.311 | 8.7 | -0.078 | 2 | 3.694% | -2.4 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.078 | 190 | 40 | 0 | 139.2 | 50.8 | 54.6 | 3.8 | -1.74 | 5.576 | 2.787 | 2 | 6.507% | 56.1 | -2.4 | 7.693 | 2.762 | 5.3 | -0.078 | 2 | 4.666% | -1.24 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.078 | 653 | 430 | 23 | 94.1 | 535.9 | 543.5 | 7.6 | 0.94 | 6.626 | 7.204 | 0.92 | 11.17% | 550.8 | 1.3 | 13.544 | 7.137 | 14.9 | -0.078 | 1.898 | 5.699% | -4.67 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.078 | 311 | 134 | 77.3 | 35.8 | 197.9 | 212.8 | 14.9 | 6.56 | 8.31 | 2.672 | 2 | 2.715% | 217.9 | 9.1 | 10.827 | 2.648 | 20 | -0.078 | 2 | 2.023% | -1.28 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.078 | 236 | 147 | 28 | 60.5 | 147.5 | 150.4 | 2.9 | -0.26 | 3.179 | 2.378 | 1.337 | 10.59% | 153.4 | -0.4 | 6.286 | 2.356 | 5.9 | -0.078 | 2 | 5.205% | -3.25 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.078 | 747.1 | 459.4 | 0 | 282.9 | 464.2 | 482.7 | 18.5 | 1.48 | 17.014 | 8.543 | 1.992 | 5.251% | 483.6 | 2.1 | 17.362 | 8.464 | 19.4 | -0.078 | 2 | 5.008% | -3.11 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.078 | 727.7 | 425.2 | 0 | 181.6 | 546.1 | 562.6 | 16.5 | 1.42 | 15.047 | 8.321 | 1.808 | 5.735% | 571.9 | 2 | 23.787 | 8.244 | 25.8 | -0.078 | 2 | 3.668% | -2.75 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.078 | 731.1 | 425.3 | 0 | 222.2 | 508.9 | 526.2 | 17.3 | 0.83 | 16.493 | 8.36 | 1.973 | 5.495% | 531.6 | 1.1 | 21.551 | 8.282 | 22.7 | -0.078 | 2 | 4.188% | -2.91 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.078 | 50 | 24 | 0 | 24.5 | 25.5 | 28.1 | 2.6 | -0.19 | 2.755 | 0.675 | 2 | 2.511% | 28.9 | -0.3 | 3.665 | 0.668 | 3.4 | -0.078 | 2 | 1.92% | -0.97 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.078 | 375 | 225 | 17.8 | 113.1 | 244.1 | 254.6 | 10.5 | -2.01 | 12.479 | 4.085 | 2 | 4.646% | 268 | -2.8 | 26.677 | 4.047 | 23.9 | -0.078 | 2 | 2.041% | -1.33 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.078 | 690 | 420 | 0 | 92.7 | 597.3 | 621.7 | 24.4 | 1.77 | 22.591 | 7.89 | 2 | 3.677% | 621.4 | 2.5 | 21.604 | 7.817 | 24.1 | -0.078 | 2 | 3.723% | -3.22 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.078 | 78 | 57 | 0 | 20.6 | 57.4 | 59.4 | 2 | 0.02 | 2.03 | 1.053 | 1.928 | 5.084% | 59.1 | 0 | 1.716 | 1.042 | 1.7 | -0.078 | 1.646 | 5.981% | -4.37 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.078 | 78 | 57 | 0 | 19.6 | 58.4 | 60.2 | 1.8 | 0.01 | 1.856 | 1.053 | 1.763 | 5.649% | 59.9 | 0 | 1.513 | 1.042 | 1.5 | -0.078 | 1.451 | 6.779% | -5.04 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.078 | 865 | 460 | 123.2 | 41.6 | 700.2 | 715.6 | 15.4 | 3.66 | 11.712 | 8.483 | 1.381 | 7.304% | 721.1 | 5.1 | 15.809 | 8.404 | 20.9 | -0.078 | 1.881 | 5.382% | -4.35 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.078 | 659 | 155 | 0 | 145.4 | 513.6 | 528.3 | 14.7 | -0.04 | 14.75 | 8.048 | 1.833 | 5.83% | 527.6 | -0.1 | 14.047 | 7.976 | 14 | -0.078 | 1.761 | 6.121% | -4.77 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.078 | 377 | 156 | 0 | 59.1 | 317.9 | 330.9 | 13 | -0.44 | 13.424 | 5.035 | 2 | 3.772% | 330.6 | -0.6 | 13.314 | 4.99 | 12.7 | -0.078 | 2 | 3.861% | -3.25 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.078 | 577 | 159 | 0 | 368.3 | 208.7 | 222.9 | 14.2 | 0.12 | 14.086 | 7.935 | 1.775 | 5.284% | 222.4 | 0.2 | 13.477 | 7.864 | 13.7 | -0.078 | 1.714 | 5.477% | -1.98 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.078 | 610 | 159 | 0 | 251.8 | 358.2 | 367.7 | 9.5 | 0.81 | 8.69 | 7.83 | 1.11 | 8.35% | 367.4 | 1.1 | 8.088 | 7.76 | 9.2 | -0.078 | 1.042 | 8.623% | -5.06 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.078 | 704 | 300 | 40 | 334 | 330 | 340.8 | 10.8 | -5.19 | 15.953 | 7.593 | 2 | 8.477% | 342.1 | -7.2 | 19.358 | 7.523 | 12.1 | -0.078 | 2 | 7.566% | -3.54 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.107 | 539.6 | 275 | 0 | 122.8 | 416.8 | 424.1 | 7.3 | -2.54 | 9.832 | 10.525 | 0.934 | 13.19% | 435.6 | -3.5 | 22.361 | 10.074 | 18.8 | -0.104 | 2 | 4.977% | -3.95 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.107 | 459 | 300 | 0 | 46 | 413 | 426.3 | 13.3 | 2.29 | 11.03 | 8.953 | 1.232 | 6.157% | 426.5 | 3.2 | 10.39 | 8.569 | 13.5 | -0.104 | 1.213 | 5.895% | -5.45 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.107 | 600 | 405 | 0 | 163.1 | 436.9 | 451.3 | 14.4 | -0.59 | 15.034 | 11.033 | 1.363 | 7.433% | 458.4 | -0.8 | 22.348 | 10.572 | 21.5 | -0.104 | 2 | 4.839% | -3.62 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.107 | 353 | 125 | 0 | 219 | 134 | 139.3 | 5.3 | -0.06 | 5.441 | 6.291 | 0.865 | 11.88% | 139 | -0.1 | 5.116 | 6.028 | 5 | -0.104 | 0.849 | 12.24% | -4.77 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.107 | 420 | 125 | 0 | 280.4 | 139.6 | 151 | 11.4 | 1.49 | 9.884 | 7.438 | 1.329 | 6.573% | 150.7 | 2.1 | 8.982 | 7.127 | 11.1 | -0.104 | 1.26 | 6.561% | -2.24 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.107 | 234 | 168 | 12 | 45.2 | 176.8 | 182.9 | 6.1 | 0 | 6.095 | 4.33 | 1.408 | 6.846% | 182.2 | 0 | 5.436 | 4.145 | 5.4 | -0.104 | 1.312 | 7.516% | -5.83 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.107 | 242 | 150 | 18 | 52.8 | 171.2 | 172 | 0.8 | -4.07 | 4.88 | 4.369 | 1.117 | 53.98% | 173.4 | -5.7 | 7.915 | 4.182 | 2.2 | -0.104 | 1.893 | 19.08% | -13.86 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.107 | 399 | 290 | 0 | 105.9 | 293.1 | 301.9 | 8.8 | 2.23 | 6.619 | 7.782 | 0.85 | 8.089% | 302.6 | 3.1 | 6.405 | 7.449 | 9.5 | -0.104 | 0.86 | 7.283% | -5.5 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.107 | 635 | 300 | 0 | 80.2 | 554.8 | 578.8 | 24 | 1.65 | 22.406 | 13.86 | 1.617 | 4.72% | 579.6 | 2.3 | 22.537 | 13.281 | 24.8 | -0.104 | 1.697 | 4.439% | -3.99 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.107 | 105 | 12 | 0 | 92.8 | 12.2 | 15.3 | 3.1 | 0.22 | 2.817 | 2.654 | 1.061 | 6.049% | 14.9 | 0.3 | 2.387 | 2.543 | 2.7 | -0.104 | 0.939 | 6.751% | -0.8 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.107 | 320 | 50 | 0 | 218.9 | 101.1 | 122.4 | 21.3 | 1.81 | 19.582 | 5.619 | 2 | 2.681% | 125.6 | 2.5 | 22.026 | 5.384 | 24.5 | -0.104 | 2 | 2.265% | -0.73 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.107 | 350 | 268 | 0 | 13.5 | 336.5 | 342.9 | 6.4 | 0.65 | 5.736 | 6.827 | 0.84 | 9.757% | 340.3 | 0.9 | 2.925 | 6.534 | 3.8 | -0.104 | 0.448 | 15.97% | -15.78 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.107 | 229 | 150 | 22 | 40.4 | 166.6 | 173.5 | 6.9 | 0.22 | 6.687 | 4.35 | 1.537 | 5.923% | 173.6 | 0.3 | 6.678 | 4.168 | 7 | -0.104 | 1.602 | 5.675% | -4.24 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.107 | 236 | 155 | 29 | 40.1 | 166.9 | 173.5 | 6.6 | 0.32 | 6.369 | 4.353 | 1.463 | 6.381% | 173.4 | 0.5 | 6.049 | 4.171 | 6.5 | -0.104 | 1.45 | 6.298% | -4.57 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.107 | 232 | 150 | 21 | 14.1 | 196.9 | 203.3 | 6.4 | 0.31 | 6.092 | 4.862 | 1.253 | 6.469% | 203.6 | 0.4 | 6.304 | 4.659 | 6.7 | -0.104 | 1.353 | 6.006% | -5.24 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.107 | 435 | 120 | 0 | 314.7 | 120.3 | 134.3 | 14 | 1.02 | 12.988 | 10.115 | 1.284 | 5.543% | 133.3 | 1.4 | 11.544 | 9.692 | 13 | -0.104 | 1.191 | 5.802% | -1.65 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.107 | 195.2 | 2.7 | 40 | 16.3 | 138.9 | 147 | 8.1 | 0.09 | 8.072 | 3.027 | 2 | 4.301% | 144.1 | 0.1 | 5.071 | 2.897 | 5.2 | -0.104 | 1.75 | 6.512% | -4.76 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.107 | 247 | 150 | 22 | 44.1 | 180.9 | 186.9 | 6 | 0.37 | 5.667 | 4.303 | 1.317 | 7.346% | 187.6 | 0.5 | 6.194 | 4.123 | 6.7 | -0.104 | 1.502 | 6.394% | -4.81 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.107 | 247 | 150 | 23 | 44.1 | 179.9 | 186.5 | 6.6 | 0.12 | 6.429 | 4.27 | 1.506 | 6.678% | 186.9 | 0.2 | 6.859 | 4.091 | 7 | -0.104 | 1.677 | 6.12% | -4.58 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.107 | 247 | 150 | 21 | 44.2 | 181.8 | 188.4 | 6.6 | 0.23 | 6.373 | 4.332 | 1.471 | 6.678% | 189.1 | 0.3 | 6.966 | 4.151 | 7.3 | -0.104 | 1.678 | 5.869% | -4.44 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.107 | 260 | 150 | 16 | 11.6 | 232.4 | 234.8 | 2.4 | 0.75 | 1.632 | 5.094 | 0.32 | 19.33% | 234.9 | 1 | 1.399 | 4.881 | 2.5 | -0.104 | 0.287 | 18.04% | -16.57 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.107 | 190 | 40 | 0 | 139.5 | 50.5 | 55.6 | 5.1 | -3.07 | 8.238 | 4.673 | 1.763 | 6.649% | 56.8 | -4.3 | 10.589 | 4.477 | 6.3 | -0.104 | 2 | 5.232% | -1.43 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.107 | 743.3 | 462.7 | 0 | 97.6 | 645.7 | 671.6 | 25.9 | 1.3 | 24.609 | 14.498 | 1.697 | 5.119% | 673.9 | 1.8 | 26.401 | 13.877 | 28.2 | -0.104 | 1.903 | 4.57% | -4.08 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.107 | 730 | 434.6 | 0 | 146.5 | 583.5 | 605.7 | 22.2 | 1.77 | 20.387 | 14.239 | 1.432 | 5.865% | 616.8 | 2.5 | 30.844 | 13.629 | 33.3 | -0.104 | 2 | 3.801% | -3.12 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.107 | 49.7 | 24 | 0 | 23.2 | 26.5 | 27.4 | 0.9 | -0.86 | 1.714 | 1.141 | 1.502 | 9.879% | 32 | -1.2 | 6.701 | 1.088 | 5.5 | -0.104 | 2 | 1.571% | -0.85 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.107 | 383 | 225 | 17.7 | 111.3 | 254 | 267.6 | 13.6 | -0.18 | 13.768 | 7.125 | 1.932 | 5.024% | 271.1 | -0.2 | 17.346 | 6.82 | 17.1 | -0.104 | 2 | 3.884% | -2.65 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.107 | 225.6 | 170 | 20 | 7.8 | 197.8 | 201.8 | 4 | -0.24 | 4.249 | 4.01 | 1.06 | 10.07% | 203.6 | -0.3 | 6.157 | 3.838 | 5.8 | -0.104 | 1.604 | 6.747% | -6.08 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.107 | 502 | 35 | 0 | 466.7 | 35.3 | 45.9 | 10.6 | 1.23 | 9.36 | 8.893 | 1.052 | 8.451% | 41.6 | 1.7 | 4.589 | 8.414 | 6.3 | -0.104 | 0.545 | 13.82% | -0.99 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.107 | 244.7 | 130 | 0 | 46 | 198.7 | 204.7 | 6 | 0.43 | 5.554 | 4.773 | 1.164 | 7.278% | 203.3 | 0.6 | 4.021 | 4.568 | 4.6 | -0.104 | 0.88 | 9.227% | -7.7 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.107 | 701 | 300 | 40 | 289.8 | 371.2 | 384.9 | 13.7 | -5.19 | 18.903 | 12.894 | 1.466 | 9.127% | 386.1 | -7.2 | 22.079 | 12.341 | 14.9 | -0.104 | 1.789 | 8.157% | -4.44 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.095 | 220 | 62 | 0 | 74.3 | 145.7 | 148.8 | 3.1 | -0.27 | 3.385 | 3.194 | 1.06 | 11.25% | 152.9 | -0.4 | 7.526 | 3.338 | 7.2 | -0.097 | 2 | 4.948% | -3.2 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.095 | 560 | 400 | 0 | 25.2 | 534.8 | 538.2 | 3.4 | -0.21 | 3.576 | 11.423 | 0.313 | 26.09% | 544.6 | -0.3 | 10.112 | 11.786 | 9.8 | -0.097 | 0.858 | 9.241% | -8.64 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.095 | 635 | 300 | 0 | 29.5 | 605.5 | 618.3 | 12.8 | 0 | 12.791 | 10.979 | 1.165 | 7.857% | 623.9 | 0 | 18.429 | 11.328 | 18.4 | -0.097 | 1.627 | 5.581% | -5.21 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.095 | 322 | 185 | 11 | 96 | 215 | 223.1 | 8.1 | 0.05 | 8.05 | 4.822 | 1.669 | 6.298% | 225.3 | 0.1 | 10.238 | 4.98 | 10.3 | -0.097 | 2 | 5.057% | -3.3 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.095 | 515.2 | 344.9 | 0 | 94.9 | 420.3 | 431 | 10.7 | -1.79 | 12.476 | 7.988 | 1.562 | 7.626% | 440.9 | -2.5 | 23.041 | 8.249 | 20.6 | -0.097 | 2 | 4.045% | -3.23 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.095 | 225.3 | 180 | 0 | 23.2 | 202.1 | 203.4 | 1.3 | 0.1 | 1.212 | 2.125 | 0.57 | 27.48% | 204.2 | 0.1 | 1.985 | 2.221 | 2.1 | -0.097 | 0.894 | 17.37% | -15.21 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.095 | 225.3 | 180 | 0 | 23.2 | 202.1 | 203.4 | 1.3 | 0.1 | 1.212 | 2.125 | 0.57 | 27.48% | 204.2 | 0.1 | 1.985 | 2.221 | 2.1 | -0.097 | 0.894 | 17.37% | -15.21 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.095 | 225.3 | 180 | 0 | 23.2 | 202.1 | 203.4 | 1.3 | 0.1 | 1.212 | 2.125 | 0.57 | 27.48% | 204.2 | 0.1 | 1.985 | 2.221 | 2.1 | -0.097 | 0.894 | 17.37% | -15.21 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.095 | 225.3 | 180 | 0 | 23.2 | 202.1 | 203.4 | 1.3 | 0.1 | 1.212 | 2.125 | 0.57 | 27.48% | 204.2 | 0.1 | 1.985 | 2.221 | 2.1 | -0.097 | 0.894 | 17.37% | -15.21 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.095 | 390 | 36 | 0 | 284.7 | 105.3 | 107.6 | 2.3 | -0.3 | 2.613 | 5.059 | 0.516 | 26.87% | 106.4 | -0.4 | 1.513 | 5.287 | 1.1 | -0.097 | 0.286 | 57.37% | -15.11 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.095 | 235 | 155 | 29 | 31.7 | 174.3 | 179.8 | 5.5 | 0.22 | 5.234 | 3.542 | 1.478 | 6.77% | 179.9 | 0.3 | 5.219 | 3.655 | 5.6 | -0.097 | 1.428 | 6.789% | -4.92 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.095 | 375 | 100 | 0 | 175.5 | 199.5 | 214.2 | 14.7 | -1.3 | 16.002 | 3.961 | 2 | 4.043% | 215.1 | -1.8 | 17.362 | 4.139 | 15.6 | -0.097 | 2 | 3.89% | -2.02 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.095 | 435.5 | 268 | 40 | 52.8 | 342.7 | 350.8 | 8.1 | -0.09 | 8.249 | 6.132 | 1.345 | 8.516% | 349.3 | -0.1 | 6.737 | 6.333 | 6.6 | -0.097 | 1.064 | 10.67% | -8.22 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.095 | 600 | 305 | 120 | 60.3 | 419.7 | 425.3 | 5.6 | 0.1 | 5.508 | 7.442 | 0.74 | 16.97% | 423.2 | 0.1 | 3.42 | 7.686 | 3.5 | -0.097 | 0.445 | 27.72% | -18.98 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.095 | 100 | 53 | 0 | 21.8 | 78.2 | 82.8 | 4.6 | 0.23 | 4.371 | 1.827 | 2 | 3.448% | 83.1 | 0.3 | 4.601 | 1.892 | 4.9 | -0.097 | 2 | 3.305% | -2.52 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.095 | 523 | 45 | 0 | 249.7 | 273.3 | 277.9 | 4.6 | -0.33 | 4.891 | 8.737 | 0.56 | 18.01% | 278.8 | -0.5 | 5.992 | 9.015 | 5.5 | -0.097 | 0.665 | 15.38% | -7.86 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.095 | 237 | 150 | 22 | 55.4 | 159.6 | 165 | 5.4 | 0.02 | 5.454 | 3.167 | 1.722 | 6.954% | 167.1 | 0 | 7.508 | 3.267 | 7.5 | -0.097 | 2 | 5.112% | -3.37 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.095 | 237 | 150 | 23 | 54.3 | 159.7 | 165.1 | 5.4 | 0.09 | 5.383 | 3.15 | 1.709 | 6.954% | 167.5 | 0.1 | 7.683 | 3.25 | 7.8 | -0.097 | 2 | 4.916% | -3.24 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.095 | 237 | 150 | 21 | 56.3 | 159.7 | 165.1 | 5.4 | 0.2 | 5.199 | 3.183 | 1.633 | 6.954% | 167.5 | 0.3 | 7.531 | 3.284 | 7.8 | -0.097 | 2 | 4.916% | -3.24 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.095 | 245 | 150 | 16 | 69.7 | 159.3 | 165.5 | 6.2 | 0.19 | 6.024 | 3.236 | 1.862 | 6.261% | 168.2 | 0.3 | 8.638 | 3.338 | 8.9 | -0.097 | 2 | 4.454% | -2.83 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.095 | 728.7 | 454.1 | 0 | 99.6 | 629.1 | 647 | 17.9 | 0 | 17.927 | 11.298 | 1.587 | 6.447% | 651.4 | 0 | 22.343 | 11.668 | 22.3 | -0.097 | 1.915 | 5.284% | -4.47 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.095 | 716.4 | 465 | 0 | 102.4 | 614 | 627.6 | 13.6 | -0.06 | 13.641 | 11.108 | 1.228 | 8.343% | 639.4 | -0.1 | 25.489 | 11.471 | 25.4 | -0.097 | 2 | 4.561% | -3.83 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.095 | 723.3 | 465 | 0 | 101.4 | 621.9 | 637.3 | 15.4 | 1 | 14.427 | 11.215 | 1.286 | 7.438% | 649.3 | 1.4 | 26.019 | 11.582 | 27.4 | -0.097 | 2 | 4.269% | -3.59 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.095 | 49.8 | 24 | 0 | 14.8 | 35 | 36.2 | 1.2 | -0.08 | 1.279 | 0.91 | 1.406 | 6.594% | 37.5 | -0.1 | 2.584 | 0.942 | 2.5 | -0.097 | 2 | 3.232% | -2.21 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.095 | 49.8 | 24 | 0 | 15 | 34.8 | 36.4 | 1.6 | 0.15 | 1.44 | 0.909 | 1.584 | 4.946% | 37.1 | 0.2 | 2.134 | 0.941 | 2.3 | -0.097 | 2 | 3.513% | -2.38 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.095 | 368 | 225 | 11.5 | 73.5 | 283 | 293.7 | 10.7 | 0.47 | 10.245 | 5.528 | 1.853 | 5.448% | 296.3 | 0.7 | 12.629 | 5.708 | 13.3 | -0.097 | 2 | 4.475% | -3.37 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.095 | 113 | 45 | 0 | 30 | 83 | 87.9 | 4.9 | -0.67 | 5.631 | 1.752 | 2 | 3.657% | 89.7 | -0.9 | 7.668 | 1.809 | 6.7 | -0.097 | 2 | 2.731% | -1.96 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.095 | 938.2 | 359.1 | 0 | 80.8 | 857.4 | 871.1 | 13.7 | 0.46 | 13.287 | 13.84 | 0.96 | 10.85% | 872 | 0.6 | 14.003 | 14.28 | 14.6 | -0.097 | 0.981 | 10.39% | -9.3 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.095 | 938.2 | 359.1 | 0 | 80.8 | 857.4 | 871.1 | 13.7 | 0.46 | 13.287 | 13.84 | 0.96 | 10.85% | 872 | 0.6 | 14.003 | 14.28 | 14.6 | -0.097 | 0.981 | 10.39% | -9.3 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.095 | 938.2 | 359.1 | 0 | 80.8 | 857.4 | 871.1 | 13.7 | 0.46 | 13.287 | 13.84 | 0.96 | 10.85% | 872 | 0.6 | 14.003 | 14.28 | 14.6 | -0.097 | 0.981 | 10.39% | -9.3 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.095 | 938.2 | 359.1 | 0 | 80.8 | 857.4 | 871.1 | 13.7 | 0.46 | 13.287 | 13.84 | 0.96 | 10.85% | 872 | 0.6 | 14.003 | 14.28 | 14.6 | -0.097 | 0.981 | 10.39% | -9.3 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.095 | 502 | 35 | 0 | 420.1 | 81.9 | 83 | 1.1 | 0.37 | 0.759 | 6.661 | 0.114 | 72.31% | 83.5 | 0.5 | 1.137 | 6.961 | 1.6 | -0.097 | 0.163 | 50.76% | -8.07 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.095 | 235.3 | 130 | 0 | 79.2 | 156.1 | 158.2 | 2.1 | -3.37 | 5.568 | 3.648 | 1.526 | 17.75% | 162.4 | -4.7 | 11.083 | 3.768 | 6.3 | -0.097 | 2 | 6.043% | -3.92 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.095 | 246 | 60 | 0 | 7.2 | 238.8 | 239.7 | 0.9 | -0.22 | 1.108 | 3.272 | 0.339 | 43.34% | 240.3 | -0.3 | 1.815 | 3.419 | 1.5 | -0.097 | 0.531 | 26.55% | -25.17 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.095 | 686 | 300 | 40 | 151.6 | 494.4 | 514.7 | 20.3 | 0 | 20.343 | 10.017 | 2 | 5.352% | 512.1 | 0 | 17.687 | 10.345 | 17.7 | -0.097 | 1.71 | 6.267% | -4.42 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 536.5 | 275 | 0 | 198.3 | 338.2 | 362.8 | 24.6 | 2.89 | 21.751 | 6.768 | 2 | 2% | 367.3 | 4 | 25.067 | 6.359 | 29.1 | -0.052 | 2 | 1.599% | -1.06 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 238 | 176 | 18.6 | 23 | 196.4 | 200.4 | 4 | 0.3 | 3.788 | 2.768 | 1.369 | 5.461% | 201.1 | 0.4 | 4.325 | 2.6 | 4.7 | -0.052 | 1.663 | 4.395% | -3.82 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 533 | 373 | 49 | 41.7 | 442.3 | 448.6 | 6.3 | 0.3 | 5.991 | 6.106 | 0.981 | 7.76% | 450.3 | 0.4 | 7.575 | 5.737 | 8 | -0.052 | 1.32 | 5.778% | -5.06 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 459 | 300 | 0 | 132.2 | 326.8 | 341.2 | 14.4 | -0.96 | 15.401 | 5.79 | 2 | 2.924% | 340.6 | -1.3 | 15.215 | 5.44 | 13.8 | -0.052 | 2 | 2.885% | -2.17 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 190 | 135 | 13 | 40.1 | 136.9 | 139.2 | 2.3 | 0.71 | 1.594 | 2.233 | 0.714 | 7.585% | 139.9 | 1 | 2.008 | 2.098 | 3 | -0.052 | 0.957 | 5.498% | -4.17 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.055 | 560 | 135 | 0 | 421 | 139 | 143.3 | 4.3 | -0.08 | 4.337 | 7.027 | 0.617 | 11.94% | 145 | -0.1 | 6.116 | 6.617 | 6 | -0.052 | 0.924 | 8.094% | -2.12 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.055 | 420 | 125 | 0 | 283.2 | 136.8 | 141.3 | 4.5 | 0 | 4.533 | 4.898 | 0.926 | 8.562% | 142 | 0 | 5.183 | 4.612 | 5.2 | -0.052 | 1.124 | 7.005% | -2.41 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.055 | 420 | 125 | 0 | 282.4 | 137.6 | 147.7 | 10.1 | -0.12 | 10.224 | 4.881 | 2 | 3.815% | 146.1 | -0.2 | 8.703 | 4.597 | 8.5 | -0.052 | 1.893 | 4.286% | -1.48 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.055 | 236 | 168 | 12 | 55.7 | 168.3 | 172.5 | 4.2 | 0.3 | 3.89 | 2.826 | 1.377 | 5.158% | 176.4 | 0.4 | 7.697 | 2.655 | 8.1 | -0.052 | 2 | 2.529% | -1.9 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 244 | 150 | 18 | 68.8 | 157.2 | 158.9 | 1.7 | -0.12 | 1.833 | 2.851 | 0.643 | 13.17% | 160.3 | -0.2 | 3.236 | 2.679 | 3.1 | -0.052 | 1.208 | 6.831% | -4.64 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 369 | 189 | 37 | 12.5 | 319.5 | 320.6 | 1.1 | -0.94 | 2.105 | 4.188 | 0.503 | 30.78% | 319.8 | -1.3 | 1.649 | 3.935 | 0.3 | -0.052 | 0.419 | 106.7% | -97.53 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 641 | 483 | 32 | 120.2 | 488.8 | 501 | 12.2 | -0.62 | 12.842 | 7.682 | 1.672 | 4.819% | 501.6 | -0.9 | 13.644 | 7.218 | 12.8 | -0.052 | 1.89 | 4.342% | -3.5 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.055 | 105 | 12 | 0 | 92.2 | 12.8 | 14.6 | 1.8 | 0 | 1.808 | 1.74 | 1.039 | 5.363% | 14.4 | 0 | 1.58 | 1.638 | 1.6 | -0.052 | 0.964 | 5.705% | -0.72 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.055 | 535 | 314 | 33 | 72.6 | 429.4 | 433.3 | 3.9 | -0.24 | 4.186 | 6.333 | 0.661 | 12.58% | 434.6 | -0.3 | 5.557 | 5.95 | 5.2 | -0.052 | 0.934 | 8.922% | -7.56 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 38.1 | 5.4 | 3 | 28.3 | 6.8 | 14.7 | 7.9 | -0.2 | 8.105 | 0.442 | 2 | 0.4457% | 20 | -0.3 | 13.512 | 0.416 | 13.2 | -0.052 | 2 | 0.2523% | -0.05 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 220 | 153 | 0 | 20.6 | 199.4 | 200.1 | 0.7 | 0 | 0.709 | 2.775 | 0.255 | 28.85% | 199.7 | 0 | 0.271 | 2.608 | 0.3 | -0.052 | 0.104 | 63.65% | -60.83 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 333 | 189 | 11 | 64.5 | 257.5 | 265 | 7.5 | 0.1 | 7.333 | 4.062 | 1.805 | 4.074% | 266.2 | 0.1 | 8.58 | 3.817 | 8.7 | -0.052 | 2 | 3.32% | -2.71 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 532.8 | 352.1 | 0 | 60.9 | 471.9 | 483.3 | 11.4 | 1.82 | 9.566 | 6.721 | 1.423 | 4.287% | 485.9 | 2.5 | 11.392 | 6.315 | 14 | -0.052 | 1.804 | 3.3% | -3.09 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.055 | 584.5 | 172.1 | 0 | 342.2 | 242.3 | 258.2 | 15.9 | 2.12 | 13.8 | 7.086 | 1.947 | 3.372% | 259.6 | 3 | 14.344 | 6.673 | 17.3 | -0.052 | 2 | 2.93% | -1.28 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.055 | 584.5 | 172.1 | 0 | 342.2 | 242.3 | 258.2 | 15.9 | 2.12 | 13.8 | 7.086 | 1.947 | 3.372% | 259.6 | 3 | 14.344 | 6.673 | 17.3 | -0.052 | 2 | 2.93% | -1.28 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.055 | 594.1 | 171.7 | 0 | 314.9 | 279.2 | 289.4 | 10.2 | 1.38 | 8.808 | 7.559 | 1.165 | 5.342% | 293 | 1.9 | 11.952 | 7.119 | 13.8 | -0.052 | 1.679 | 3.733% | -1.85 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.055 | 594.1 | 171.7 | 0 | 314.9 | 279.2 | 289.4 | 10.2 | 1.38 | 8.808 | 7.559 | 1.165 | 5.342% | 293 | 1.9 | 11.952 | 7.119 | 13.8 | -0.052 | 1.679 | 3.733% | -1.85 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.055 | 427.6 | 180.3 | 0 | 171.7 | 255.9 | 268.2 | 12.3 | -0.09 | 12.336 | 6.505 | 1.896 | 3.189% | 269.8 | -0.1 | 14.006 | 6.127 | 13.9 | -0.052 | 2 | 2.668% | -1.69 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.055 | 484 | 272 | 0 | 17.4 | 466.6 | 470.2 | 3.6 | 0.41 | 3.243 | 6.106 | 0.531 | 12.33% | 470.3 | 0.6 | 3.175 | 5.737 | 3.7 | -0.052 | 0.554 | 11.34% | -11.55 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 480 | 264 | 0 | 45.6 | 434.4 | 438.2 | 3.8 | 0.89 | 2.867 | 6.055 | 0.473 | 11.59% | 436.2 | 1.2 | 0.533 | 5.689 | 1.8 | -0.052 | 0.094 | 23.13% | -22.11 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 928.3 | 461 | 150 | 23.8 | 754.5 | 769.7 | 15.2 | 0.59 | 14.629 | 9.817 | 1.49 | 5.6% | 772 | 0.8 | 16.679 | 9.224 | 17.5 | -0.052 | 1.808 | 4.599% | -3.95 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 411 | 215 | 80 | 113.7 | 217.3 | 218.2 | 0.9 | 0.6 | 0.352 | 4.176 | 0.084 | 41.89% | 217.3 | 0.8 | -0.832 | 3.923 | 0 | -0.052 | 0 | 0% |  | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 491 | 349 | 38 | 87.6 | 365.4 | 376.2 | 10.8 | 0.89 | 9.841 | 5.714 | 1.722 | 4.17% | 376.3 | 1.2 | 9.626 | 5.369 | 10.9 | -0.052 | 1.793 | 3.907% | -3.07 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.055 | 240 | 155 | 29 | 53.9 | 157.1 | 160 | 2.9 | 0.55 | 2.384 | 2.88 | 0.828 | 7.596% | 160.3 | 0.8 | 2.421 | 2.712 | 3.2 | -0.052 | 0.893 | 6.509% | -4.49 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 448.8 | 273 | 40 | 87.3 | 321.5 | 331.9 | 10.4 | -0.58 | 10.966 | 5.157 | 2 | 3.958% | 328.6 | -0.8 | 7.862 | 4.845 | 7.1 | -0.052 | 1.623 | 5.482% | -4.15 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 604 | 305 | 120 | 176.1 | 307.9 | 316.7 | 8.8 | 0.54 | 8.288 | 6.106 | 1.357 | 6.295% | 321.6 | 0.8 | 12.974 | 5.737 | 13.7 | -0.052 | 2 | 3.823% | -2.06 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 615 | 260 | 130 | 142.7 | 342.3 | 346.9 | 4.6 | 2.28 | 2.277 | 6.118 | 0.372 | 12.26% | 348.8 | 3.2 | 3.337 | 5.749 | 6.5 | -0.052 | 0.581 | 8.204% | -4.82 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 615 | 260 | 135 | 138.3 | 341.7 | 346.4 | 4.7 | 2.03 | 2.673 | 6.055 | 0.441 | 12% | 348.1 | 2.8 | 3.644 | 5.689 | 6.4 | -0.052 | 0.64 | 8.333% | -4.89 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.055 | 831 | 261 | 0 | 568.6 | 262.4 | 280.1 | 17.7 | 1.24 | 16.466 | 11.06 | 1.489 | 4.305% | 281.2 | 1.7 | 17.043 | 10.415 | 18.8 | -0.052 | 1.636 | 3.832% | -1.28 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.055 | 808 | 451 | 0 | 356.3 | 451.7 | 461.1 | 9.4 | -0.31 | 9.654 | 10.473 | 0.922 | 7.882% | 461.7 | -0.4 | 10.426 | 9.863 | 10 | -0.052 | 1.057 | 7.006% | -4.14 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.055 | 103 | 61 | 0 | 21.3 | 81.7 | 86.3 | 4.6 | 0 | 4.677 | 1.533 | 2 | 2.059% | 85.9 | 0 | 4.219 | 1.433 | 4.2 | -0.052 | 2 | 2.132% | -1.78 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 541.6 | 316.2 | 41.9 | 16.2 | 483.5 | 493.4 | 9.9 | 2.36 | 7.578 | 6.304 | 1.202 | 5.018% | 494 | 3.3 | 7.216 | 5.923 | 10.5 | -0.052 | 1.218 | 4.473% | -4.22 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 525 | 305.2 | 41.6 | 11.3 | 472.1 | 481.8 | 9.7 | 0.59 | 9.182 | 6.098 | 1.506 | 4.964% | 481 | 0.8 | 8.108 | 5.73 | 8.9 | -0.052 | 1.415 | 5.116% | -4.86 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.055 | 243 | 150 | 22 | 68.8 | 152.2 | 155.2 | 3 | 0.58 | 2.413 | 2.691 | 0.897 | 7.434% | 155.3 | 0.8 | 2.273 | 2.534 | 3.1 | -0.052 | 0.897 | 6.803% | -4.49 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.055 | 243 | 150 | 23 | 67.5 | 152.5 | 155.6 | 3.1 | 0.5 | 2.656 | 2.677 | 0.992 | 7.195% | 157.2 | 0.7 | 3.99 | 2.521 | 4.7 | -0.052 | 1.583 | 4.487% | -2.97 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.055 | 243 | 150 | 21 | 69.6 | 152.4 | 155.7 | 3.3 | 0.43 | 2.837 | 2.704 | 1.049 | 6.759% | 157 | 0.6 | 4.05 | 2.546 | 4.6 | -0.052 | 1.59 | 4.584% | -3.03 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.055 | 253 | 150 | 16 | 64.7 | 172.3 | 176.1 | 3.8 | 0.36 | 3.474 | 2.788 | 1.246 | 6.111% | 177.7 | 0.5 | 4.969 | 2.626 | 5.4 | -0.052 | 1.892 | 4.066% | -2.92 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.055 | 260 | 110 | 16 | 121.6 | 122.4 | 126.7 | 4.3 | 0.12 | 4.184 | 2.936 | 1.425 | 5.549% | 127.9 | 0.2 | 5.384 | 2.765 | 5.5 | -0.052 | 1.947 | 4.102% | -2.03 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.055 | 700 | 650 | 0 | 49.8 | 650.2 | 665.5 | 15.3 | -1.01 | 16.364 | 11.711 | 1.397 | 4.196% | 664 | -1.4 | 15.263 | 11.029 | 13.8 | -0.052 | 1.384 | 4.398% | -4.32 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.055 | 500 | 347 | 28.9 | 120.6 | 350.5 | 362 | 11.5 | 1.18 | 10.348 | 5.943 | 1.741 | 3.988% | 367.2 | 1.6 | 15.04 | 5.584 | 16.7 | -0.052 | 2 | 2.597% | -1.92 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.055 | 664 | 189.6 | 0 | 474.2 | 189.8 | 206.1 | 16.3 | -0.32 | 16.643 | 6.274 | 2 | 3.736% | 203.4 | -0.4 | 14.004 | 5.908 | 13.6 | -0.052 | 2 | 4.233% | -1.28 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.055 | 664 | 189.6 | 0 | 474.2 | 189.8 | 206.1 | 16.3 | -0.32 | 16.643 | 6.274 | 2 | 3.736% | 203.4 | -0.4 | 14.004 | 5.908 | 13.6 | -0.052 | 2 | 4.233% | -1.28 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.055 | 664 | 189.6 | 0 | 474.2 | 189.8 | 206.1 | 16.3 | -0.32 | 16.643 | 6.274 | 2 | 3.736% | 203.4 | -0.4 | 14.004 | 5.908 | 13.6 | -0.052 | 2 | 4.233% | -1.28 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.055 | 664 | 189.6 | 0 | 474.2 | 189.8 | 206.1 | 16.3 | -0.32 | 16.643 | 6.274 | 2 | 3.736% | 203.4 | -0.4 | 14.004 | 5.908 | 13.6 | -0.052 | 2 | 4.233% | -1.28 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.055 | 664 | 189.6 | 0 | 474.2 | 189.8 | 206.1 | 16.3 | -0.32 | 16.643 | 6.274 | 2 | 3.736% | 203.4 | -0.4 | 14.004 | 5.908 | 13.6 | -0.052 | 2 | 4.233% | -1.28 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.055 | 385 | 225 | 4.3 | 155.1 | 225.6 | 233.3 | 7.7 | -0.06 | 7.77 | 4.802 | 1.618 | 4.587% | 234.3 | -0.1 | 8.746 | 4.512 | 8.7 | -0.052 | 1.938 | 3.839% | -2.37 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 245 | 185 | 0 | 59.7 | 185.3 | 187.5 | 2.2 | -0.29 | 2.578 | 3.091 | 0.834 | 10.22% | 188.4 | -0.4 | 3.546 | 2.904 | 3.1 | -0.052 | 1.221 | 6.859% | -5.47 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 712 | 420 | 0 | 248.8 | 463.2 | 486.5 | 23.3 | 1.3 | 21.919 | 8.982 | 2 | 2.802% | 490.1 | 1.8 | 25.029 | 8.439 | 26.9 | -0.052 | 2 | 2.295% | -1.58 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 223.7 | 118 | 0 | 35 | 188.7 | 193.1 | 4.4 | -0.1 | 4.51 | 2.822 | 1.598 | 4.667% | 192.1 | -0.1 | 3.543 | 2.651 | 3.4 | -0.052 | 1.336 | 5.71% | -5.08 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.055 | 940 | 359.1 | 0 | 575.9 | 364.1 | 377.1 | 13 | -0.77 | 13.729 | 6.58 | 2 | 6.63% | 380.2 | -1.1 | 17.164 | 6.197 | 16.1 | -0.052 | 2 | 5.062% | -2.07 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.055 | 940 | 359.1 | 0 | 575.9 | 364.1 | 377.1 | 13 | -0.77 | 13.729 | 6.58 | 2 | 6.63% | 380.2 | -1.1 | 17.164 | 6.197 | 16.1 | -0.052 | 2 | 5.062% | -2.07 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.055 | 940 | 359.1 | 0 | 575.9 | 364.1 | 377.1 | 13 | -0.77 | 13.729 | 6.58 | 2 | 6.63% | 380.2 | -1.1 | 17.164 | 6.197 | 16.1 | -0.052 | 2 | 5.062% | -2.07 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.055 | 940 | 359.1 | 0 | 575.9 | 364.1 | 377.1 | 13 | -0.77 | 13.729 | 6.58 | 2 | 6.63% | 380.2 | -1.1 | 17.164 | 6.197 | 16.1 | -0.052 | 2 | 5.062% | -2.07 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.055 | 80 | 64 | 0 | 15.7 | 64.3 | 65.9 | 1.6 | -0.09 | 1.646 | 1.191 | 1.382 | 4.601% | 65.8 | -0.1 | 1.583 | 1.113 | 1.5 | -0.052 | 1.422 | 4.641% | -3.91 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.055 | 82 | 57 | 0 | 22.9 | 59.1 | 60.3 | 1.2 | 0.24 | 1 | 1.22 | 0.819 | 6.287% | 60.2 | 0.3 | 0.784 | 1.141 | 1.1 | -0.052 | 0.687 | 6.486% | -4.9 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.055 | 880 | 465 | 123.4 | 142.7 | 613.9 | 624.7 | 10.8 | -2.26 | 13.136 | 9.544 | 1.376 | 7.472% | 627.6 | -3.1 | 16.841 | 8.967 | 13.7 | -0.052 | 1.878 | 5.569% | -4.11 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.055 | 666 | 155 | 0 | 510.8 | 155.2 | 168 | 12.8 | -0.59 | 13.309 | 10.442 | 1.275 | 4.772% | 168.2 | -0.8 | 13.798 | 9.834 | 13 | -0.052 | 1.403 | 4.442% | -1.09 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.055 | 663 | 156 | 0 | 504.5 | 158.5 | 171.7 | 13.2 | 0.48 | 12.676 | 10.387 | 1.22 | 4.606% | 172 | 0.7 | 12.852 | 9.782 | 13.5 | -0.052 | 1.314 | 4.258% | -1.07 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.055 | 577 | 159 | 0 | 417.4 | 159.6 | 172.2 | 12.6 | -0.14 | 12.774 | 8.933 | 1.43 | 4.2% | 171.8 | -0.2 | 12.372 | 8.413 | 12.2 | -0.052 | 1.471 | 4.101% | -1.2 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.055 | 610 | 159 | 0 | 403.5 | 206.5 | 220.3 | 13.8 | 2.4 | 11.352 | 9.247 | 1.228 | 4.054% | 219.9 | 3.3 | 10.035 | 8.709 | 13.4 | -0.052 | 1.152 | 3.947% | -1.41 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.055 | 702 | 300 | 40 | 283.6 | 378.4 | 389.9 | 11.5 | 0.86 | 10.622 | 8.352 | 1.272 | 5.598% | 390.5 | 1.2 | 10.833 | 7.847 | 12.1 | -0.052 | 1.38 | 5.03% | -2.86 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.064 | 330 | 55 | 0 | 64.8 | 265.2 | 277.1 | 11.9 | 3.69 | 8.182 | 2.845 | 2 | 2.963% | 277.1 | 5.1 | 6.741 | 2.429 | 11.9 | -0.059 | 2 | 2.732% | -2.37 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.064 | 231 | 169 | 0 | 41.4 | 189.6 | 194.7 | 5.1 | -0.94 | 6.04 | 2.694 | 2 | 4.837% | 194.3 | -1.3 | 6.028 | 2.435 | 4.7 | -0.059 | 2 | 4.839% | -4.3 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.064 | 220 | 62 | 0 | 21.6 | 198.4 | 200.9 | 2.5 | 0.05 | 2.458 | 2.172 | 1.132 | 9.409% | 202.2 | 0.1 | 3.703 | 1.854 | 3.8 | -0.059 | 1.997 | 5.708% | -5.55 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.064 | 230 | 60 | 0 | 5.6 | 224.4 | 229.1 | 4.7 | 1.17 | 3.595 | 1.924 | 1.869 | 5.232% | 228.9 | 1.6 | 2.884 | 1.642 | 4.5 | -0.059 | 1.756 | 5.039% | -5.31 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.064 | 410 | 70 | 0 | 44.9 | 365.1 | 374.9 | 9.8 | 0.07 | 9.726 | 3.214 | 2 | 4.468% | 377.7 | 0.1 | 12.482 | 2.744 | 12.6 | -0.059 | 2 | 3.204% | -3.09 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.064 | 420 | 125 | 0 | 42.4 | 377.6 | 381.9 | 4.3 | -0.29 | 4.603 | 5.141 | 0.895 | 10.43% | 379.1 | -0.4 | 1.958 | 4.665 | 1.5 | -0.059 | 0.42 | 27.55% | -26.83 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.064 | 420 | 125 | 0 | 82.5 | 337.5 | 343.2 | 5.7 | 0.28 | 5.456 | 5.023 | 1.086 | 7.865% | 343.2 | 0.4 | 5.384 | 4.558 | 5.7 | -0.059 | 1.181 | 7.251% | -6.31 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.064 | 230 | 168 | 12 | 22 | 196 | 200.8 | 4.8 | -0.12 | 4.929 | 2.543 | 1.938 | 5.117% | 200.4 | -0.2 | 4.55 | 2.298 | 4.4 | -0.059 | 1.98 | 5.147% | -4.75 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.064 | 238 | 155 | 18 | 42.6 | 177.4 | 181.4 | 4 | 0 | 4.009 | 2.566 | 1.562 | 6.354% | 181.9 | 0 | 4.471 | 2.319 | 4.5 | -0.059 | 1.928 | 5.207% | -4.2 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.064 | 105 | 12 | 0 | 79.5 | 25.5 | 28.7 | 3.2 | 0.68 | 2.546 | 1.598 | 1.594 | 3.509% | 29.6 | 0.9 | 3.224 | 1.45 | 4.1 | -0.059 | 2 | 2.525% | -0.66 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.064 | 330 | 185 | 11 | 64.5 | 254.5 | 262.3 | 7.8 | 2.06 | 5.691 | 3.721 | 1.529 | 4.516% | 262.9 | 2.9 | 5.534 | 3.363 | 8.4 | -0.059 | 1.646 | 3.866% | -3.23 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.064 | 518.5 | 345.8 | 0 | 47.3 | 471.2 | 480.6 | 9.4 | -0.15 | 9.518 | 6.049 | 1.574 | 5.887% | 481.5 | -0.2 | 10.546 | 5.466 | 10.3 | -0.059 | 1.929 | 4.953% | -4.88 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.064 | 572.3 | 148.8 | 0 | 24.5 | 547.8 | 555.2 | 7.4 | 0 | 7.388 | 6.294 | 1.174 | 8.253% | 554.4 | 0 | 6.634 | 5.712 | 6.6 | -0.059 | 1.161 | 8.531% | -8.85 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.064 | 572.3 | 148.8 | 0 | 24.5 | 547.8 | 555.2 | 7.4 | 0 | 7.388 | 6.294 | 1.174 | 8.253% | 554.4 | 0 | 6.634 | 5.712 | 6.6 | -0.059 | 1.161 | 8.531% | -8.85 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.064 | 320 | 245 | 0 | 48.6 | 271.4 | 277 | 5.6 | -0.46 | 5.962 | 3.733 | 1.597 | 6.1% | 276.1 | -0.6 | 5.248 | 3.373 | 4.7 | -0.059 | 1.556 | 6.701% | -6.15 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.064 | 470 | 180 | 0 | 68.9 | 401.1 | 402.2 | 1.1 | -0.93 | 2.021 | 3.463 | 0.584 | 45.63% | 403.1 | -1.3 | 3.33 | 2.956 | 2 | -0.059 | 1.126 | 23.14% | -21.36 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.064 | 470 | 180 | 0 | 68.9 | 401.1 | 402.2 | 1.1 | -0.93 | 2.021 | 3.463 | 0.584 | 45.63% | 403.1 | -1.3 | 3.33 | 2.956 | 2 | -0.059 | 1.126 | 23.14% | -21.36 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.064 | 470 | 180 | 0 | 68.9 | 401.1 | 402.2 | 1.1 | -0.93 | 2.021 | 3.463 | 0.584 | 45.63% | 403.1 | -1.3 | 3.33 | 2.956 | 2 | -0.059 | 1.126 | 23.14% | -21.36 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.064 | 470 | 180 | 0 | 68.9 | 401.1 | 402.2 | 1.1 | -0.93 | 2.021 | 3.463 | 0.584 | 45.63% | 403.1 | -1.3 | 3.33 | 2.956 | 2 | -0.059 | 1.126 | 23.14% | -21.36 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.064 | 235 | 155 | 29 | 39.5 | 166.5 | 170.7 | 4.2 | -0.68 | 4.929 | 2.628 | 1.875 | 5.975% | 170.6 | -0.9 | 5.012 | 2.385 | 4.1 | -0.059 | 2 | 5.643% | -4.32 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.064 | 231 | 150 | 21 | 40.7 | 169.3 | 173.9 | 4.6 | -0.76 | 5.383 | 2.703 | 1.991 | 5.363% | 173.7 | -1.1 | 5.443 | 2.453 | 4.4 | -0.059 | 2 | 5.169% | -4.1 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.064 | 425 | 120 | 0 | 60.9 | 364.1 | 373.8 | 9.7 | -0.15 | 9.866 | 4.951 | 1.993 | 4.676% | 373.3 | -0.2 | 9.415 | 4.493 | 9.2 | -0.059 | 2 | 4.546% | -4.22 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.064 | 425 | 120 | 0 | 27.8 | 397.2 | 407 | 9.8 | 4.79 | 4.972 | 4.805 | 1.035 | 4.629% | 408 | 6.7 | 4.127 | 4.36 | 10.8 | -0.059 | 0.946 | 3.872% | -3.92 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.064 | 179 | 0 | 13.2 | 17.9 | 147.9 | 153.3 | 5.4 | 1.56 | 3.848 | 1.934 | 1.99 | 3.541% | 152.9 | 2.2 | 2.756 | 1.748 | 5 | -0.059 | 1.577 | 3.526% | -3.15 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.064 | 122 | 15 | 0 | 15.2 | 106.8 | 107.4 | 0.6 | 0.22 | 0.405 | 1.097 | 0.369 | 21.78% | 107.7 | 0.3 | 0.62 | 0.937 | 0.9 | -0.059 | 0.662 | 13.39% | -12.59 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.064 | 118 | 15 | 0 | 12.2 | 105.8 | 115.6 | 9.8 | 1.09 | 8.743 | 1.052 | 2 | 1.29% | 115.5 | 1.5 | 8.19 | 0.898 | 9.7 | -0.059 | 2 | 1.202% | -1.16 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.064 | 233 | 150 | 22 | 40.4 | 170.6 | 174.7 | 4.1 | -0.55 | 4.594 | 2.386 | 1.925 | 6.069% | 174.9 | -0.8 | 5.084 | 2.165 | 4.3 | -0.059 | 2 | 5.335% | -4.23 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.064 | 232 | 150 | 23 | 40.4 | 168.6 | 172.9 | 4.3 | -0.67 | 4.993 | 2.347 | 2 | 5.762% | 173.1 | -0.9 | 5.391 | 2.13 | 4.5 | -0.059 | 2 | 5.076% | -3.99 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.064 | 223 | 150 | 17 | 39.3 | 166.7 | 170.8 | 4.1 | -0.61 | 4.708 | 2.309 | 2 | 5.809% | 171 | -0.9 | 5.114 | 2.095 | 4.3 | -0.059 | 2 | 5.106% | -4.13 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.064 | 232 | 150 | 21 | 40.3 | 170.7 | 175 | 4.3 | -0.61 | 4.984 | 2.387 | 2 | 5.762% | 175.3 | -0.8 | 5.444 | 2.166 | 4.6 | -0.059 | 2 | 4.966% | -3.95 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.064 | 240 | 150 | 16 | 42.9 | 181.1 | 185.9 | 4.8 | -0.66 | 5.504 | 2.507 | 2 | 5.339% | 185.5 | -0.9 | 5.34 | 2.275 | 4.4 | -0.059 | 2 | 5.37% | -4.38 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.064 | 710 | 423.2 | 0 | 96.8 | 613.2 | 628.5 | 15.3 | -0.12 | 15.406 | 8.282 | 1.86 | 4.952% | 629 | -0.2 | 15.921 | 7.484 | 15.8 | -0.059 | 2 | 4.421% | -4.14 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.064 | 713.3 | 417.8 | 0 | 94.2 | 619.1 | 632.9 | 13.8 | -1 | 14.739 | 8.32 | 1.771 | 5.515% | 637.7 | -1.4 | 19.981 | 7.519 | 18.6 | -0.059 | 2 | 3.773% | -3.55 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.064 | 719.9 | 455 | 0 | 93.4 | 626.5 | 641.2 | 14.7 | -0.83 | 15.523 | 8.397 | 1.849 | 5.226% | 646.2 | -1.1 | 20.878 | 7.589 | 19.7 | -0.059 | 2 | 3.595% | -3.39 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.064 | 48.2 | 24 | 0 | 9.2 | 39 | 41.6 | 2.6 | -0.3 | 2.909 | 0.664 | 2 | 1.988% | 42 | -0.4 | 3.381 | 0.594 | 3 | -0.059 | 2 | 1.589% | -1.38 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.064 | 49.8 | 24 | 0 | 9.5 | 40.3 | 41.5 | 1.2 | -0.25 | 1.516 | 0.686 | 2 | 4.45% | 42.7 | -0.3 | 2.785 | 0.614 | 2.4 | -0.059 | 2 | 2.052% | -1.78 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.064 | 111 | 36 | 0 | 23.6 | 87.4 | 93.9 | 6.5 | 0.05 | 6.485 | 1.295 | 2 | 1.826% | 94.6 | 0.1 | 7.173 | 1.17 | 7.2 | -0.059 | 2 | 1.52% | -1.29 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.064 | 61 | 20 | 0 | 26.7 | 34.3 | 36.3 | 2 | -0.47 | 2.414 | 0.804 | 2 | 3.268% | 37.5 | -0.7 | 3.843 | 0.73 | 3.2 | -0.059 | 2 | 1.883% | -1.13 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.064 | 41 | 13 | 0 | 23.6 | 17.4 | 18.9 | 1.5 | -0.41 | 1.973 | 0.405 | 2 | 2.953% | 19 | -0.6 | 2.203 | 0.346 | 1.6 | -0.059 | 2 | 2.555% | -1.12 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.064 | 237 | 130 | 0 | 45 | 192 | 196.1 | 4.1 | -0.24 | 4.342 | 2.764 | 1.571 | 6.173% | 195.7 | -0.3 | 4.032 | 2.498 | 3.7 | -0.059 | 1.614 | 6.306% | -5.53 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.064 | 165 | 27 | 0 | 7.3 | 157.7 | 160.3 | 2.6 | -0.15 | 2.77 | 1.513 | 1.831 | 6.791% | 161.7 | -0.2 | 4.282 | 1.292 | 4 | -0.059 | 2 | 4.07% | -4.19 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.064 | 42 | 13 | 0 | 29 | 13 | 15.4 | 2.4 | -0.18 | 2.615 | 0.578 | 2 | 1.878% | 18.4 | -0.2 | 5.646 | 0.518 | 5.4 | -0.059 | 2 | 0.7701% | -0.25 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.064 | 42 | 13 | 0 | 28.9 | 13.1 | 15.6 | 2.5 | -0.18 | 2.622 | 0.578 | 2 | 1.803% | 19 | -0.2 | 6.103 | 0.518 | 5.9 | -0.059 | 2 | 0.7048% | -0.23 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | FOSS | -0.082 | 330 | 55 | 0 | 273.5 | 56.5 | 59.1 | 2.6 | -0.17 | 2.765 | 2.928 | 0.944 | 17.37% | 58.2 | -0.2 | 1.949 | 2.969 | 1.7 | -0.083 | 0.657 | 26.89% | -4.51 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.082 | 586 | 220 | 0 | 12.3 | 573.7 | 573.6 | -0.1 | -2.59 | 2.537 | 12.057 | 0.21 | -801.1% | 571.6 | -3.6 | 1.48 | 12.179 | -2.1 | -0.083 | 0.122 | -38.62% | 37.32 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 230 | 160 | 0 | 59.9 | 170.1 | 175.1 | 5 | -0.24 | 5.223 | 3.593 | 1.454 | 6.292% | 175.1 | -0.3 | 5.328 | 3.631 | 5 | -0.083 | 1.468 | 6.369% | -4.64 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 514 | 325 | 49 | 65.3 | 399.7 | 405.6 | 5.9 | -0.41 | 6.266 | 7.264 | 0.863 | 11.91% | 407.5 | -0.6 | 8.375 | 7.34 | 7.8 | -0.083 | 1.141 | 9.119% | -7 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.082 | 220 | 62 | 0 | 138.8 | 81.2 | 83 | 1.8 | -1.1 | 2.889 | 3.291 | 0.878 | 16.74% | 85.2 | -1.5 | 5.486 | 3.338 | 4 | -0.083 | 1.644 | 7.623% | -2.76 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 420 | 280 | 0 | 14.2 | 405.8 | 410 | 4.2 | -1.27 | 5.449 | 6.87 | 0.793 | 13.67% | 409.4 | -1.8 | 5.401 | 6.94 | 3.6 | -0.083 | 0.778 | 16.15% | -15.4 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.082 | 420 | 70 | 0 | 314.7 | 105.3 | 108.2 | 2.9 | -2.29 | 5.197 | 6.236 | 0.833 | 19.8% | 108.3 | -3.2 | 6.181 | 6.299 | 3 | -0.083 | 0.981 | 19.38% | -4.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.082 | 749 | 306 | 0 | 367 | 382 | 395.8 | 13.8 | 1.58 | 12.235 | 10.066 | 1.216 | 7.422% | 394.2 | 2.2 | 10.009 | 10.207 | 12.2 | -0.083 | 0.981 | 8.497% | -4.27 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.082 | 105 | 12 | 0 | 92.9 | 12.1 | 14.3 | 2.2 | 0.06 | 2.23 | 2.14 | 1.042 | 6.536% | 14.3 | 0.1 | 2.138 | 2.161 | 2.2 | -0.083 | 0.989 | 6.615% | -0.74 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.082 | 315 | 50 | 0 | 132.9 | 182.1 | 197 | 14.9 | -0.19 | 15.115 | 4.235 | 2 | 2.891% | 199.1 | -0.3 | 17.308 | 4.278 | 17 | -0.083 | 2 | 2.565% | -1.46 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.082 | 420 | 104 | 0 | 301.4 | 118.6 | 134 | 15.4 | 0.09 | 15.367 | 5.471 | 2 | 3.729% | 137.2 | 0.1 | 18.555 | 5.527 | 18.6 | -0.083 | 2 | 3.125% | -0.87 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 331 | 141 | 11 | 63 | 257 | 264.3 | 7.3 | 0.21 | 7.049 | 4.999 | 1.41 | 6.201% | 265.5 | 0.3 | 8.164 | 5.051 | 8.5 | -0.083 | 1.616 | 5.39% | -4.13 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 212 | 130 | 14 | 40.8 | 157.2 | 166.5 | 9.3 | -0.13 | 9.435 | 3.093 | 2 | 3.118% | 167.3 | -0.2 | 10.289 | 3.125 | 10.1 | -0.083 | 2 | 2.906% | -2.12 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 153 | 80 | 0 | 27.9 | 125.1 | 128.5 | 3.4 | 0 | 3.387 | 2.39 | 1.417 | 6.158% | 128.1 | 0 | 3.039 | 2.415 | 3 | -0.083 | 1.258 | 7.064% | -5.69 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | STM | -0.082 | 111.5 | 18.5 | 0 | 6.9 | 104.6 | 108.6 | 4 | 0.2 | 3.785 | 2.258 | 1.677 | 3.817% | 109.5 | 0.3 | 4.634 | 2.281 | 4.9 | -0.083 | 2 | 3.154% | -2.91 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.082 | 308.9 | 54.9 | 0 | 59.4 | 249.5 | 257.5 | 8 | -0.09 | 8.095 | 6.094 | 1.328 | 5.281% | 257.3 | -0.1 | 7.86 | 6.156 | 7.8 | -0.083 | 1.277 | 5.482% | -4.37 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | FOSS | -0.082 | 375 | 100 | 0 | 25.6 | 349.4 | 367.2 | 17.8 | 0.65 | 17.094 | 4.463 | 2 | 2.882% | 370 | 0.9 | 19.663 | 4.526 | 20.6 | -0.083 | 2 | 2.521% | -2.32 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.082 | 233 | 150 | 22 | 40.1 | 170.9 | 175.8 | 4.9 | -0.04 | 4.869 | 3.165 | 1.538 | 6.504% | 176.2 | -0.1 | 5.285 | 3.197 | 5.3 | -0.083 | 1.653 | 6.087% | -4.4 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.082 | 233 | 150 | 23 | 38.9 | 171.1 | 176.2 | 5.1 | 0.05 | 5.028 | 3.149 | 1.597 | 6.249% | 176.8 | 0.1 | 5.621 | 3.181 | 5.7 | -0.083 | 1.767 | 5.66% | -4.1 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.082 | 220 | 150 | 17 | 38.8 | 164.2 | 168.8 | 4.6 | 0.09 | 4.5 | 3.014 | 1.493 | 6.542% | 169.3 | 0.1 | 4.94 | 3.044 | 5.1 | -0.083 | 1.623 | 5.973% | -4.39 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.082 | 233 | 150 | 21 | 40.1 | 171.9 | 177 | 5.1 | -0.08 | 5.247 | 3.19 | 1.645 | 6.249% | 177.2 | -0.1 | 5.458 | 3.223 | 5.3 | -0.083 | 1.694 | 6.087% | -4.43 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.082 | 238 | 150 | 16 | 41.7 | 180.3 | 185.7 | 5.4 | 0.22 | 5.179 | 3.279 | 1.58 | 6.029% | 186.1 | 0.3 | 5.483 | 3.312 | 5.8 | -0.083 | 1.655 | 5.681% | -4.24 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.082 | 240 | 150 | 16 | 41.4 | 182.6 | 188.3 | 5.7 | -0.08 | 5.731 | 3.329 | 1.722 | 5.759% | 187.8 | -0.1 | 5.295 | 3.363 | 5.2 | -0.083 | 1.575 | 6.39% | -4.79 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.082 | 195 | 40 | 0 | 145.7 | 49.3 | 53.8 | 4.5 | -3.13 | 7.583 | 3.868 | 1.96 | 5.929% | 55.3 | -4.4 | 10.265 | 3.908 | 6 | -0.083 | 2 | 4.501% | -1.12 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | GT | -0.082 | 103 | 35 | 0 | 66.9 | 36.1 | 37.9 | 1.8 | 0 | 1.824 | 1.896 | 0.962 | 7.836% | 39.1 | 0 | 3.016 | 1.918 | 3 | -0.083 | 1.573 | 4.759% | -1.64 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.082 | 103 | 35 | 0 | 66.6 | 36.4 | 37.7 | 1.3 | 0 | 1.362 | 1.896 | 0.718 | 10.85% | 39.1 | 0 | 2.708 | 1.918 | 2.7 | -0.083 | 1.412 | 5.288% | -1.83 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.082 | 810 | 350 | 0 | 36.1 | 773.9 | 789.2 | 15.3 | 2.02 | 13.27 | 16.666 | 0.796 | 7.237% | 786.5 | 2.8 | 9.73 | 16.835 | 12.6 | -0.083 | 0.578 | 8.895% | -8.39 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 654.5 | 250 | 91.6 | 16.6 | 546.3 | 559.3 | 13 | 0 | 12.956 | 8.795 | 1.473 | 6.883% | 563.7 | 0 | 17.377 | 8.887 | 17.4 | -0.083 | 1.955 | 5.205% | -4.29 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 713.4 | 407.9 | 0 | 96.9 | 616.5 | 633.5 | 17 | -0.24 | 17.255 | 11.144 | 1.548 | 5.737% | 634.9 | -0.3 | 18.707 | 11.261 | 18.4 | -0.083 | 1.661 | 5.365% | -4.58 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 707.1 | 412.1 | 0 | 99.7 | 607.4 | 623.1 | 15.7 | -0.41 | 16.153 | 11.046 | 1.462 | 6.157% | 632 | -0.6 | 25.168 | 11.162 | 24.6 | -0.083 | 2 | 3.977% | -3.37 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 709.5 | 411.6 | 0 | 95.8 | 613.7 | 631 | 17.3 | 0 | 17.219 | 11.084 | 1.554 | 5.607% | 640.6 | 0 | 26.85 | 11.199 | 26.9 | -0.083 | 2 | 3.65% | -3.12 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.082 | 49.5 | 24 | 0 | 5.5 | 44 | 45 | 1 | 0 | 0.972 | 0.911 | 1.067 | 6.793% | 44.8 | 0 | 0.735 | 0.921 | 0.8 | -0.083 | 0.798 | 8.595% | -7.48 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.082 | 49.8 | 24 | 0 | 5.7 | 44.1 | 45.4 | 1.3 | -0.07 | 1.383 | 0.916 | 1.509 | 5.257% | 44.8 | -0.1 | 0.883 | 0.927 | 0.7 | -0.083 | 0.953 | 9.882% | -8.57 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 456.8 | 235 | 0 | 82.6 | 374.2 | 381.7 | 7.5 | -1.89 | 9.352 | 7.136 | 1.311 | 8.328% | 393.1 | -2.6 | 21.491 | 7.211 | 18.9 | -0.083 | 2 | 3.345% | -2.7 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 223.5 | 170 | 20 | 7.4 | 196.1 | 198.8 | 2.7 | 0.12 | 2.586 | 3.179 | 0.814 | 11.32% | 201.6 | 0.2 | 5.322 | 3.212 | 5.5 | -0.083 | 1.657 | 5.627% | -4.87 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 114 | 40 | 0 | 58 | 56 | 58.5 | 2.5 | -0.89 | 3.466 | 1.781 | 1.946 | 6.243% | 60.3 | -1.2 | 5.579 | 1.799 | 4.3 | -0.083 | 2 | 3.674% | -1.77 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 232 | 130 | 0 | 40.9 | 191.1 | 196.1 | 5 | -0.27 | 5.202 | 3.624 | 1.435 | 6.347% | 196.7 | -0.4 | 5.946 | 3.662 | 5.6 | -0.083 | 1.624 | 5.736% | -4.66 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.082 | 169 | 70 | 0 | 98.2 | 70.8 | 75.7 | 4.9 | 0.18 | 4.682 | 1.636 | 2 | 4.725% | 74.6 | 0.2 | 3.564 | 1.659 | 3.8 | -0.083 | 2 | 6.167% | -2.53 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 671 | 300 | 40 | 93.4 | 537.6 | 552.8 | 15.2 | -6.05 | 21.22 | 9.858 | 2 | 6.035% | 551.6 | -8.4 | 22.445 | 9.961 | 14 | -0.083 | 2 | 6.632% | -5.25 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 643.4 | 250 | 55 | 113.2 | 475.2 | 479.8 | 4.6 | 0.39 | 4.184 | 12.326 | 0.339 | 19.12% | 481 | 0.5 | 5.183 | 12.73 | 5.8 | -0.085 | 0.407 | 15.72% | -11.19 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 230 | 160 | 10 | 58.5 | 161.5 | 168.5 | 7 | 0.3 | 6.716 | 4.609 | 1.457 | 4.495% | 167.7 | 0.4 | 5.775 | 4.76 | 6.2 | -0.085 | 1.213 | 5.26% | -3.56 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 514 | 329 | 49 | 135.9 | 329.1 | 340.9 | 11.8 | -0.12 | 11.889 | 9.741 | 1.22 | 5.956% | 346.9 | -0.2 | 17.979 | 10.061 | 17.8 | -0.085 | 1.787 | 4.092% | -2.53 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.082 | 410 | 70 | 0 | 318.2 | 91.8 | 114.2 | 22.4 | -0.23 | 22.569 | 7.742 | 2 | 2.504% | 108.1 | -0.3 | 16.59 | 8.03 | 16.3 | -0.085 | 2 | 3.567% | -0.77 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 420 | 280 | 0 | 32.1 | 387.9 | 388.3 | 0.4 | -6.06 | 6.487 | 9.205 | 0.705 | 143.6% | 379.9 | -8.4 | 0.443 | 9.498 | -8 | -0.085 | 0.047 | -7.441% | 6.62 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 420 | 270 | 0 | 135 | 285 | 299 | 14 | -0.04 | 14.025 | 8.589 | 1.633 | 4.102% | 297.9 | -0.1 | 12.979 | 8.863 | 12.9 | -0.085 | 1.464 | 4.615% | -3.02 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.082 | 420 | 70 | 0 | 324 | 96 | 118 | 22 | -0.8 | 22.822 | 8.325 | 2 | 2.61% | 123.5 | -1.1 | 28.669 | 8.591 | 27.5 | -0.085 | 2 | 2.165% | -0.48 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.082 | 400 | 70 | 0 | 303.8 | 96.2 | 111.7 | 15.5 | 1.37 | 14.111 | 8.155 | 1.73 | 3.529% | 112.5 | 1.9 | 14.375 | 8.415 | 16.3 | -0.085 | 1.708 | 3.478% | -0.8 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.082 | 732 | 310 | 0 | 420.4 | 311.6 | 339.1 | 27.5 | 1.21 | 26.316 | 15.854 | 1.66 | 3.64% | 339.6 | 1.7 | 26.353 | 16.445 | 28 | -0.085 | 1.602 | 3.706% | -1.52 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 243 | 161 | 0 | 15.8 | 227.2 | 230.7 | 3.5 | -0.34 | 3.85 | 5.09 | 0.756 | 9.497% | 232 | -0.5 | 5.24 | 5.257 | 4.8 | -0.085 | 0.997 | 7.178% | -6.46 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 354 | 153 | 61 | 12 | 281 | 284.7 | 3.7 | -0.12 | 3.777 | 6.138 | 0.615 | 13.08% | 280.4 | -0.2 | -0.464 | 6.339 | -0.6 | -0.085 | 0 | -83.63% | 63.96 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.082 | 105 | 12 | 0 | 92.2 | 12.8 | 16.4 | 3.6 | 0.42 | 3.227 | 2.863 | 1.127 | 3.994% | 15.6 | 0.6 | 2.222 | 2.954 | 2.8 | -0.085 | 0.752 | 5.323% | -0.61 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 34 | 8 | 0 | 20.2 | 13.8 | 19.5 | 5.7 | 0 | 5.765 | 0.712 | 2 | 0.8202% | 20.8 | 0 | 7.056 | 0.736 | 7 | -0.085 | 2 | 0.6921% | -0.27 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 506 | 337.3 | 0 | 57.9 | 448.1 | 465.3 | 17.2 | 0.23 | 16.967 | 10.599 | 1.601 | 4.022% | 467.4 | 0.3 | 19.054 | 10.947 | 19.3 | -0.085 | 1.741 | 3.716% | -3.17 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 461 | 260 | 0 | 11.8 | 449.2 | 449.4 | 0.2 | 0 | 0.28 | 9.657 | 0.029 | 315.2% | 450.4 | 0 | 1.243 | 9.974 | 1.2 | -0.085 | 0.125 | 54.45% | -51.14 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 888.3 | 461 | 5.2 | 30 | 853.1 | 876.3 | 23.2 | -2.86 | 26.013 | 18.499 | 1.406 | 5.234% | 882.8 | -4 | 33.694 | 19.106 | 29.7 | -0.085 | 1.764 | 4.238% | -3.92 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | STM | -0.082 | 303.2 | 56.2 | 0 | 206.6 | 96.6 | 108.2 | 11.6 | -3.54 | 15.142 | 8.213 | 1.844 | 3.575% | 103.8 | -4.9 | 12.173 | 8.475 | 7.2 | -0.085 | 1.436 | 5.97% | -1.83 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.082 | 176.4 | 0 | 40 | 32.4 | 104 | 119 | 15 | 0.23 | 14.723 | 2.857 | 2 | 1.609% | 126 | 0.3 | 21.69 | 2.951 | 22 | -0.085 | 2 | 1.137% | -0.64 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 358 | 235 | 7 | 100.2 | 250.8 | 273.3 | 22.5 | 1.24 | 21.327 | 7.353 | 2 | 2.176% | 272.6 | 1.7 | 20.104 | 7.594 | 21.8 | -0.085 | 2 | 2.328% | -1.57 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.082 | 523 | 45 | 0 | 456.1 | 66.9 | 77.3 | 10.4 | -0.18 | 10.572 | 11.179 | 0.946 | 6.875% | 76.3 | -0.2 | 9.62 | 11.535 | 9.4 | -0.085 | 0.834 | 7.885% | -0.97 | 0.017 | 0.05 | 6.284% | 5.784%
Wind | WND | WIND | -0.082 | 183.9 | 0 | 0 | 11.4 | 172.5 | 174.7 | 2.2 | -0.24 | 2.401 | 5.07 | 0.474 | 11.44% | 174.2 | -0.3 | 1.965 | 5.231 | 1.7 | -0.085 | 0.376 | 15.34% | -13.85 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | FOSS | -0.082 | 118 | 15 | 0 | 102.8 | 15.2 | 21.7 | 6.5 | 0 | 6.427 | 2.319 | 2 | 2.49% | 23.9 | 0 | 8.677 | 2.405 | 8.7 | -0.085 | 2 | 1.928% | -0.23 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.082 | 230 | 150 | 22 | 38.4 | 169.6 | 174.2 | 4.6 | 0.45 | 4.141 | 4.165 | 0.994 | 6.839% | 175.6 | 0.6 | 5.378 | 4.298 | 6 | -0.085 | 1.251 | 5.435% | -3.86 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.082 | 229 | 150 | 23 | 37.3 | 168.7 | 173.9 | 5.2 | 0.43 | 4.765 | 4.108 | 1.16 | 6.024% | 175.4 | 0.6 | 6.101 | 4.239 | 6.7 | -0.085 | 1.439 | 4.846% | -3.44 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.082 | 222 | 150 | 17 | 37.2 | 167.8 | 172.3 | 4.5 | 0.5 | 4.068 | 4.094 | 0.994 | 6.749% | 173.8 | 0.7 | 5.288 | 4.224 | 6 | -0.085 | 1.252 | 5.246% | -3.82 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.082 | 229 | 150 | 21 | 38.4 | 169.6 | 176.6 | 7 | 0.46 | 6.571 | 4.159 | 1.58 | 4.475% | 176 | 0.6 | 5.742 | 4.291 | 6.4 | -0.085 | 1.338 | 5.073% | -3.62 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.082 | 238 | 150 | 16 | 39.7 | 182.3 | 189.2 | 6.9 | 0.37 | 6.558 | 4.412 | 1.487 | 4.718% | 188.4 | 0.5 | 5.613 | 4.552 | 6.1 | -0.085 | 1.233 | 5.532% | -4.08 | 0.017 | 0.05 | 6.335% | 5.367%
Wind | WND | WIND | -0.082 | 66.8 | 0 | 0 | 3.7 | 63.1 | 65.3 | 2.2 | -5.72 | 7.972 | 1.842 | 2 | 4.163% | 66.4 | -8 | 11.32 | 1.901 | 3.3 | -0.085 | 2 | 2.876% | -2.6 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.082 | 653.7 | 250 | 157.7 | 155.8 | 340.2 | 349 | 8.8 | -6.48 | 15.271 | 10.39 | 1.47 | 10.16% | 356.2 | -9 | 25.007 | 10.732 | 16 | -0.085 | 2 | 5.79% | -2.9 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 700.6 | 409 | 24.5 | 66.9 | 609.2 | 631.7 | 22.5 | 0.35 | 22.179 | 14.163 | 1.566 | 4.257% | 640.6 | 0.5 | 30.922 | 14.628 | 31.4 | -0.085 | 2 | 3.162% | -2.65 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 703.1 | 408.4 | 27.4 | 103.5 | 572.2 | 594.4 | 22.2 | 0.35 | 21.887 | 14.155 | 1.546 | 4.33% | 603.2 | 0.5 | 30.536 | 14.619 | 31 | -0.085 | 2 | 3.214% | -2.52 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.082 | 49.3 | 24 | 0 | 10.3 | 39 | 40.9 | 1.9 | -0.16 | 2.096 | 1.216 | 1.723 | 3.561% | 43.9 | -0.2 | 5.124 | 1.26 | 4.9 | -0.085 | 2 | 1.431% | -1.08 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.082 | 47.7 | 24 | 0 | 6.7 | 41 | 41.3 | 0.3 | -0.9 | 1.229 | 1.179 | 1.042 | 21.82% | 44.1 | -1.3 | 4.387 | 1.221 | 3.1 | -0.085 | 2 | 2.189% | -1.8 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.082 | 49.4 | 24 | 0 | 10.8 | 38.6 | 39.6 | 1 | -0.46 | 1.401 | 1.22 | 1.148 | 6.78% | 43.5 | -0.6 | 5.515 | 1.264 | 4.9 | -0.085 | 2 | 1.434% | -1.07 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 460 | 230 | 0.1 | 144.6 | 315.3 | 351.6 | 36.3 | 6.25 | 30.042 | 9.634 | 2 | 1.733% | 370.1 | 8.7 | 46.069 | 9.95 | 54.8 | -0.085 | 2 | 1.19% | -0.79 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 223.5 | 170 | 20 | 17.5 | 186 | 188.4 | 2.4 | -1.71 | 4.057 | 4.263 | 0.952 | 12.74% | 190.3 | -2.4 | 6.652 | 4.403 | 4.3 | -0.085 | 1.511 | 7.37% | -5.91 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 112 | 36 | 0 | 71.8 | 40.2 | 48.5 | 8.3 | 0.97 | 7.378 | 2.346 | 2 | 1.848% | 50.5 | 1.4 | 9.032 | 2.423 | 10.3 | -0.085 | 2 | 1.543% | -0.53 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.082 | 76 | 57 | 0 | 18.7 | 57.3 | 59.6 | 2.3 | 0.12 | 2.162 | 1.876 | 1.152 | 4.528% | 59.2 | 0.2 | 1.688 | 1.943 | 1.9 | -0.085 | 0.869 | 5.682% | -4.11 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.082 | 76 | 57 | 0 | 18.1 | 57.9 | 60.4 | 2.5 | 0.19 | 2.294 | 1.876 | 1.223 | 4.166% | 59.9 | 0.3 | 1.688 | 1.943 | 2 | -0.085 | 0.869 | 5.397% | -3.94 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.082 | 169 | 27 | 0 | 141.5 | 27.5 | 36.3 | 8.8 | -0.03 | 8.766 | 2.192 | 2 | 2.631% | 34.2 | 0 | 6.672 | 2.274 | 6.7 | -0.085 | 2 | 3.582% | -0.55 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.082 | 169 | 27 | 0 | 141.6 | 27.4 | 33.6 | 6.2 | 0.03 | 6.163 | 1.931 | 2 | 3.734% | 34.3 | 0 | 6.795 | 2.003 | 6.9 | -0.085 | 2 | 3.478% | -0.53 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 706 | 295 | 70 | 109.4 | 526.6 | 550.8 | 24.2 | 0.25 | 23.977 | 13.323 | 1.8 | 3.988% | 553.8 | 0.3 | 26.838 | 13.76 | 27.2 | -0.085 | 1.95 | 3.678% | -2.64 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 676 | 300 | 40 | 135.6 | 500.4 | 535.9 | 35.5 | 1.73 | 33.802 | 13.324 | 2 | 2.603% | 538.5 | 2.4 | 35.689 | 13.761 | 38.1 | -0.085 | 2 | 2.514% | -1.79 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 231 | 159 | 10 | 59.8 | 161.2 | 166.2 | 5 | -0.41 | 5.363 | 3.936 | 1.363 | 5.704% | 165 | -0.6 | 4.375 | 3.778 | 3.8 | -0.071 | 1.158 | 7.201% | -5.22 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 514 | 328 | 49 | 128.8 | 336.2 | 349.1 | 12.9 | -0.41 | 13.346 | 8.281 | 1.612 | 4.916% | 353.1 | -0.6 | 17.489 | 7.95 | 16.9 | -0.071 | 2 | 3.601% | -2.45 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 459 | 300 | 0 | 9.5 | 449.5 | 453.9 | 4.4 | 1.26 | 3.134 | 8.174 | 0.383 | 12.87% | 454.1 | 1.8 | 2.861 | 7.847 | 4.6 | -0.071 | 0.365 | 11.81% | -12.05 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.074 | 230 | 60 | 0 | 163.1 | 66.9 | 76.6 | 9.7 | -1.95 | 11.64 | 3.879 | 2 | 2.93% | 76.3 | -2.7 | 12.146 | 3.679 | 9.4 | -0.071 | 2 | 2.901% | -0.87 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 560 | 400 | 0 | 55.9 | 504.1 | 514.1 | 10 | -0.1 | 10.069 | 12.96 | 0.777 | 6.91% | 513.5 | -0.1 | 9.459 | 12.455 | 9.4 | -0.071 | 0.759 | 7.053% | -6.61 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 420 | 260 | 0 | 18.5 | 401.5 | 408.7 | 7.2 | -2.24 | 9.407 | 7.81 | 1.204 | 7.198% | 409 | -3.1 | 10.624 | 7.506 | 7.5 | -0.071 | 1.415 | 6.63% | -6.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 420 | 260 | 0 | 28.7 | 391.3 | 403.5 | 12.2 | -0.84 | 13.092 | 7.76 | 1.687 | 4.248% | 403.2 | -1.2 | 13.141 | 7.457 | 11.9 | -0.071 | 1.762 | 4.179% | -4.05 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 420 | 70 | 0 | 340.2 | 79.8 | 95.1 | 15.3 | -3.13 | 18.346 | 7.117 | 2 | 3.387% | 95.1 | -4.4 | 19.646 | 6.84 | 15.3 | -0.071 | 2 | 3.25% | -0.64 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 732 | 309 | 0 | 21.5 | 710.5 | 726.8 | 16.3 | 2.66 | 13.642 | 10.579 | 1.29 | 5.542% | 728.8 | 3.7 | 14.504 | 10.033 | 18.3 | -0.071 | 1.446 | 4.736% | -4.79 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 105 | 12 | 0 | 91.7 | 13.3 | 15.7 | 2.4 | 0.87 | 1.562 | 2.428 | 0.643 | 5.408% | 15.2 | 1.2 | 0.745 | 2.334 | 1.9 | -0.071 | 0.319 | 6.554% | -0.85 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 420 | 50 | 0 | 120.8 | 299.2 | 318.1 | 18.9 | 0.48 | 18.372 | 8.247 | 2 | 2.742% | 319.4 | 0.7 | 19.456 | 7.925 | 20.2 | -0.071 | 2 | 2.462% | -1.83 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 37 | 19 | 0 | 4.8 | 32.2 | 34.9 | 2.7 | 0 | 2.7 | 0.659 | 2 | 1.701% | 37 | 0 | 4.8 | 0.633 | 4.8 | -0.071 | 2 | 0.9181% | -0.82 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 329 | 138 | 11 | 61.6 | 256.4 | 266.1 | 9.7 | -0.04 | 9.713 | 5.663 | 1.715 | 4.186% | 266.4 | -0.1 | 10.108 | 5.437 | 10 | -0.071 | 1.859 | 3.896% | -3.16 | 0.017 | 0.058 | 5.933% | 5.163%
Wind | WND | WIND | -0.074 | 51 | 0 | 0 | 5.8 | 45.2 | 44.4 | -0.8 | -3.66 | 2.833 | 1.192 | 2 | -7.898% | 45.7 | -5.1 | 5.574 | 1.145 | 0.5 | -0.071 | 2 | 12.13% | -11.09 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | SUB | FOSS | -0.074 | 470 | 180 | 0 | 51.2 | 418.8 | 425.1 | 6.3 | 2.61 | 3.683 | 6.271 | 0.587 | 9.21% | 426.2 | 3.6 | 3.749 | 5.948 | 7.4 | -0.071 | 0.63 | 7.523% | -6.97 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 470 | 180 | 0 | 51.2 | 418.8 | 425.1 | 6.3 | 2.61 | 3.683 | 6.271 | 0.587 | 9.21% | 426.2 | 3.6 | 3.749 | 5.948 | 7.4 | -0.071 | 0.63 | 7.523% | -6.97 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 470 | 180 | 0 | 51.2 | 418.8 | 425.1 | 6.3 | 2.61 | 3.683 | 6.271 | 0.587 | 9.21% | 426.2 | 3.6 | 3.749 | 5.948 | 7.4 | -0.071 | 0.63 | 7.523% | -6.97 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 470 | 180 | 0 | 51.2 | 418.8 | 425.1 | 6.3 | 2.61 | 3.683 | 6.271 | 0.587 | 9.21% | 426.2 | 3.6 | 3.749 | 5.948 | 7.4 | -0.071 | 0.63 | 7.523% | -6.97 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | STM | -0.074 | 302 | 55 | 0 | 61.2 | 240.8 | 250 | 9.2 | -0.17 | 9.353 | 6.777 | 1.38 | 4.052% | 248.3 | -0.2 | 7.807 | 6.513 | 7.5 | -0.071 | 1.199 | 4.769% | -3.96 | 0.017 | 0.05 | 5.146% | 4.85%
Wind | WND | WIND | -0.074 | 195.9 | 0 | 0 | 36.9 | 159 | 162.1 | 3.1 | -0.21 | 3.329 | 4.578 | 0.727 | 7.803% | 162.7 | -0.3 | 4.074 | 4.399 | 3.7 | -0.071 | 0.926 | 6.273% | -5.29 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | COGN | -0.074 | 224 | 150 | 22 | 37.7 | 164.3 | 169 | 4.7 | 0.99 | 3.741 | 3.855 | 0.97 | 5.884% | 168.9 | 1.4 | 3.199 | 3.705 | 4.6 | -0.071 | 0.864 | 5.768% | -4.4 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.074 | 231 | 155 | 29 | 35.8 | 166.2 | 170.4 | 4.2 | 1 | 3.197 | 3.879 | 0.824 | 6.79% | 170.5 | 1.4 | 2.904 | 3.728 | 4.3 | -0.071 | 0.779 | 6.364% | -4.76 | 0.017 | 0.05 | 5.933% | 5.163%
Wind | WND | WIND | -0.074 | 192.7 | 0 | 0 | 29.6 | 163.1 | 161.3 | -1.8 | -5.13 | 3.294 | 4.504 | 0.731 | -13.22% | 162.5 | -7.1 | 6.528 | 4.328 | -0.6 | -0.071 | 1.508 | -38.05% | 33.48 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | FOSS | -0.074 | 425 | 120 | 0 | 287.4 | 137.6 | 159 | 21.4 | 1.6 | 19.866 | 8.88 | 2 | 2.451% | 161.6 | 2.2 | 21.794 | 8.534 | 24 | -0.071 | 2 | 2.097% | -0.71 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 174.8 | 0 | 40 | 11.9 | 122.9 | 129.4 | 6.5 | -0.75 | 7.291 | 2.401 | 2 | 3.321% | 126.2 | -1 | 4.295 | 2.305 | 3.3 | -0.071 | 1.864 | 6.277% | -4.58 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 605 | 304 | 120 | 87.3 | 397.7 | 409.6 | 11.9 | 2.11 | 9.782 | 8.637 | 1.132 | 6.273% | 416.8 | 2.9 | 16.162 | 8.292 | 19.1 | -0.071 | 1.949 | 3.75% | -2.57 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 610 | 305 | 120 | 21.9 | 468.1 | 479 | 10.9 | 3 | 7.941 | 8.726 | 0.91 | 6.905% | 479.1 | 4.2 | 6.882 | 8.377 | 11 | -0.071 | 0.822 | 6.565% | -5.25 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.074 | 831 | 261 | 0 | 191.5 | 639.5 | 663.5 | 24 | -3.86 | 27.841 | 14.629 | 1.903 | 4.272% | 669.5 | -5.4 | 35.365 | 14.059 | 30 | -0.071 | 2 | 3.279% | -2.63 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.074 | 842 | 451 | 0 | 58.9 | 783.1 | 807 | 23.9 | 4.14 | 19.793 | 13.892 | 1.425 | 4.346% | 804.8 | 5.8 | 15.959 | 13.351 | 21.7 | -0.071 | 1.195 | 4.593% | -4.45 | 0.017 | 0.05 | 6.284% | 5.784%
Wind | WND | WIND | -0.074 | 186.5 | 0 | 0 | 12.9 | 173.6 | 178 | 4.4 | -0.05 | 4.501 | 4.358 | 1.033 | 5.234% | 177.9 | -0.1 | 4.387 | 4.188 | 4.3 | -0.071 | 1.048 | 5.139% | -4.97 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | GT | -0.074 | 228 | 150 | 23 | 37.3 | 167.7 | 172.2 | 4.5 | 0.83 | 3.633 | 3.458 | 1.05 | 6.255% | 172.4 | 1.2 | 3.53 | 3.323 | 4.7 | -0.071 | 1.062 | 5.746% | -4.39 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.074 | 218 | 150 | 17 | 38.4 | 162.6 | 167.2 | 4.6 | 0.61 | 4.006 | 3.394 | 1.18 | 5.851% | 168 | 0.9 | 4.57 | 3.261 | 5.4 | -0.071 | 1.401 | 4.782% | -3.71 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.074 | 232 | 150 | 16 | 39.4 | 176.6 | 181.2 | 4.6 | 0.87 | 3.722 | 3.588 | 1.037 | 6.226% | 181.2 | 1.2 | 3.445 | 3.448 | 4.6 | -0.071 | 0.999 | 5.974% | -4.73 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.074 | 195 | 40 | 0 | 145.6 | 49.4 | 59.2 | 9.8 | -1.84 | 11.671 | 4.378 | 2 | 2.457% | 59.9 | -2.6 | 13.068 | 4.207 | 10.5 | -0.071 | 2 | 2.2% | -0.58 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | WDS | STM | -0.074 | 105 | 70 | 0 | 5.1 | 99.9 | 101.9 | 2 | -0.12 | 2.081 | 2.203 | 0.945 | 6.489% | 102 | -0.2 | 2.221 | 2.107 | 2.1 | -0.071 | 1.054 | 5.93% | -5.85 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.074 | 654.1 | 250 | 155.1 | 22.1 | 476.9 | 488 | 11.1 | 0.73 | 10.427 | 8.885 | 1.174 | 7.27% | 491.6 | 1 | 13.707 | 8.53 | 14.7 | -0.071 | 1.607 | 5.267% | -4 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 699.7 | 398.8 | 73 | 95 | 531.7 | 553 | 21.3 | 0.53 | 20.703 | 11.161 | 1.855 | 4.053% | 551.7 | 0.7 | 19.233 | 10.714 | 20 | -0.071 | 1.795 | 4.141% | -3.28 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 695.7 | 407.3 | 29.4 | 89 | 577.3 | 592.6 | 15.3 | 0.89 | 14.477 | 11.866 | 1.22 | 5.61% | 600.9 | 1.2 | 22.411 | 11.391 | 23.6 | -0.071 | 1.967 | 3.49% | -3.02 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 696.1 | 406.7 | 21.2 | 64.6 | 610.3 | 626.6 | 16.3 | 0.77 | 15.56 | 12.019 | 1.295 | 5.269% | 635.3 | 1.1 | 23.947 | 11.538 | 25 | -0.071 | 2 | 3.296% | -3.01 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.074 | 49.8 | 24 | 0 | 12.6 | 37.2 | 38.8 | 1.6 | -0.29 | 1.834 | 1.045 | 1.755 | 3.856% | 41.3 | -0.4 | 4.434 | 1 | 4.1 | -0.071 | 2 | 1.444% | -1.11 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 49.8 | 24 | 0 | 12.9 | 36.9 | 39.4 | 2.5 | -0.33 | 2.858 | 1.046 | 2 | 2.468% | 44.1 | -0.5 | 7.64 | 1 | 7.2 | -0.071 | 2 | 0.8224% | -0.63 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 460 | 230 | 6.8 | 116.2 | 337 | 360.1 | 23.1 | 0.77 | 22.395 | 8.071 | 2 | 2.457% | 376.2 | 1.1 | 38.176 | 7.748 | 39.2 | -0.071 | 2 | 1.389% | -1.06 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 218.7 | 170 | 20 | 19.4 | 179.3 | 181.6 | 2.3 | 1.77 | 0.604 | 3.539 | 0.171 | 11.74% | 181.7 | 2.5 | -0.02 | 3.397 | 2.4 | -0.071 | 0 | 10.79% | -9.2 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 223.4 | 170 | 20 | 27.9 | 175.5 | 178.7 | 3.2 | -0.12 | 3.316 | 3.622 | 0.915 | 8.619% | 179.3 | -0.2 | 3.95 | 3.477 | 3.8 | -0.071 | 1.136 | 6.964% | -5.69 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 112 | 36 | 0 | 71.3 | 40.7 | 46.5 | 5.8 | -0.34 | 6.103 | 1.995 | 2 | 2.386% | 48.3 | -0.5 | 8.124 | 1.915 | 7.6 | -0.071 | 2 | 1.748% | -0.66 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.074 | 502 | 35 | 0 | 464.9 | 37.1 | 42 | 4.9 | -0.26 | 5.184 | 7.936 | 0.653 | 12.65% | 39 | -0.4 | 2.225 | 7.527 | 1.9 | -0.071 | 0.296 | 31.29% | -2.38 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 266 | 100 | 20 | 42.8 | 203.2 | 209.3 | 6.1 | -0.45 | 6.572 | 4.381 | 1.5 | 5.383% | 215.4 | -0.6 | 12.876 | 4.206 | 12.2 | -0.071 | 2 | 2.582% | -2.05 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.074 | 169 | 25 | 0 | 140.7 | 28.3 | 34.5 | 6.2 | 0.32 | 5.869 | 1.643 | 2 | 3.371% | 33.6 | 0.4 | 4.883 | 1.558 | 5.3 | -0.071 | 2 | 3.784% | -0.65 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 240 | 54 | 0 | 111.9 | 128.1 | 136.6 | 8.5 | 2.02 | 6.554 | 4.062 | 1.614 | 3.489% | 139 | 2.8 | 8.097 | 3.852 | 10.9 | -0.071 | 2 | 2.611% | -1.44 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 230 | 159 | 10 | 42.7 | 177.3 | 182.4 | 5.1 | -0.24 | 5.367 | 4.019 | 1.335 | 5.718% | 182.9 | -0.3 | 5.978 | 3.588 | 5.6 | -0.069 | 1.666 | 4.728% | -4.01 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 500 | 326 | 36 | 48.7 | 415.3 | 421.8 | 6.5 | 0.18 | 6.351 | 8.476 | 0.749 | 9.748% | 425.3 | 0.2 | 9.804 | 7.568 | 10 | -0.069 | 1.295 | 5.753% | -5.26 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 459 | 300 | 0 | 46.5 | 412.5 | 424.3 | 11.8 | -1.04 | 12.865 | 8.385 | 1.534 | 4.93% | 424.8 | -1.5 | 13.759 | 7.486 | 12.3 | -0.069 | 1.838 | 4.294% | -4.25 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.076 | 230 | 110 | 0 | 72.6 | 157.4 | 161.8 | 4.4 | 0.06 | 4.366 | 3.768 | 1.159 | 6.634% | 162.8 | 0.1 | 5.314 | 3.251 | 5.4 | -0.069 | 1.634 | 4.909% | -3.68 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 560 | 200 | 0 | 24.4 | 535.6 | 549.3 | 13.7 | -0.38 | 14.05 | 13.417 | 1.047 | 5.18% | 551.6 | -0.5 | 16.488 | 12.015 | 16 | -0.069 | 1.372 | 4.027% | -4.24 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 785 | 300 | 0 | 31.4 | 753.6 | 768.2 | 14.6 | 0.04 | 14.549 | 18.531 | 0.785 | 6.812% | 774.1 | 0.1 | 20.489 | 16.595 | 20.5 | -0.069 | 1.235 | 4.405% | -4.66 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 420 | 280 | 0 | 42.4 | 377.6 | 385.9 | 8.3 | -0.07 | 8.308 | 7.919 | 1.049 | 6.413% | 383.4 | -0.1 | 5.887 | 7.092 | 5.8 | -0.069 | 0.83 | 8.332% | -8.24 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 420 | 280 | 0 | 58.4 | 361.6 | 370.2 | 8.6 | -0.11 | 8.752 | 7.85 | 1.115 | 6.189% | 371.5 | -0.2 | 10.043 | 7.03 | 9.9 | -0.069 | 1.429 | 4.882% | -4.62 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.076 | 420 | 70 | 0 | 106.1 | 313.9 | 321.9 | 8 | -0.33 | 8.303 | 8.929 | 0.93 | 6.654% | 324.5 | -0.5 | 11.086 | 7.996 | 10.6 | -0.069 | 1.386 | 4.559% | -3.75 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 635 | 300 | 0 | 28.6 | 606.4 | 621.2 | 14.8 | 0 | 14.863 | 12.889 | 1.153 | 5.437% | 623.9 | 0 | 17.55 | 11.542 | 17.5 | -0.069 | 1.521 | 4.174% | -4.39 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.076 | 105 | 12 | 0 | 92.6 | 12.4 | 15.6 | 3.2 | 0.35 | 2.877 | 2.49 | 1.155 | 4.165% | 15.4 | 0.5 | 2.546 | 2.229 | 3 | -0.069 | 1.142 | 4.034% | -0.51 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.076 | 420 | 50 | 0 | 22.4 | 397.6 | 416 | 18.4 | -0.35 | 18.724 | 8.493 | 2 | 2.893% | 414.4 | -0.5 | 17.303 | 7.606 | 16.8 | -0.069 | 2 | 2.877% | -3 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 330 | 137 | 11 | 60.1 | 258.9 | 267.7 | 8.8 | -0.11 | 8.937 | 5.827 | 1.534 | 4.753% | 269 | -0.2 | 10.257 | 5.203 | 10.1 | -0.069 | 1.971 | 3.76% | -3.24 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | STM | -0.076 | 302.1 | 55.1 | 0 | 60.4 | 241.7 | 250.1 | 8.4 | 0.02 | 8.355 | 6.949 | 1.202 | 4.559% | 250.6 | 0 | 8.809 | 6.223 | 8.9 | -0.069 | 1.416 | 3.907% | -3.44 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | FOSS | -0.076 | 390 | 40 | 0 | 36.2 | 353.8 | 361.5 | 7.7 | 1.7 | 5.979 | 5.916 | 1.011 | 6.423% | 362.4 | 2.4 | 6.212 | 5.105 | 8.6 | -0.069 | 1.217 | 5.222% | -5.2 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.076 | 223 | 150 | 22 | 38.2 | 162.8 | 167 | 4.2 | 0.49 | 3.803 | 3.929 | 0.968 | 6.732% | 167.8 | 0.7 | 4.33 | 3.518 | 5 | -0.069 | 1.231 | 5.135% | -4.12 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.076 | 229 | 155 | 29 | 34.4 | 165.6 | 170.4 | 4.8 | 0.39 | 4.361 | 3.93 | 1.11 | 6.049% | 170.6 | 0.5 | 4.365 | 3.519 | 5 | -0.069 | 1.24 | 5.273% | -4.19 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.076 | 425 | 120 | 0 | 140.3 | 284.7 | 303.3 | 18.6 | 2.32 | 16.299 | 8.124 | 2 | 2.896% | 303.6 | 3.2 | 15.72 | 7.275 | 18.9 | -0.069 | 2 | 2.587% | -1.91 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.076 | 435 | 120 | 0 | 12.2 | 422.8 | 429.3 | 6.5 | -0.29 | 6.783 | 7.44 | 0.912 | 8.481% | 430.9 | -0.4 | 8.527 | 6.662 | 8.1 | -0.069 | 1.28 | 6.179% | -6.61 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 174.1 | 0 | 40 | 29.4 | 104.7 | 110.3 | 5.6 | 0.82 | 4.794 | 2.45 | 1.957 | 3.943% | 109.1 | 1.1 | 3.193 | 2.187 | 4.4 | -0.069 | 1.46 | 4.557% | -3.01 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.076 | 392 | 57 | 0 | 327.4 | 64.6 | 73.5 | 8.9 | -0.18 | 9.089 | 7.858 | 1.157 | 5.582% | 73.5 | -0.2 | 9.164 | 7.037 | 8.9 | -0.069 | 1.302 | 5.068% | -0.92 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.076 | 118 | 15 | 0 | 14.5 | 103.5 | 109.8 | 6.3 | -0.11 | 6.392 | 1.967 | 2 | 2.381% | 110.5 | -0.2 | 7.167 | 1.697 | 7 | -0.069 | 2 | 1.947% | -1.86 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.076 | 227 | 150 | 22 | 37.8 | 167.2 | 171.3 | 4.1 | 0.45 | 3.667 | 3.542 | 1.035 | 7.02% | 172.1 | 0.6 | 4.248 | 3.172 | 4.9 | -0.069 | 1.339 | 5.333% | -4.32 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.076 | 219 | 150 | 17 | 37.6 | 164.4 | 168.4 | 4 | 0.66 | 3.321 | 3.493 | 0.951 | 6.942% | 169.1 | 0.9 | 3.71 | 3.128 | 4.7 | -0.069 | 1.186 | 5.365% | -4.42 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.076 | 233 | 150 | 16 | 40 | 177 | 181.6 | 4.6 | 0.82 | 3.698 | 3.701 | 0.999 | 6.422% | 182.1 | 1.1 | 3.884 | 3.314 | 5.1 | -0.069 | 1.172 | 5.259% | -4.39 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.076 | 195 | 40 | 0 | 24.4 | 170.6 | 176.5 | 5.9 | -0.84 | 6.765 | 4.122 | 1.641 | 4.191% | 176.4 | -1.2 | 6.992 | 3.692 | 5.8 | -0.069 | 1.894 | 3.871% | -3.72 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.076 | 693.1 | 455 | 27.4 | 78.1 | 587.6 | 605.6 | 18 | 0.59 | 17.379 | 12.161 | 1.429 | 4.879% | 614 | 0.8 | 25.579 | 10.858 | 26.4 | -0.069 | 2 | 3.02% | -2.82 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 694.3 | 455 | 10.4 | 36.2 | 647.7 | 666 | 18.3 | 0.35 | 17.974 | 12.493 | 1.439 | 4.807% | 673.5 | 0.5 | 25.357 | 11.154 | 25.8 | -0.069 | 2 | 3.096% | -3.18 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.076 | 48.8 | 24 | 0 | 8.2 | 40.6 | 41.9 | 1.3 | 0.15 | 1.209 | 1.05 | 1.152 | 4.777% | 46.4 | 0.2 | 5.631 | 0.927 | 5.8 | -0.069 | 2 | 0.9725% | -0.88 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.076 | 47.8 | 24 | 0 | 5.9 | 41.9 | 42.6 | 0.7 | 0.03 | 0.717 | 1.028 | 0.698 | 8.69% | 46.7 | 0 | 4.74 | 0.908 | 4.8 | -0.069 | 2 | 1.151% | -1.1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.076 | 49.1 | 24 | 0 | 7.7 | 41.4 | 42 | 0.6 | -0.11 | 0.715 | 1.057 | 0.676 | 10.41% | 46.6 | -0.2 | 5.345 | 0.934 | 5.2 | -0.069 | 2 | 1.091% | -1 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 455 | 230 | 2.3 | 43.2 | 409.5 | 419.8 | 10.3 | 0.12 | 10.176 | 8.27 | 1.23 | 5.598% | 422.7 | 0.2 | 13.036 | 7.384 | 13.2 | -0.069 | 1.766 | 3.966% | -3.93 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 112 | 40 | 0 | 30.3 | 81.7 | 88.7 | 7 | 0.04 | 6.968 | 2.046 | 2 | 2.031% | 91.2 | 0 | 9.451 | 1.827 | 9.5 | -0.069 | 2 | 1.359% | -1.09 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.076 | 502 | 35 | 0 | 21.3 | 480.7 | 484 | 3.3 | -4.6 | 7.933 | 6.972 | 1.138 | 19.29% | 487.3 | -6.4 | 13.015 | 6.016 | 6.6 | -0.069 | 2 | 8.756% | -9.22 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.076 | 57 | 15 | 0 | 36.1 | 20.9 | 22.9 | 2 | 0.3 | 1.63 | 0.976 | 1.67 | 3.624% | 23.3 | 0.4 | 1.94 | 0.874 | 2.4 | -0.069 | 2 | 2.743% | -1.09 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.076 | 55 | 20 | 0 | 34.7 | 20.3 | 21.6 | 1.3 | 0.18 | 1.098 | 0.933 | 1.176 | 5.381% | 21 | 0.2 | 0.454 | 0.836 | 0.7 | -0.069 | 0.543 | 9.076% | -3.63 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.076 | 41 | 13 | 0 | 26 | 15 | 15.4 | 0.4 | -0.24 | 0.658 | 0.753 | 0.874 | 13.12% | 14.9 | -0.3 | 0.228 | 0.65 | -0.1 | -0.069 | 0.352 | -47.72% | 18.43 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 266 | 100 | 18.9 | 11.9 | 235.2 | 240.7 | 5.5 | -0.82 | 6.294 | 4.515 | 1.394 | 6.131% | 243.8 | -1.1 | 9.678 | 4.031 | 8.6 | -0.069 | 2 | 3.56% | -3.46 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.076 | 157 | 140 | 0 | 8.8 | 148.2 | 152.7 | 4.5 | 1.12 | 3.398 | 2.688 | 1.264 | 4.432% | 154 | 1.6 | 4.293 | 2.319 | 5.8 | -0.069 | 1.851 | 3.123% | -3.23 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.076 | 40 | 13 | 0 | 26.4 | 13.6 | 15 | 1.4 | 0.18 | 1.298 | 0.861 | 1.508 | 3.639% | 14.8 | 0.2 | 1.004 | 0.761 | 1.2 | -0.069 | 1.32 | 3.857% | -1.41 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.117 | 190 | 85 | 0 | 37.8 | 152.2 | 161.1 | 8.9 | -0.05 | 8.936 | 5.254 | 1.701 | 4.166% | 170.2 | -0.1 | 18.057 | 5.546 | 18 | -0.122 | 2 | 2.148% | -1.65 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.117 | 508 | 327 | 48 | 17.5 | 442.5 | 448.8 | 6.3 | -2.18 | 8.421 | 10.808 | 0.779 | 15.73% | 452 | -3 | 12.495 | 11.362 | 9.5 | -0.122 | 1.1 | 10.88% | -9.08 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.117 | 459 | 300 | 0 | 24.6 | 434.4 | 445.9 | 11.5 | -0.58 | 12.095 | 10.784 | 1.122 | 7.786% | 447 | -0.8 | 13.368 | 11.337 | 12.6 | -0.122 | 1.179 | 7.409% | -6.72 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.117 | 220 | 62 | 0 | 62.5 | 157.5 | 163.7 | 6.2 | 0.43 | 5.722 | 5.519 | 1.037 | 6.928% | 164.9 | 0.6 | 6.751 | 5.86 | 7.4 | -0.122 | 1.152 | 6.053% | -4.14 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.117 | 230 | 60 | 0 | 65.7 | 164.3 | 169 | 4.7 | -0.33 | 5.074 | 5.12 | 0.991 | 9.555% | 169.4 | -0.5 | 5.604 | 5.436 | 5.1 | -0.122 | 1.031 | 9.181% | -6.27 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.117 | 420 | 260 | 0 | 44.8 | 375.2 | 382.8 | 7.6 | 0.38 | 7.152 | 10.12 | 0.707 | 10.78% | 383.1 | 0.5 | 7.278 | 10.629 | 7.9 | -0.122 | 0.685 | 10.81% | -9.26 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.117 | 420 | 70 | 0 | 106.2 | 313.8 | 322.9 | 9.1 | 0.1 | 8.989 | 11.415 | 0.787 | 9.003% | 324.1 | 0.1 | 10.137 | 11.989 | 10.3 | -0.122 | 0.846 | 8.294% | -5.94 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.117 | 400 | 70 | 0 | 51.7 | 348.3 | 347.5 | -0.8 | -4.47 | 3.657 | 11.725 | 0.312 | -97.54% | 348.8 | -6.2 | 6.69 | 12.314 | 0.5 | -0.122 | 0.543 | 162.7% | -135.78 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.117 | 732 | 658 | 0 | 19.2 | 712.8 | 730.2 | 17.4 | 1.6 | 15.776 | 14.916 | 1.058 | 8.207% | 733.9 | 2.2 | 18.916 | 15.836 | 21.1 | -0.122 | 1.194 | 7.057% | -6.58 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.117 | 327 | 137 | 11 | 46 | 270 | 280.2 | 10.2 | -0.14 | 10.348 | 7.424 | 1.394 | 6.254% | 283 | -0.2 | 13.24 | 7.805 | 13 | -0.122 | 1.696 | 5.117% | -4.05 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.117 | 212 | 130 | 14 | 45.2 | 152.8 | 163.6 | 10.8 | -1.65 | 12.387 | 4.652 | 2 | 3.83% | 164.5 | -2.3 | 13.944 | 4.89 | 11.7 | -0.122 | 2 | 3.687% | -2.54 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.117 | 20 | 0 | 0 | 18.5 | 1.5 | 24.5 | 23 | 1.33 | 21.662 | 0.47 | 2 | 0.1708% | 24.5 | 1.8 | 21.078 | 0.494 | 23 | -0.122 | 2 | 0.178% | -0.01 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | STM | -0.117 | 307.9 | 54.5 | 0 | 60.8 | 247.1 | 257.3 | 10.2 | 0.01 | 10.159 | 9.048 | 1.123 | 5.889% | 257.5 | 0 | 10.374 | 9.502 | 10.4 | -0.122 | 1.092 | 6.023% | -4.63 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | FOSS | -0.117 | 234 | 47 | 0 | 10.6 | 223.4 | 230.7 | 7.3 | -2.9 | 10.141 | 5.049 | 2 | 6.258% | 228.4 | -4 | 8.985 | 5.36 | 5 | -0.122 | 1.676 | 9.527% | -8.7 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.117 | 223 | 150 | 22 | 28.9 | 172.1 | 178.4 | 6.3 | -0.05 | 6.355 | 5.156 | 1.233 | 6.907% | 178.7 | -0.1 | 6.658 | 5.415 | 6.6 | -0.122 | 1.229 | 6.874% | -5.08 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.117 | 230 | 155 | 29 | 36.1 | 164.9 | 171.1 | 6.2 | -0.33 | 6.559 | 5.039 | 1.302 | 7.238% | 171.3 | -0.5 | 6.835 | 5.293 | 6.4 | -0.122 | 1.291 | 7.312% | -5.02 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.117 | 395 | 100 | 0 | 18.2 | 376.8 | 390.5 | 13.7 | 1.04 | 12.762 | 7.998 | 1.596 | 5.626% | 393.3 | 1.4 | 15.103 | 8.492 | 16.5 | -0.122 | 1.778 | 4.871% | -4.45 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.117 | 425 | 120 | 0 | 269.2 | 155.8 | 180.9 | 25.1 | 6.68 | 18.464 | 11.452 | 1.612 | 3.303% | 188.2 | 9.3 | 23.126 | 12.028 | 32.4 | -0.122 | 1.923 | 2.668% | -0.94 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.117 | 435 | 120 | 0 | 51.2 | 383.8 | 410.6 | 26.8 | 7.84 | 19.032 | 9.68 | 1.966 | 3.166% | 417.8 | 10.9 | 23.162 | 10.167 | 34 | -0.122 | 2 | 2.602% | -2.2 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.117 | 392 | 57 | 0 | 285.6 | 106.4 | 99.8 | -6.6 | -13.9 | 7.279 | 10.137 | 0.718 | -11.59% | 97.5 | -19.3 | 10.385 | 10.647 | -8.9 | -0.122 | 0.975 | -8.959% | 2.33 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.117 | 530 | 200 | 0 | 57 | 473 | 485.7 | 12.7 | 1.31 | 11.405 | 12.984 | 0.878 | 8.14% | 498.3 | 1.8 | 23.447 | 13.636 | 25.3 | -0.122 | 1.719 | 4.261% | -3.64 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.117 | 226 | 150 | 22 | 46.2 | 157.8 | 167.1 | 9.3 | 2.86 | 6.4 | 4.503 | 1.421 | 4.742% | 168.7 | 4 | 6.875 | 4.73 | 10.9 | -0.122 | 1.454 | 4.219% | -2.82 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.117 | 225 | 150 | 23 | 45.2 | 156.8 | 165.6 | 8.8 | 2.57 | 6.208 | 4.461 | 1.391 | 4.989% | 167 | 3.6 | 6.566 | 4.685 | 10.2 | -0.122 | 1.401 | 4.488% | -2.99 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.117 | 218 | 150 | 17 | 44.5 | 156.5 | 165 | 8.5 | 2.23 | 6.265 | 4.457 | 1.406 | 5.005% | 166.3 | 3.1 | 6.727 | 4.681 | 9.8 | -0.122 | 1.437 | 4.526% | -3.11 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.117 | 225 | 150 | 21 | 45.8 | 158.2 | 167.5 | 9.3 | 2.96 | 6.318 | 4.505 | 1.402 | 4.721% | 168.6 | 4.1 | 6.27 | 4.731 | 10.4 | -0.122 | 1.325 | 4.402% | -2.96 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.117 | 231 | 150 | 16 | 14.4 | 200.6 | 213.9 | 13.3 | 4.71 | 8.594 | 4.955 | 1.735 | 3.389% | 215 | 6.6 | 7.809 | 5.204 | 14.4 | -0.122 | 1.501 | 3.264% | -2.71 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.117 | 233 | 150 | 16 | 5.4 | 211.6 | 220.2 | 8.6 | 2.53 | 6.083 | 5.154 | 1.18 | 5.286% | 221.6 | 3.5 | 6.418 | 5.413 | 10 | -0.122 | 1.186 | 4.74% | -4.12 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.117 | 70 | 20 | 0 | 41.1 | 28.9 | 31.3 | 2.4 | -0.25 | 2.66 | 2.08 | 1.279 | 5.699% | 31.4 | -0.3 | 2.781 | 2.185 | 2.5 | -0.122 | 1.273 | 5.705% | -2.24 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.117 | 115 | 38 | 0 | 14.1 | 100.9 | 104.2 | 3.3 | -1.42 | 4.68 | 3.387 | 1.382 | 6.804% | 104.9 | -2 | 5.914 | 3.557 | 4 | -0.122 | 1.662 | 5.853% | -4.91 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.117 | 195 | 40 | 0 | 31.9 | 163.1 | 166.8 | 3.7 | -0.01 | 3.796 | 5.311 | 0.715 | 10.28% | 166.8 | 0 | 3.805 | 5.577 | 3.7 | -0.122 | 0.682 | 10.72% | -8.59 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | GT | -0.117 | 103 | 35 | 0 | 55.5 | 47.5 | 47.9 | 0.4 | -0.44 | 0.84 | 2.848 | 0.295 | 50.28% | 51 | -0.6 | 4.115 | 3.007 | 3.5 | -0.122 | 1.369 | 5.992% | -2.64 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.117 | 654 | 250 | 81.8 | 22.3 | 549.9 | 561.6 | 11.7 | 0.04 | 11.62 | 13.444 | 0.864 | 10.9% | 563.9 | 0.1 | 13.89 | 14.133 | 14 | -0.122 | 0.983 | 9.501% | -7.66 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.117 | 110 | 25 | 0 | 9.2 | 100.8 | 106.6 | 5.8 | -0.94 | 6.747 | 2.922 | 2 | 3.703% | 106.5 | -1.3 | 6.985 | 3.069 | 5.7 | -0.122 | 2 | 3.929% | -3.44 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.117 | 697.1 | 455 | 26.6 | 73.3 | 597.2 | 617.9 | 20.7 | -0.47 | 21.201 | 15.753 | 1.346 | 6.568% | 632.2 | -0.7 | 35.685 | 16.561 | 35 | -0.122 | 2 | 4.051% | -3.33 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.117 | 700.6 | 455 | 8.5 | 42.5 | 649.6 | 672 | 22.4 | 0.59 | 21.803 | 16.261 | 1.341 | 6.1% | 685.8 | 0.8 | 35.422 | 17.094 | 36.2 | -0.122 | 2 | 3.936% | -3.5 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.117 | 49.7 | 24 | 0 | 14.8 | 34.9 | 37.8 | 2.9 | 0.07 | 2.853 | 1.374 | 2 | 3.352% | 39.4 | 0.1 | 4.449 | 1.451 | 4.5 | -0.122 | 2 | 2.252% | -1.51 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.117 | 49.8 | 24 | 0 | 15 | 34.8 | 37.4 | 2.6 | 0.03 | 2.594 | 1.378 | 1.882 | 3.746% | 43.2 | 0 | 8.351 | 1.455 | 8.4 | -0.122 | 2 | 1.209% | -0.8 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.117 | 15 | 9 | 0 | 5.6 | 9.4 | 11.1 | 1.7 | 0.05 | 1.701 | 0.376 | 2 | 1.754% | 11.2 | 0.1 | 1.776 | 0.4 | 1.8 | -0.122 | 2 | 1.726% | -0.99 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.117 | 20 | 9 | 0 | 10.7 | 9.3 | 10.2 | 0.9 | 0.03 | 0.856 | 0.502 | 1.706 | 4.396% | 10.3 | 0 | 0.879 | 0.533 | 1 | -0.122 | 1.65 | 4.123% | -1.76 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.117 | 454 | 230 | 0 | 22.8 | 431.2 | 438.9 | 7.7 | 0.06 | 7.589 | 10.667 | 0.711 | 11.5% | 440.9 | 0.1 | 9.604 | 11.213 | 9.7 | -0.122 | 0.856 | 9.52% | -8.67 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.117 | 495 | 347 | 10 | 27.8 | 457.2 | 468.2 | 11 | 2.95 | 8.081 | 11.395 | 0.709 | 8.778% | 470.7 | 4.1 | 9.395 | 11.979 | 13.5 | -0.122 | 0.784 | 7.458% | -6.6 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.117 | 112 | 36 | 0 | 20.3 | 91.7 | 98.3 | 6.6 | 0 | 6.632 | 2.631 | 2 | 3.313% | 100.4 | 0 | 8.697 | 2.766 | 8.7 | -0.122 | 2 | 2.621% | -2.05 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.117 | 57 | 15 | 0 | 4.9 | 52.1 | 52.9 | 0.8 | -1.48 | 2.285 | 1.658 | 1.378 | 13.93% | 53 | -2.1 | 2.981 | 1.741 | 0.9 | -0.122 | 1.712 | 12.91% | -11.26 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.117 | 41 | 13 | 0 | 27.5 | 13.5 | 14.4 | 0.9 | 0.12 | 0.736 | 1.029 | 0.716 | 8.946% | 14 | 0.2 | 0.322 | 1.092 | 0.5 | -0.122 | 0.294 | 16.79% | -5.15 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.117 | 231 | 130 | 0 | 44.8 | 186.2 | 193.1 | 6.9 | 0.4 | 6.489 | 5.427 | 1.196 | 6.532% | 192.7 | 0.5 | 5.932 | 5.705 | 6.5 | -0.122 | 1.04 | 7.231% | -5.58 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.117 | 235 | 51 | 0 | 144.3 | 90.7 | 86.2 | -4.5 | -7.38 | 2.899 | 5.29 | 0.548 | -10.2% | 81.6 | -10.3 | 1.169 | 5.617 | -9.1 | -0.122 | 0.208 | -5.257% | 1.94 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.109 | 459 | 300 | 0 | 26.1 | 432.9 | 442.9 | 10 | 0.2 | 9.842 | 9.476 | 1.039 | 8.341% | 444.1 | 0.3 | 10.945 | 10.013 | 11.2 | -0.113 | 1.093 | 7.721% | -7.02 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.109 | 220 | 62 | 0 | 49.1 | 170.9 | 173.4 | 2.5 | -2.71 | 5.207 | 4.712 | 1.105 | 16.01% | 176 | -3.8 | 8.794 | 5.044 | 5.1 | -0.113 | 1.743 | 8.135% | -6.08 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.109 | 230 | 60 | 0 | 50.4 | 179.6 | 179.8 | 0.2 | -2.47 | 2.673 | 4.336 | 0.617 | 209.2% | 180.5 | -3.4 | 4.377 | 4.641 | 0.9 | -0.113 | 0.943 | 48.19% | -36.19 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.109 | 410 | 70 | 0 | 13.4 | 396.6 | 408.1 | 11.5 | -4.85 | 16.339 | 6.938 | 2 | 6.482% | 411.2 | -6.8 | 21.314 | 7.426 | 14.6 | -0.113 | 2 | 5.293% | -4.93 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.109 | 785 | 575 | 0 | 73.7 | 711.3 | 724.7 | 13.4 | -0.36 | 13.804 | 19.923 | 0.693 | 10.64% | 732.1 | -0.5 | 21.324 | 21.028 | 20.8 | -0.113 | 1.014 | 7.109% | -6.21 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.109 | 420 | 220 | 0 | 46.5 | 373.5 | 380.6 | 7.1 | -0.17 | 7.286 | 8.91 | 0.818 | 10.75% | 381.7 | -0.2 | 8.449 | 9.405 | 8.2 | -0.113 | 0.898 | 9.65% | -8.27 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.109 | 335 | 70 | 0 | 12 | 323 | 323.8 | 0.8 | -5.94 | 6.683 | 8.678 | 0.77 | 76.11% | 322.6 | -8.3 | 7.89 | 9.16 | -0.4 | -0.113 | 0.861 | -157.8% | 146.63 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.109 | 105 | 12 | 0 | 44.9 | 60.1 | 64.4 | 4.3 | 1.3 | 2.916 | 2.713 | 1.075 | 4.443% | 64.7 | 1.8 | 2.72 | 2.864 | 4.6 | -0.113 | 0.95 | 4.305% | -2.37 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.109 | 326 | 138 | 11 | 60.2 | 254.8 | 263.8 | 9 | 0.07 | 8.915 | 6.503 | 1.371 | 6.584% | 265.6 | 0.1 | 10.724 | 6.872 | 10.8 | -0.113 | 1.56 | 5.688% | -4.28 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.109 | 566 | 149 | 0 | 12.5 | 553.5 | 561.5 | 8 | 0.11 | 7.885 | 10.803 | 0.73 | 12.86% | 559.8 | 0.1 | 6.139 | 11.402 | 6.3 | -0.113 | 0.538 | 16.92% | -15.96 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.109 | 566 | 149 | 0 | 12.5 | 553.5 | 561.5 | 8 | 0.11 | 7.885 | 10.803 | 0.73 | 12.86% | 559.8 | 0.1 | 6.139 | 11.402 | 6.3 | -0.113 | 0.538 | 16.92% | -15.96 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | STM | -0.109 | 103.8 | 18.8 | 0 | 9.1 | 94.7 | 98.1 | 3.4 | -0.24 | 3.565 | 2.762 | 1.291 | 5.555% | 98.5 | -0.3 | 4.06 | 2.915 | 3.8 | -0.113 | 1.393 | 5.152% | -4.52 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.109 | 121.3 | 19.3 | 0 | 25.6 | 95.7 | 100.4 | 4.7 | -0.22 | 4.9 | 3.229 | 1.518 | 4.695% | 100.7 | -0.3 | 5.261 | 3.408 | 5 | -0.113 | 1.544 | 4.575% | -3.47 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.109 | 307.8 | 54.8 | 0 | 60.7 | 247.1 | 256.2 | 9.1 | 0.08 | 8.951 | 7.968 | 1.123 | 6.148% | 256.5 | 0.1 | 9.304 | 8.41 | 9.4 | -0.113 | 1.106 | 6.17% | -4.77 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | COGN | -0.109 | 229 | 155 | 29 | 24.2 | 175.8 | 181.1 | 5.3 | -0.03 | 5.326 | 4.572 | 1.165 | 7.855% | 181.7 | 0 | 5.92 | 4.826 | 5.9 | -0.113 | 1.227 | 7.315% | -5.41 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.109 | 425 | 120 | 0 | 96.6 | 328.4 | 333.6 | 5.2 | -8.71 | 13.947 | 8.922 | 1.563 | 14.85% | 335.6 | -12.1 | 19.405 | 9.417 | 7.2 | -0.113 | 2 | 11.12% | -8.28 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.109 | 425 | 120 | 0 | 77.7 | 347.3 | 363.2 | 15.9 | 0.87 | 15.069 | 8.695 | 1.733 | 4.858% | 364.7 | 1.2 | 16.159 | 9.178 | 17.4 | -0.113 | 1.761 | 4.602% | -3.62 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.109 | 174 | 0 | 0 | 12.1 | 161.9 | 168.2 | 6.3 | 0.14 | 6.208 | 3.592 | 1.728 | 5.022% | 165.5 | 0.2 | 3.495 | 3.796 | 3.6 | -0.113 | 0.921 | 9.111% | -8.16 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.109 | 122 | 15 | 0 | 7.3 | 114.7 | 114.7 | 0 | -0.22 | 0.218 | 2.365 | 0.092 | 0% | 114.9 | -0.3 | 0.488 | 2.531 | 0.2 | -0.113 | 0.193 | 115.2% | -103.9 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.109 | 226 | 150 | 22 | 38.7 | 165.3 | 170 | 4.7 | -0.16 | 4.814 | 3.959 | 1.216 | 8.741% | 171.1 | -0.2 | 5.993 | 4.178 | 5.8 | -0.113 | 1.434 | 7.343% | -5.17 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.109 | 225 | 150 | 23 | 38.7 | 163.3 | 168.4 | 5.1 | -0.24 | 5.257 | 3.922 | 1.34 | 8.02% | 169.5 | -0.3 | 6.474 | 4.14 | 6.2 | -0.113 | 1.564 | 6.839% | -4.78 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.109 | 218 | 150 | 17 | 38.4 | 162.6 | 167.2 | 4.6 | -0.17 | 4.772 | 3.92 | 1.218 | 8.616% | 168.3 | -0.2 | 5.903 | 4.137 | 5.7 | -0.113 | 1.427 | 7.208% | -5.18 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.109 | 225 | 150 | 21 | 38.6 | 165.4 | 170.4 | 5 | -0.23 | 5.189 | 3.96 | 1.31 | 8.181% | 171.1 | -0.3 | 6.009 | 4.179 | 5.7 | -0.113 | 1.438 | 7.439% | -5.27 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.109 | 231 | 150 | 16 | 13.1 | 201.9 | 206.9 | 5 | -0.2 | 5.202 | 4.406 | 1.181 | 8.399% | 207.7 | -0.3 | 6.118 | 4.65 | 5.8 | -0.113 | 1.316 | 7.506% | -6.32 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.109 | 70 | 20 | 0 | 8.6 | 61.4 | 64.3 | 2.9 | 0.53 | 2.393 | 1.773 | 1.349 | 4.395% | 64.4 | 0.7 | 2.31 | 1.872 | 3 | -0.113 | 1.234 | 4.404% | -3.71 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.109 | 110 | 38 | 0 | 6.1 | 103.9 | 108.3 | 4.4 | -4.06 | 8.443 | 2.85 | 2 | 4.548% | 108.9 | -5.6 | 10.675 | 3.008 | 5 | -0.113 | 2 | 4.149% | -3.77 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.109 | 184 | 40 | 0 | 7.3 | 176.7 | 178.5 | 1.8 | -2.69 | 4.465 | 4.376 | 1.02 | 18.59% | 178.3 | -3.7 | 5.26 | 4.619 | 1.6 | -0.113 | 1.139 | 21.68% | -20.05 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | GT | -0.109 | 103 | 35 | 0 | 27.2 | 75.8 | 73.1 | -2.7 | -3.85 | 1.109 | 2.503 | 0.443 | -6.941% | 75.6 | -5.4 | 5.128 | 2.658 | -0.2 | -0.113 | 1.929 | -97.13% | 68.71 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | FOSS | -0.109 | 138 | 25 | 0 | 9.2 | 128.8 | 134.5 | 5.7 | -0.71 | 6.377 | 3.392 | 1.88 | 4.403% | 133.7 | -1 | 5.885 | 3.58 | 4.9 | -0.113 | 1.644 | 5.31% | -4.77 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.109 | 694.1 | 406.5 | 27 | 75.7 | 591.4 | 607.4 | 16 | -0.35 | 16.434 | 13.772 | 1.193 | 7.883% | 619.1 | -0.5 | 28.235 | 14.553 | 27.7 | -0.113 | 1.94 | 4.72% | -3.88 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.109 | 63 | 35 | 0 | 27.7 | 35.3 | 38.4 | 3.1 | -0.27 | 3.326 | 1.531 | 2 | 3.701% | 38.7 | -0.4 | 3.677 | 1.626 | 3.4 | -0.113 | 2 | 3.498% | -1.88 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.109 | 64 | 35 | 0 | 28.8 | 35.2 | 38 | 2.8 | -0.29 | 3.115 | 1.556 | 2 | 4.163% | 38.4 | -0.4 | 3.568 | 1.651 | 3.2 | -0.113 | 2 | 3.776% | -1.99 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.109 | 64 | 35 | 0 | 28.2 | 35.8 | 38.9 | 3.1 | -0.27 | 3.352 | 1.556 | 2 | 3.76% | 39.1 | -0.4 | 3.614 | 1.651 | 3.3 | -0.113 | 2 | 3.661% | -1.96 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.109 | 65 | 37 | 0 | 27.8 | 37.2 | 40.2 | 3 | -0.27 | 3.262 | 1.58 | 2 | 3.946% | 40.5 | -0.4 | 3.581 | 1.677 | 3.3 | -0.113 | 2 | 3.718% | -2.04 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.109 | 49.7 | 24 | 0 | 6.9 | 42.8 | 44.4 | 1.6 | -0.11 | 1.724 | 1.208 | 1.427 | 5.661% | 46.5 | -0.2 | 3.911 | 1.283 | 3.7 | -0.113 | 2 | 2.537% | -2.09 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.109 | 49.9 | 24 | 0 | 7.3 | 42.6 | 44.4 | 1.8 | -0.12 | 1.841 | 1.212 | 1.52 | 5.052% | 45.7 | -0.2 | 3.28 | 1.286 | 3.1 | -0.113 | 2 | 3.041% | -2.49 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.109 | 451.6 | 230 | 0 | 39.4 | 412.2 | 421.5 | 9.3 | -0.12 | 9.368 | 9.323 | 1.005 | 8.825% | 425.6 | -0.2 | 13.564 | 9.852 | 13.4 | -0.113 | 1.377 | 6.349% | -5.59 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.109 | 223.5 | 170 | 0 | 8.3 | 215.2 | 215 | -0.2 | -0.24 | 0.079 | 4.614 | 0.017 | -203.2% | 214.8 | -0.3 | -0.029 | 4.876 | -0.4 | -0.113 | 0 | -105.3% | 97.67 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.109 | 114 | 36 | 0 | 20.4 | 93.6 | 99 | 5.4 | -0.04 | 5.416 | 2.353 | 2 | 3.84% | 99.8 | 0 | 6.261 | 2.487 | 6.2 | -0.113 | 2 | 3.467% | -2.74 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.109 | 41 | 13 | 0 | 11.9 | 29.1 | 30.3 | 1.2 | -0.12 | 1.254 | 0.878 | 1.428 | 6.254% | 30.5 | -0.2 | 1.55 | 0.94 | 1.4 | -0.113 | 1.649 | 5.556% | -3.74 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.109 | 231 | 130 | 0 | 45.3 | 185.7 | 192.1 | 6.4 | -0.4 | 6.804 | 4.769 | 1.427 | 6.561% | 192.1 | -0.5 | 6.914 | 5.039 | 6.4 | -0.113 | 1.372 | 6.802% | -5.27 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.109 | 40 | 13 | 0 | 16.5 | 23.5 | 30.6 | 7.1 | 4.07 | 3.024 | 0.972 | 2 | 1.027% | 33.4 | 5.7 | 4.192 | 1.032 | 9.9 | -0.113 | 2 | 0.7638% | -0.43 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.109 | 40 | 13 | 0 | 15.8 | 24.2 | 30.1 | 5.9 | 4.43 | 1.568 | 0.972 | 1.613 | 1.236% | 33.4 | 6.2 | 3.085 | 1.032 | 9.2 | -0.113 | 2 | 0.8219% | -0.47 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.084 | 190 | 85 | 0 | 43.7 | 146.3 | 150.5 | 4.2 | 0.21 | 3.973 | 4.402 | 0.903 | 6.34% | 152.7 | 0.3 | 6.062 | 4.603 | 6.4 | -0.087 | 1.317 | 4.309% | -3.2 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | FOSS | -0.084 | 125 | 55 | 0 | 24.2 | 100.8 | 103.4 | 2.6 | -0.12 | 2.739 | 1.711 | 1.601 | 6.753% | 109.1 | -0.2 | 8.505 | 1.801 | 8.3 | -0.087 | 2 | 2.191% | -1.69 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 228 | 159 | 0 | 42.4 | 185.6 | 191.4 | 5.8 | 0.06 | 5.692 | 4.486 | 1.269 | 5.508% | 191.3 | 0.1 | 5.575 | 4.675 | 5.7 | -0.087 | 1.193 | 5.805% | -4.55 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 502 | 327 | 49 | 64.6 | 388.4 | 396.4 | 8 | 0.35 | 7.656 | 8.914 | 0.859 | 8.789% | 398.6 | 0.5 | 9.736 | 9.289 | 10.2 | -0.087 | 1.048 | 7.139% | -5.33 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.084 | 220 | 62 | 0 | 49.3 | 170.7 | 178.2 | 7.5 | -0.05 | 7.565 | 4.439 | 1.704 | 4.114% | 180.4 | -0.1 | 9.767 | 4.673 | 9.7 | -0.087 | 2 | 3.295% | -2.46 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 230 | 60 | 0 | 144.7 | 85.3 | 93.3 | 8 | -0.66 | 8.626 | 4.352 | 1.982 | 4.032% | 94.2 | -0.9 | 9.783 | 4.582 | 8.9 | -0.087 | 2 | 3.754% | -1.34 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 410 | 70 | 0 | 97.6 | 312.4 | 315 | 2.6 | -0.75 | 3.376 | 6.631 | 0.509 | 22.1% | 323.2 | -1 | 11.88 | 6.981 | 10.8 | -0.087 | 1.702 | 5.51% | -4.04 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.084 | 420 | 180 | 0 | 31.3 | 388.7 | 395.6 | 6.9 | -0.19 | 7.133 | 8.57 | 0.832 | 8.526% | 397 | -0.3 | 8.555 | 8.922 | 8.3 | -0.087 | 0.959 | 7.341% | -6.55 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 420 | 70 | 0 | 160.9 | 259.1 | 269.2 | 10.1 | 0 | 10.089 | 8.797 | 1.147 | 5.825% | 275.5 | 0 | 16.384 | 9.159 | 16.4 | -0.087 | 1.789 | 3.715% | -2.21 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 335 | 70 | 0 | 62.2 | 272.8 | 287.4 | 14.6 | 1 | 13.608 | 7.754 | 1.755 | 3.214% | 288.9 | 1.4 | 14.748 | 8.073 | 16.1 | -0.087 | 1.827 | 3.019% | -2.37 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 512 | 360 | 0 | 16.1 | 495.9 | 498.7 | 2.8 | -0.45 | 3.206 | 10.075 | 0.318 | 25.61% | 499.1 | -0.6 | 3.843 | 10.498 | 3.2 | -0.087 | 0.366 | 23.21% | -21.69 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.084 | 105 | 12 | 0 | 86.9 | 18.1 | 21.2 | 3.1 | -0.35 | 3.416 | 2.667 | 1.281 | 4.751% | 21.5 | -0.5 | 3.902 | 2.776 | 3.4 | -0.087 | 1.405 | 4.486% | -0.74 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 315 | 50 | 0 | 19 | 296 | 316.2 | 20.2 | 0.22 | 20.016 | 6.536 | 2 | 2.185% | 317.8 | 0.3 | 21.535 | 6.804 | 21.8 | -0.087 | 2 | 2.096% | -1.9 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 326 | 138 | 11 | 59.9 | 255.1 | 264 | 8.9 | 0.01 | 8.907 | 6.198 | 1.437 | 5.131% | 265.8 | 0 | 10.668 | 6.459 | 10.7 | -0.087 | 1.652 | 4.42% | -3.34 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 20 | 0 | 0 | 18.4 | 1.6 | 19.6 | 18 | -0.52 | 18.596 | 0.394 | 2 | 0.1571% | 20.6 | -0.7 | 19.794 | 0.41 | 19 | -0.087 | 2 | 0.1541% | -0.01 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | STM | -0.084 | 103.9 | 18.9 | 0 | 21.8 | 82.1 | 86.4 | 4.3 | -0.03 | 4.299 | 2.642 | 1.627 | 3.389% | 86.7 | 0 | 4.61 | 2.75 | 4.6 | -0.087 | 1.676 | 3.281% | -2.49 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.084 | 121.4 | 19.4 | 0 | 25.1 | 96.3 | 99.8 | 3.5 | 0.26 | 3.223 | 3.083 | 1.045 | 4.864% | 100.1 | 0.4 | 3.407 | 3.209 | 3.8 | -0.087 | 1.062 | 4.64% | -3.54 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.084 | 307.8 | 54.8 | 0 | 61.2 | 246.6 | 255.1 | 8.5 | 0 | 8.456 | 7.607 | 1.112 | 5.073% | 255.2 | 0 | 8.622 | 7.919 | 8.6 | -0.087 | 1.089 | 5.193% | -4.01 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | FOSS | -0.084 | 234 | 47 | 0 | 116.3 | 117.7 | 127.7 | 10 | 0.36 | 9.663 | 4.347 | 2 | 3.282% | 127.4 | 0.5 | 9.193 | 4.576 | 9.7 | -0.087 | 2 | 3.504% | -1.69 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 390 | 40 | 0 | 290.1 | 99.9 | 117.1 | 17.2 | 0.26 | 16.885 | 6.987 | 2 | 3.178% | 117.9 | 0.4 | 17.588 | 7.355 | 18 | -0.087 | 2 | 3.145% | -0.77 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 395 | 100 | 0 | 143.1 | 251.9 | 281.7 | 29.8 | -1.82 | 31.676 | 5.961 | 2 | 1.858% | 271.5 | -2.5 | 22.181 | 6.275 | 19.6 | -0.087 | 2 | 2.925% | -1.8 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 435 | 120 | 0 | 314.8 | 120.2 | 133.2 | 13 | 0.15 | 12.762 | 10.211 | 1.25 | 4.687% | 135.5 | 0.2 | 15.059 | 10.631 | 15.3 | -0.087 | 1.417 | 4.124% | -1.1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 435 | 120 | 0 | 314.6 | 120.4 | 132 | 11.6 | 0.29 | 11.389 | 10.22 | 1.114 | 5.252% | 132.3 | 0.4 | 11.552 | 10.639 | 11.9 | -0.087 | 1.086 | 5.303% | -1.41 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 177.6 | 0 | 0 | 40.2 | 137.4 | 143.5 | 6.1 | 0.25 | 5.855 | 3.495 | 1.675 | 4.081% | 141.8 | 0.4 | 4.053 | 3.642 | 4.4 | -0.087 | 1.113 | 5.859% | -4.37 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.084 | 92 | 35 | 0 | 40.7 | 51.3 | 54.2 | 2.9 | 0.15 | 2.803 | 2.132 | 1.315 | 4.451% | 54.2 | 0.2 | 2.687 | 2.229 | 2.9 | -0.087 | 1.205 | 4.61% | -2.47 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.084 | 82 | 35 | 0 | 46.3 | 35.7 | 38.7 | 3 | 0.24 | 2.67 | 1.9 | 1.405 | 3.836% | 38.6 | 0.3 | 2.556 | 1.987 | 2.9 | -0.087 | 1.287 | 4.11% | -1.71 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | FOSS | -0.084 | 122 | 15 | 0 | 72.4 | 49.6 | 49.6 | 0 | -0.44 | 0.47 | 2.338 | 0.201 | 0% | 50.1 | -0.6 | 1.16 | 2.462 | 0.5 | -0.087 | 0.471 | 35.49% | -13.77 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.084 | 229 | 150 | 22 | 37.6 | 169.4 | 173.5 | 4.1 | 0.28 | 3.896 | 3.871 | 1.007 | 7.826% | 173.7 | 0.4 | 3.974 | 4.03 | 4.3 | -0.087 | 0.986 | 7.729% | -5.51 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.084 | 228 | 150 | 23 | 37.7 | 167.3 | 171.7 | 4.4 | 0.12 | 4.221 | 3.807 | 1.109 | 7.261% | 171.8 | 0.2 | 4.348 | 3.964 | 4.5 | -0.087 | 1.097 | 7.353% | -5.2 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.084 | 218 | 150 | 17 | 37.5 | 163.5 | 167.8 | 4.3 | 0.12 | 4.182 | 3.738 | 1.119 | 7.104% | 168 | 0.2 | 4.297 | 3.892 | 4.5 | -0.087 | 1.104 | 7.031% | -5.08 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.084 | 228 | 150 | 21 | 37.6 | 169.4 | 173.7 | 4.3 | 0.29 | 3.947 | 3.874 | 1.019 | 7.43% | 174 | 0.4 | 4.123 | 4.033 | 4.6 | -0.087 | 1.022 | 7.193% | -5.15 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.084 | 233 | 150 | 16 | 12.1 | 204.9 | 209 | 4.1 | 0.18 | 3.889 | 4.279 | 0.909 | 7.963% | 210.2 | 0.2 | 5.008 | 4.454 | 5.3 | -0.087 | 1.124 | 6.38% | -5.41 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.084 | 70 | 20 | 0 | 42.4 | 27.6 | 31.2 | 3.6 | 0.89 | 2.722 | 1.749 | 1.556 | 2.73% | 31 | 1.2 | 2.179 | 1.821 | 3.4 | -0.087 | 1.196 | 2.994% | -1.13 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.084 | 110 | 38 | 0 | 43.5 | 66.5 | 68.4 | 1.9 | 0.56 | 1.33 | 2.762 | 0.482 | 8.12% | 70.4 | 0.8 | 3.095 | 2.875 | 3.9 | -0.087 | 1.077 | 4.097% | -2.38 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.084 | 184 | 40 | 0 | 35.4 | 148.6 | 157.2 | 8.6 | 1.5 | 7.027 | 4.243 | 1.656 | 2.999% | 157.9 | 2.1 | 7.227 | 4.418 | 9.3 | -0.087 | 1.636 | 2.872% | -2.23 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | GT | -0.084 | 102 | 35 | 0 | 46.3 | 55.7 | 62.7 | 7 | 0 | 7.04 | 2.363 | 2 | 2.044% | 66.8 | 0 | 11.08 | 2.471 | 11.1 | -0.087 | 2 | 1.335% | -0.7 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.084 | 102 | 35 | 0 | 45.7 | 56.3 | 62.7 | 6.4 | 0 | 6.452 | 2.363 | 2 | 2.236% | 67 | 0 | 10.71 | 2.471 | 10.7 | -0.087 | 2 | 1.385% | -0.73 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | FOSS | -0.084 | 138 | 25 | 0 | 110.5 | 27.5 | 32.5 | 5 | 0.35 | 4.641 | 1.836 | 2 | 3.87% | 31.7 | 0.5 | 3.665 | 1.911 | 4.2 | -0.087 | 1.918 | 4.771% | -0.91 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 694.6 | 395.4 | 20.3 | 50 | 624.3 | 643 | 18.7 | -0.71 | 19.336 | 13.268 | 1.457 | 5.202% | 646.8 | -1 | 23.457 | 13.826 | 22.5 | -0.087 | 1.697 | 4.478% | -3.88 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 693.2 | 405.8 | 28.3 | 81 | 583.9 | 599 | 15.1 | -0.24 | 15.332 | 13.083 | 1.172 | 6.429% | 611.9 | -0.3 | 28.343 | 13.633 | 28 | -0.087 | 2 | 3.591% | -2.92 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 703 | 405.1 | 21.1 | 67.2 | 614.7 | 629.3 | 14.6 | -0.18 | 14.713 | 13.418 | 1.097 | 6.743% | 642.7 | -0.2 | 28.232 | 13.982 | 28 | -0.087 | 2 | 3.642% | -3.07 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.084 | 49.7 | 24 | 0 | 13.8 | 35.9 | 39 | 3.1 | 0.34 | 2.748 | 1.152 | 2 | 2.254% | 45.6 | 0.5 | 9.158 | 1.204 | 9.7 | -0.087 | 2 | 0.7459% | -0.52 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 49.8 | 24 | 0 | 14.2 | 35.6 | 38.5 | 2.9 | 0.14 | 2.755 | 1.155 | 2 | 2.414% | 45.1 | 0.2 | 9.324 | 1.208 | 9.5 | -0.087 | 2 | 0.7631% | -0.52 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 457.9 | 230 | 0 | 23 | 434.9 | 444.2 | 9.3 | 0.41 | 8.873 | 9.01 | 0.985 | 6.896% | 448.5 | 0.6 | 13.011 | 9.389 | 13.6 | -0.087 | 1.386 | 4.884% | -4.47 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 112 | 36 | 0 | 20.4 | 91.6 | 98.2 | 6.6 | 0.01 | 6.541 | 2.204 | 2 | 2.38% | 99.3 | 0 | 7.662 | 2.297 | 7.7 | -0.087 | 2 | 2.113% | -1.66 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.084 | 167 | 55 | 0 | 111.5 | 55.5 | 60.7 | 5.2 | 0.99 | 4.243 | 3.056 | 1.388 | 4.507% | 60.7 | 1.4 | 3.851 | 3.218 | 5.2 | -0.087 | 1.197 | 4.668% | -1.48 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 440 | 35 | 0 | 344.8 | 95.2 | 106.3 | 11.1 | -3.72 | 14.839 | 8.13 | 1.825 | 5.555% | 99 | -5.2 | 8.95 | 8.559 | 3.8 | -0.087 | 1.046 | 16.8% | -3.49 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 57 | 15 | 0 | 41.2 | 15.8 | 17.5 | 1.7 | 0.18 | 1.492 | 1.039 | 1.435 | 4.711% | 17.1 | 0.2 | 1.054 | 1.082 | 1.3 | -0.087 | 0.974 | 6.379% | -1.68 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 26 | 10 | 0 | 15.5 | 10.5 | 10.3 | -0.2 | -0.18 | 0.01 | 0.525 | 0.019 | -18.48% | 10.5 | -0.2 | 0.291 | 0.552 | 0 | -0.087 | 0.527 | 0% |  | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 265 | 100 | 20 | 8.5 | 236.5 | 237.3 | 0.8 | -0.45 | 1.328 | 4.821 | 0.275 | 46.41% | 237.8 | -0.6 | 1.929 | 5.024 | 1.3 | -0.087 | 0.384 | 29.58% | -25.45 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 231 | 130 | 0 | 44.1 | 186.9 | 191.7 | 4.8 | 0.52 | 4.216 | 4.545 | 0.928 | 6.743% | 192.1 | 0.7 | 4.416 | 4.737 | 5.2 | -0.087 | 0.932 | 6.447% | -5.03 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 348 | 249 | 19 | 8 | 321 | 322.4 | 1.4 | -0.06 | 1.539 | 6.474 | 0.238 | 34.82% | 322.2 | -0.1 | 1.325 | 6.746 | 1.2 | -0.087 | 0.196 | 42.07% | -37.43 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.084 | 155 | 73 | 0 | 47.8 | 107.2 | 119.9 | 12.7 | -1.41 | 14.062 | 2.782 | 2 | 1.713% | 118.8 | -2 | 13.579 | 2.929 | 11.6 | -0.087 | 2 | 1.942% | -1.29 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 672 | 300 | 8.9 | 32.3 | 630.8 | 644.2 | 13.4 | 0.86 | 12.597 | 13.048 | 0.965 | 7.023% | 648.4 | 1.2 | 16.38 | 13.597 | 17.6 | -0.087 | 1.205 | 5.538% | -5.02 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.084 | 43 | 13 | 0 | 29.6 | 13.4 | 14.9 | 1.5 | 0.06 | 1.503 | 0.996 | 1.508 | 4.032% | 15.2 | 0.1 | 1.761 | 1.042 | 1.8 | -0.087 | 1.69 | 3.48% | -1.03 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.071 | 513.6 | 275 | 12 | 37.1 | 464.5 | 466 | 1.5 | -2.42 | 3.913 | 5.896 | 0.664 | 40.54% | 477.5 | -3.4 | 16.379 | 5.682 | 13 | -0.069 | 2 | 4.546% | -4.23 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.071 | 227 | 166 | 48.5 | 8.6 | 169.9 | 173.8 | 3.9 | 0.53 | 3.367 | 2.098 | 1.605 | 6.895% | 173.7 | 0.7 | 3.047 | 2.022 | 3.8 | -0.069 | 1.507 | 6.877% | -5.28 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.071 | 503 | 340 | 62.8 | 10.6 | 429.6 | 434.1 | 4.5 | 0.35 | 4.164 | 5.174 | 0.805 | 13.23% | 436.2 | 0.5 | 6.15 | 4.987 | 6.6 | -0.069 | 1.233 | 8.769% | -7.7 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.071 | 220 | 62 | 0 | 39.5 | 180.5 | 183.5 | 3 | 0.37 | 2.561 | 2.197 | 1.166 | 8.697% | 185.2 | 0.5 | 4.114 | 2.077 | 4.7 | -0.069 | 1.981 | 5.395% | -4.53 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.071 | 410 | 70 | 0 | 71.5 | 338.5 | 344.9 | 6.4 | 0.38 | 6.058 | 3.268 | 1.854 | 7.59% | 347.6 | 0.5 | 8.593 | 3.088 | 9.1 | -0.069 | 2 | 5.188% | -4.4 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.071 | 560 | 400 | 0 | 41.8 | 518.2 | 527.6 | 9.4 | -0.5 | 9.909 | 8.753 | 1.132 | 7.053% | 529.8 | -0.7 | 12.277 | 8.448 | 11.6 | -0.069 | 1.453 | 5.554% | -5.28 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.071 | 420 | 260 | 0 | 15.6 | 404.4 | 409.8 | 5.4 | 0.36 | 5.046 | 5.22 | 0.967 | 9.209% | 408 | 0.5 | 3.089 | 5.038 | 3.6 | -0.069 | 0.613 | 13.42% | -13.28 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.071 | 420 | 70 | 0 | 139.5 | 280.5 | 283.9 | 3.4 | -1.16 | 4.603 | 5.624 | 0.819 | 14.63% | 285.6 | -1.6 | 6.782 | 5.428 | 5.1 | -0.069 | 1.25 | 9.476% | -6.5 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.071 | 380 | 70 | 0 | 95.2 | 284.8 | 291.2 | 6.4 | -2.23 | 8.606 | 5.506 | 1.563 | 7.03% | 290.2 | -3.1 | 8.476 | 5.314 | 5.4 | -0.069 | 1.595 | 8.098% | -6.24 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.071 | 749 | 625 | 0 | 99.7 | 649.3 | 657.4 | 8.1 | -0.29 | 8.329 | 6.217 | 1.34 | 10.95% | 658.6 | -0.4 | 9.699 | 5.876 | 9.3 | -0.069 | 1.651 | 9.268% | -8.26 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.071 | 357 | 150 | 68 | 18.9 | 270.1 | 271.8 | 1.7 | 0.35 | 1.348 | 3.397 | 0.397 | 24.87% | 270.9 | 0.5 | 0.322 | 3.274 | 0.8 | -0.069 | 0.098 | 51.35% | -39.92 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.071 | 315 | 50 | 0 | 49.2 | 265.8 | 274.4 | 8.6 | -1.05 | 9.607 | 3.929 | 2 | 4.338% | 275.6 | -1.5 | 11.184 | 3.792 | 9.8 | -0.069 | 2 | 3.699% | -3.21 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.071 | 212 | 130 | 5.1 | 19.6 | 187.3 | 190.9 | 3.6 | 0.43 | 3.242 | 2.432 | 1.333 | 6.976% | 191.8 | 0.6 | 3.942 | 2.344 | 4.5 | -0.069 | 1.682 | 5.424% | -4.92 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.071 | 40 | 0 | 0 | 38.4 | 1.6 | 15.1 | 13.5 | 1.18 | 12.302 | 0.47 | 2 | 0.3527% | 13.6 | 1.6 | 10.308 | 0.453 | 12 | -0.069 | 2 | 0.3857% | -0.01 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.071 | 256 | 160 | 0 | 5.3 | 250.7 | 251.3 | 0.6 | 0 | 0.633 | 3.009 | 0.21 | 50.54% | 250.7 | 0 | 0 | 2.9 | 0 | -0.069 | 0 | 0% |  | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | STM | -0.071 | 308.9 | 55.9 | 0 | 145.5 | 163.4 | 170 | 6.6 | 0.01 | 6.627 | 4.697 | 1.411 | 5.543% | 169.8 | 0 | 6.327 | 4.533 | 6.4 | -0.069 | 1.396 | 5.555% | -3.02 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.071 | 477 | 345 | 49.9 | 9.1 | 418 | 428.5 | 10.5 | 0.29 | 10.186 | 5.02 | 2 | 5.378% | 428.9 | 0.4 | 10.484 | 4.838 | 10.9 | -0.069 | 2 | 5.035% | -4.54 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.071 | 225 | 150 | 22 | 39.1 | 163.9 | 167.1 | 3.2 | 0 | 3.208 | 2.588 | 1.239 | 8.329% | 167.9 | 0 | 4.06 | 2.498 | 4 | -0.069 | 1.625 | 6.476% | -4.84 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.071 | 231 | 155 | 29 | 38.1 | 163.9 | 167.9 | 4 | -0.22 | 4.27 | 2.576 | 1.658 | 6.841% | 167.9 | -0.3 | 4.354 | 2.486 | 4 | -0.069 | 1.751 | 6.648% | -4.84 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.071 | 232 | 150 | 29 | 31.5 | 171.5 | 175.1 | 3.6 | -0.11 | 3.71 | 2.651 | 1.399 | 7.634% | 175.5 | -0.2 | 4.157 | 2.559 | 4 | -0.069 | 1.625 | 6.677% | -5.07 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.071 | 228 | 150 | 21 | 23.9 | 183.1 | 186.4 | 3.3 | -0.04 | 3.296 | 2.802 | 1.176 | 8.184% | 187.2 | -0.1 | 4.135 | 2.705 | 4.1 | -0.069 | 1.529 | 6.402% | -5.28 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.071 | 395 | 100 | 0 | 88.1 | 306.9 | 314 | 7.1 | -2.85 | 10 | 3.089 | 2 | 6.591% | 310.2 | -4 | 7.298 | 2.919 | 3.3 | -0.069 | 2 | 13.78% | -10.99 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.071 | 425 | 120 | 0 | 304.5 | 120.5 | 131.1 | 10.6 | 1.45 | 9.143 | 6.062 | 1.508 | 4.747% | 136.2 | 2 | 13.698 | 5.851 | 15.7 | -0.069 | 2 | 3.115% | -0.91 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.071 | 178.1 | 0 | 0 | 39.7 | 138.4 | 142.9 | 4.5 | -0.09 | 4.576 | 2.093 | 2 | 4.69% | 142 | -0.1 | 3.691 | 2.018 | 3.6 | -0.069 | 1.83 | 5.697% | -4.54 | 0.017 | 0.058 | 5.933% | 5.163%
Wind | WND | WIND | -0.071 | 185.2 | 0 | 0 | 14.6 | 170.6 | 173.4 | 2.8 | -0.1 | 2.947 | 2.895 | 1.018 | 7.837% | 173.1 | -0.1 | 2.684 | 2.794 | 2.5 | -0.069 | 0.961 | 8.531% | -8.06 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | GT | -0.071 | 235 | 150 | 28 | 40 | 167 | 171 | 4 | -0.06 | 4.075 | 2.324 | 1.753 | 6.959% | 171.5 | -0.1 | 4.59 | 2.243 | 4.5 | -0.069 | 2 | 6.012% | -4.39 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.071 | 234 | 150 | 29 | 39 | 166 | 170.2 | 4.2 | -0.12 | 4.325 | 2.293 | 1.886 | 6.6% | 170.7 | -0.2 | 4.902 | 2.213 | 4.7 | -0.069 | 2 | 5.732% | -4.17 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.071 | 227 | 150 | 23 | 38.7 | 165.3 | 169.2 | 3.9 | 0.14 | 3.825 | 2.292 | 1.669 | 6.895% | 169.4 | 0.2 | 3.977 | 2.212 | 4.1 | -0.069 | 1.798 | 6.374% | -4.76 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.071 | 115 | 38 | 0 | 43.6 | 71.4 | 71.8 | 0.4 | 0.03 | 0.373 | 1.749 | 0.213 | 34.09% | 72.7 | 0 | 1.293 | 1.688 | 1.3 | -0.069 | 0.766 | 10.19% | -6.48 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.071 | 200 | 40 | 0 | 57.3 | 142.7 | 144 | 1.3 | -0.8 | 2.101 | 2.826 | 0.744 | 18.23% | 143.7 | -1.1 | 2.136 | 2.728 | 1 | -0.069 | 0.783 | 23.03% | -16.86 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | GT | -0.071 | 102 | 35 | 0 | 51.6 | 50.4 | 50.2 | -0.2 | -0.44 | 0.286 | 1.415 | 0.202 | -60.49% | 53.6 | -0.6 | 3.869 | 1.36 | 3.2 | -0.069 | 2 | 3.674% | -1.85 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.071 | 102 | 35 | 0 | 50.8 | 51.2 | 51.7 | 0.5 | -0.36 | 0.879 | 1.415 | 0.621 | 24.2% | 55.6 | -0.5 | 4.876 | 1.36 | 4.4 | -0.069 | 2 | 2.672% | -1.37 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.071 | 316 | 196 | 49.1 | 30.7 | 236.2 | 237.6 | 1.4 | 0.24 | 1.085 | 3.137 | 0.346 | 26.73% | 241.5 | 0.3 | 4.943 | 3.024 | 5.3 | -0.069 | 1.635 | 6.862% | -5.27 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.071 | 134 | 25 | 0 | 104.3 | 29.7 | 35 | 5.3 | -1.06 | 6.373 | 1.08 | 2 | 2.997% | 35 | -1.5 | 6.764 | 1.042 | 5.3 | -0.069 | 2 | 2.913% | -0.66 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.071 | 695.4 | 455 | 25.8 | 72.5 | 597.1 | 608.9 | 11.8 | 0.53 | 11.324 | 7.871 | 1.439 | 6.976% | 617.6 | 0.7 | 19.804 | 7.586 | 20.5 | -0.069 | 2 | 3.902% | -3.45 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.071 | 49.6 | 24 | 0 | 15.1 | 34.5 | 36.3 | 1.8 | 0 | 1.769 | 0.688 | 2 | 3.276% | 38.2 | 0 | 3.71 | 0.661 | 3.7 | -0.069 | 2 | 1.549% | -1.1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.071 | 49.8 | 24 | 0 | 15 | 34.8 | 36.5 | 1.7 | 0.05 | 1.648 | 0.692 | 2 | 3.483% | 38.4 | 0.1 | 3.495 | 0.664 | 3.6 | -0.069 | 2 | 1.599% | -1.14 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.071 | 460.9 | 232 | 0 | 74 | 386.9 | 395.4 | 8.5 | -0.06 | 8.472 | 5.418 | 1.564 | 6.42% | 397.8 | -0.1 | 10.939 | 5.221 | 10.9 | -0.069 | 2 | 4.865% | -4.2 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.071 | 112 | 36 | 0 | 23.6 | 88.4 | 93.5 | 5.1 | -0.12 | 5.208 | 1.317 | 2 | 2.604% | 95 | -0.2 | 6.818 | 1.269 | 6.6 | -0.069 | 2 | 1.956% | -1.58 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.071 | 150 | 55 | 0 | 86.4 | 63.6 | 64.2 | 0.6 | -1.41 | 1.976 | 1.417 | 1.394 | 29.68% | 63.7 | -2 | 1.972 | 1.34 | 0.1 | -0.069 | 1.472 | 173.1% | -74.69 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.071 | 265 | 100 | 20 | 14.9 | 230.1 | 231.7 | 1.6 | 1.09 | 0.562 | 2.88 | 0.195 | 19.62% | 232.7 | 1.5 | 1.078 | 2.775 | 2.6 | -0.069 | 0.388 | 11.73% | -10.46 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.071 | 56 | 48 | 0 | 7.8 | 48.2 | 50 | 1.8 | 0.17 | 1.641 | 0.777 | 2 | 3.697% | 49.9 | 0.2 | 1.515 | 0.746 | 1.7 | -0.069 | 2 | 3.805% | -3.34 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.071 | 56 | 48 | 0 | 7.4 | 48.6 | 50.5 | 1.9 | 0.16 | 1.747 | 0.777 | 2 | 3.503% | 50.5 | 0.2 | 1.635 | 0.746 | 1.9 | -0.069 | 2 | 3.404% | -3.01 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.071 | 56 | 48 | 0 | 7.9 | 48.1 | 50.3 | 2.2 | 0.18 | 2.027 | 0.777 | 2 | 3.025% | 50.2 | 0.3 | 1.866 | 0.746 | 2.1 | -0.069 | 2 | 3.08% | -2.7 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.071 | 56 | 48 | 0 | 7.1 | 48.9 | 51.1 | 2.2 | 0.14 | 2.013 | 0.777 | 2 | 3.025% | 51 | 0.2 | 1.871 | 0.746 | 2.1 | -0.069 | 2 | 3.08% | -2.74 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.071 | 56 | 48 | 0 | 7.2 | 48.8 | 50.5 | 1.7 | 0.11 | 1.588 | 0.777 | 2 | 3.915% | 50.4 | 0.2 | 1.464 | 0.746 | 1.6 | -0.069 | 1.961 | 4.043% | -3.59 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.071 | 56 | 48 | 0 | 7.5 | 48.5 | 50.8 | 2.3 | 0.28 | 2.007 | 0.777 | 2 | 2.893% | 50.7 | 0.4 | 1.834 | 0.746 | 2.2 | -0.069 | 2 | 2.94% | -2.6 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.071 | 112 | 65 | 0 | 21.1 | 90.9 | 91.8 | 0.9 | 0.15 | 0.748 | 1.317 | 0.568 | 14.76% | 92.9 | 0.2 | 1.812 | 1.269 | 2 | -0.069 | 1.428 | 6.454% | -5.36 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.071 | 162 | 74 | 0 | 58 | 104 | 112.1 | 8.1 | -0.01 | 8.08 | 1.422 | 2 | 2.374% | 110.5 | 0 | 6.51 | 1.344 | 6.5 | -0.069 | 2 | 2.875% | -1.88 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.071 | 162 | 74 | 0 | 51.2 | 110.8 | 113.5 | 2.7 | -0.63 | 3.397 | 1.444 | 2 | 7.121% | 112.2 | -0.9 | 2.261 | 1.365 | 1.4 | -0.069 | 1.656 | 13.35% | -9.32 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.071 | 709 | 288 | 70 | 41 | 598 | 608.8 | 10.8 | -0.75 | 11.574 | 7.511 | 1.541 | 7.771% | 610.8 | -1 | 13.846 | 7.239 | 12.8 | -0.069 | 1.913 | 6.372% | -5.53 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.071 | 679 | 300 | 0 | 14.7 | 664.3 | 667.3 | 3 | -5.19 | 8.235 | 7.981 | 1.032 | 26.79% | 670.3 | -7.2 | 13.288 | 7.692 | 6 | -0.069 | 1.727 | 13.02% | -13.1 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.091 | 591 | 220 | 0 | 120.6 | 470.4 | 489 | 18.6 | 8.26 | 10.412 | 15.163 | 0.687 | 4.821% | 483 | 11.5 | 1.116 | 13.67 | 12.6 | -0.083 | 0.082 | 6.491% | -5.66 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.091 | 582 | 220 | 0 | 331.1 | 250.9 | 268.5 | 17.6 | 2.05 | 15.569 | 14.932 | 1.043 | 5.017% | 264 | 2.9 | 10.274 | 13.462 | 13.1 | -0.083 | 0.763 | 6.148% | -2.9 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.091 | 445 | 300 | 0 | 44.7 | 400.3 | 412.2 | 11.9 | -0.32 | 12.252 | 8.72 | 1.405 | 5.674% | 411.2 | -0.4 | 11.386 | 7.841 | 10.9 | -0.083 | 1.452 | 5.65% | -5.57 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.091 | 524 | 305 | 0 | 62.9 | 461.1 | 469.6 | 8.5 | -0.77 | 9.284 | 10.268 | 0.904 | 9.353% | 468.8 | -1.1 | 8.753 | 9.233 | 7.7 | -0.083 | 0.948 | 9.418% | -9.08 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.091 | 785 | 605 | 0 | 179.9 | 605.1 | 626.4 | 21.3 | 0.19 | 21.128 | 16.918 | 1.249 | 5.591% | 628.9 | 0.3 | 23.614 | 15.253 | 23.8 | -0.083 | 1.548 | 4.564% | -3.85 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.091 | 420 | 270 | 0 | 126.3 | 293.7 | 303.2 | 9.5 | 0.52 | 8.918 | 8.063 | 1.106 | 6.708% | 303.6 | 0.7 | 9.169 | 7.269 | 9.9 | -0.083 | 1.261 | 5.872% | -4.5 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.091 | 405 | 270 | 0 | 111.3 | 293.7 | 305.5 | 11.8 | -0.28 | 12.07 | 7.764 | 1.555 | 5.208% | 304.4 | -0.4 | 11.07 | 7 | 10.7 | -0.083 | 1.581 | 5.239% | -4.16 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.091 | 420 | 70 | 0 | 321.4 | 98.6 | 110.7 | 12.1 | -0.38 | 12.48 | 7.769 | 1.606 | 5.267% | 110.2 | -0.5 | 12.152 | 7.004 | 11.6 | -0.083 | 1.735 | 5.011% | -1.29 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.091 | 749 | 360 | 0 | 389 | 360 | 363.4 | 3.4 | -1.7 | 5.073 | 13.629 | 0.372 | 33.43% | 370.5 | -2.4 | 12.869 | 11.904 | 10.5 | -0.083 | 1.081 | 9.873% | -5.19 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.091 | 360 | 154 | 64 | 10 | 286 | 288 | 2 | 0.41 | 1.601 | 5.8 | 0.276 | 27.31% | 287.1 | 0.6 | 0.54 | 5.216 | 1.1 | -0.083 | 0.103 | 45.3% | -39.41 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.091 | 640 | 300 | 0 | 29 | 611 | 624.3 | 13.3 | 1.12 | 12.129 | 13.92 | 0.871 | 7.3% | 627.6 | 1.6 | 15.04 | 12.55 | 16.6 | -0.083 | 1.198 | 5.335% | -5.58 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.091 | 627 | 475 | 0 | 13.2 | 613.8 | 622.8 | 9 | -1.01 | 9.968 | 12.286 | 0.811 | 10.57% | 626.7 | -1.4 | 14.292 | 11.048 | 12.9 | -0.083 | 1.294 | 6.726% | -7.21 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.091 | 105 | 12 | 0 | 92.7 | 12.3 | 16.3 | 4 | 0.08 | 3.931 | 2.665 | 1.475 | 3.988% | 15.7 | 0.1 | 3.228 | 2.402 | 3.4 | -0.083 | 1.344 | 4.28% | -0.54 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.091 | 420 | 50 | 0 | 369 | 51 | 70.7 | 19.7 | -1.13 | 20.761 | 6.993 | 2 | 3.235% | 71.9 | -1.6 | 22.45 | 6.305 | 20.9 | -0.083 | 2 | 2.781% | -0.37 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.091 | 28 | 8 | 0 | 17.9 | 10.1 | 19.7 | 9.6 | 0 | 9.607 | 0.549 | 2 | 0.4453% | 21 | 0 | 10.92 | 0.493 | 10.9 | -0.083 | 2 | 0.358% | -0.14 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.091 | 324 | 142 | 11 | 62 | 251 | 262.3 | 11.3 | -0.01 | 11.326 | 6.133 | 1.847 | 4.351% | 263.4 | 0 | 12.425 | 5.515 | 12.4 | -0.083 | 2 | 3.617% | -3.07 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.091 | 232 | 150 | 22 | 38.2 | 171.8 | 177.8 | 6 | 0.5 | 5.519 | 4.505 | 1.225 | 5.869% | 177.5 | 0.7 | 5.015 | 4.062 | 5.7 | -0.083 | 1.235 | 5.635% | -4.57 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.091 | 238 | 155 | 29 | 38.2 | 170.8 | 176.5 | 5.7 | 0.25 | 5.4 | 4.47 | 1.208 | 6.338% | 176.2 | 0.3 | 5.088 | 4.03 | 5.4 | -0.083 | 1.263 | 6.102% | -4.79 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.091 | 240 | 150 | 29 | 43 | 168 | 174.8 | 6.8 | 0.09 | 6.695 | 4.474 | 1.497 | 5.357% | 175.7 | 0.1 | 7.578 | 4.033 | 7.7 | -0.083 | 1.879 | 4.315% | -3.31 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.091 | 235 | 150 | 21 | 40.8 | 173.2 | 179.9 | 6.7 | -0.13 | 6.851 | 4.612 | 1.485 | 5.324% | 180 | -0.2 | 6.965 | 4.158 | 6.8 | -0.083 | 1.675 | 4.785% | -3.86 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.091 | 183.5 | 0 | 40 | 31.2 | 112.3 | 121.8 | 9.5 | -0.06 | 9.581 | 2.812 | 2 | 2.933% | 122.6 | -0.1 | 10.393 | 2.529 | 10.3 | -0.083 | 2 | 2.467% | -1.65 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.091 | 610 | 304 | 120 | 61.3 | 428.7 | 440 | 11.3 | -1.89 | 13.212 | 9.602 | 1.376 | 8.19% | 443.9 | -2.6 | 17.851 | 8.634 | 15.2 | -0.083 | 2 | 5.553% | -4.28 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.091 | 615 | 305 | 120 | 46.2 | 448.8 | 454.8 | 6 | -0.17 | 6.112 | 9.7 | 0.63 | 15.55% | 456.4 | -0.2 | 7.849 | 8.722 | 7.6 | -0.083 | 0.9 | 11.2% | -8.95 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.091 | 515 | 307.2 | 25 | 13.5 | 476.5 | 488 | 11.5 | 0.42 | 11.166 | 9.601 | 1.163 | 6.794% | 486.1 | 0.6 | 9.037 | 8.633 | 9.6 | -0.083 | 1.047 | 7.424% | -7.53 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.091 | 238 | 150 | 22 | 48.6 | 167.4 | 173.1 | 5.7 | 0.54 | 5.164 | 3.997 | 1.292 | 6.338% | 175.7 | 0.8 | 7.558 | 3.604 | 8.3 | -0.083 | 2 | 3.97% | -3.06 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.091 | 238 | 150 | 23 | 46.9 | 168.1 | 174.4 | 6.3 | 0.45 | 5.845 | 3.982 | 1.468 | 5.734% | 176.5 | 0.6 | 7.756 | 3.59 | 8.4 | -0.083 | 2 | 3.923% | -3.03 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.091 | 228 | 150 | 17 | 43.4 | 167.6 | 173.6 | 6 | 0.44 | 5.579 | 3.916 | 1.425 | 5.768% | 174.9 | 0.6 | 6.721 | 3.53 | 7.3 | -0.083 | 1.904 | 4.324% | -3.48 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.091 | 238 | 150 | 21 | 48.6 | 168.4 | 174.4 | 6 | 0.62 | 5.465 | 4.028 | 1.357 | 6.021% | 176.2 | 0.9 | 6.975 | 3.632 | 7.8 | -0.083 | 1.921 | 4.225% | -3.27 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.091 | 245 | 150 | 16 | 57.1 | 171.9 | 178.7 | 6.8 | 0.42 | 6.418 | 4.117 | 1.559 | 5.469% | 180.4 | 0.6 | 7.963 | 3.711 | 8.5 | -0.083 | 2 | 3.991% | -3.06 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.091 | 535 | 262 | 0 | 237.3 | 297.7 | 310.3 | 12.6 | 1.68 | 10.972 | 13.726 | 0.799 | 6.442% | 310.5 | 2.3 | 10.522 | 12.375 | 12.8 | -0.083 | 0.85 | 5.784% | -3.53 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.091 | 735 | 320 | 0 | 107.4 | 627.6 | 638.1 | 10.5 | -4.74 | 15.249 | 18.857 | 0.809 | 10.62% | 643.3 | -6.6 | 22.26 | 17.001 | 15.7 | -0.083 | 1.309 | 6.478% | -6.06 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | WDS | STM | -0.091 | 105 | 70 | 0 | 34.4 | 70.6 | 72.9 | 2.3 | 0.12 | 2.231 | 2.423 | 0.921 | 6.936% | 72.9 | 0.2 | 2.179 | 2.158 | 2.3 | -0.083 | 1.01 | 6.328% | -4.64 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.091 | 673 | 426 | 30 | 83.3 | 559.7 | 567.6 | 7.9 | -0.77 | 8.66 | 12.6 | 0.687 | 12.92% | 576.3 | -1.1 | 17.71 | 11.33 | 16.6 | -0.083 | 1.563 | 5.61% | -5.11 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.091 | 664.2 | 189.6 | 0 | 19 | 645.2 | 659 | 13.8 | 1.55 | 12.189 | 11.331 | 1.076 | 7.302% | 661.7 | 2.2 | 14.312 | 10.216 | 16.5 | -0.083 | 1.401 | 5.57% | -5.93 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.091 | 664.2 | 189.6 | 0 | 19 | 645.2 | 659 | 13.8 | 1.55 | 12.189 | 11.331 | 1.076 | 7.302% | 661.7 | 2.2 | 14.312 | 10.216 | 16.5 | -0.083 | 1.401 | 5.57% | -5.93 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.091 | 664.2 | 189.6 | 0 | 19 | 645.2 | 659 | 13.8 | 1.55 | 12.189 | 11.331 | 1.076 | 7.302% | 661.7 | 2.2 | 14.312 | 10.216 | 16.5 | -0.083 | 1.401 | 5.57% | -5.93 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.091 | 664.2 | 189.6 | 0 | 19 | 645.2 | 659 | 13.8 | 1.55 | 12.189 | 11.331 | 1.076 | 7.302% | 661.7 | 2.2 | 14.312 | 10.216 | 16.5 | -0.083 | 1.401 | 5.57% | -5.93 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.091 | 664.2 | 189.6 | 0 | 19 | 645.2 | 659 | 13.8 | 1.55 | 12.189 | 11.331 | 1.076 | 7.302% | 661.7 | 2.2 | 14.312 | 10.216 | 16.5 | -0.083 | 1.401 | 5.57% | -5.93 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.091 | 720.4 | 407.2 | 26.3 | 93.7 | 600.4 | 625.7 | 25.3 | -0.47 | 25.71 | 13.601 | 1.89 | 4.32% | 624 | -0.7 | 24.214 | 12.23 | 23.6 | -0.083 | 1.98 | 4.224% | -3.86 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.091 | 711.5 | 455 | 32 | 110.7 | 568.8 | 589.6 | 20.8 | -0.12 | 20.882 | 13.315 | 1.568 | 5.189% | 596.9 | -0.2 | 28.279 | 11.973 | 28.1 | -0.083 | 2 | 3.504% | -3.07 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.091 | 712.9 | 455 | 18.9 | 60.6 | 633.4 | 653.3 | 19.9 | 0.24 | 19.707 | 13.599 | 1.449 | 5.435% | 661.5 | 0.3 | 27.814 | 12.228 | 28.1 | -0.083 | 2 | 3.511% | -3.42 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.091 | 480 | 232 | 3.8 | 182.5 | 293.7 | 320.3 | 26.6 | -1.06 | 27.643 | 9.331 | 2 | 2.738% | 332.8 | -1.5 | 40.578 | 8.391 | 39.1 | -0.083 | 2 | 1.699% | -1.14 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.091 | 690 | 420 | 0 | 26.6 | 663.4 | 687.2 | 23.8 | 0.19 | 23.629 | 13.521 | 1.748 | 4.398% | 687.6 | 0.3 | 23.94 | 12.158 | 24.2 | -0.083 | 1.969 | 3.945% | -4.16 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.091 | 610 | 310 | 0 | 20.7 | 589.3 | 587.8 | -1.5 | -2.97 | 1.409 | 15.65 | 0.09 | -61.7% | 589.2 | -4.1 | 3.962 | 14.11 | -0.1 | -0.083 | 0.281 | -844.1% | 893.49 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.091 | 78 | 55 | 0 | 20.9 | 57.1 | 59.2 | 2.1 | 0.1 | 1.966 | 1.8 | 1.092 | 5.647% | 58.8 | 0.1 | 1.558 | 1.603 | 1.7 | -0.083 | 0.972 | 6.364% | -5.08 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.091 | 79 | 55 | 0 | 20.4 | 58.6 | 61 | 2.4 | -0.02 | 2.395 | 1.823 | 1.314 | 5.004% | 60.4 | 0 | 1.831 | 1.623 | 1.8 | -0.083 | 1.128 | 6.087% | -4.92 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.091 | 265 | 100 | 20 | 54.6 | 190.4 | 197.7 | 7.3 | -0.54 | 7.909 | 4.801 | 1.647 | 5.51% | 202.2 | -0.8 | 12.585 | 4.317 | 11.8 | -0.083 | 2 | 3.109% | -2.44 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.091 | 258 | 165 | 0 | 35.9 | 222.1 | 230.2 | 8.1 | -0.56 | 8.701 | 5.056 | 1.721 | 4.834% | 231.9 | -0.8 | 10.58 | 4.546 | 9.8 | -0.083 | 2 | 3.645% | -3.43 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.098 | 190 | 85 | 0 | 37.3 | 152.7 | 158.9 | 6.2 | 0.58 | 5.584 | 3.911 | 1.428 | 5.01% | 163.6 | 0.8 | 10.094 | 4.011 | 10.9 | -0.1 | 2 | 2.908% | -2.29 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.098 | 511.8 | 275 | 12 | 43.9 | 455.9 | 453.6 | -2.3 | -11.92 | 9.64 | 8.733 | 1.104 | -36.36% | 457.9 | -16.6 | 18.574 | 8.938 | 2 | -0.1 | 2 | 42.66% | -37.22 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 459 | 300 | 0 | 46.7 | 412.3 | 425 | 12.7 | 1.21 | 11.41 | 8.02 | 1.423 | 5.905% | 425.2 | 1.7 | 11.153 | 8.208 | 12.9 | -0.1 | 1.359 | 5.932% | -5.22 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.098 | 220 | 62 | 0 | 61.1 | 158.9 | 165.3 | 6.4 | 0.25 | 6.148 | 3.815 | 1.612 | 5.623% | 166.6 | 0.3 | 7.276 | 3.931 | 7.7 | -0.1 | 1.851 | 4.769% | -3.36 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.098 | 508 | 330 | 0 | 31.8 | 476.2 | 476.5 | 0.3 | -0.41 | 0.681 | 8.876 | 0.077 | 276.7% | 476.9 | -0.6 | 1.268 | 9.085 | 0.7 | -0.1 | 0.14 | 121% | -111.07 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.098 | 420 | 260 | 0 | 44.1 | 375.9 | 383.5 | 7.6 | 0.07 | 7.538 | 7.579 | 0.994 | 9.03% | 380.1 | 0.1 | 4.127 | 7.753 | 4.2 | -0.1 | 0.532 | 16.67% | -14.61 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.098 | 420 | 260 | 0 | 49.9 | 370.1 | 376.8 | 6.7 | 0.18 | 6.521 | 7.561 | 0.862 | 10.24% | 376.6 | 0.3 | 6.241 | 7.733 | 6.5 | -0.1 | 0.807 | 10.77% | -9.3 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.098 | 746 | 309 | 0 | 290.3 | 455.7 | 478.4 | 22.7 | 5.68 | 17.108 | 11.346 | 1.508 | 5.37% | 485 | 7.9 | 21.486 | 11.691 | 29.3 | -0.1 | 1.838 | 4.245% | -2.54 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.098 | 175 | 146 | 0 | 6.3 | 168.7 | 168.8 | 0.1 | -0.35 | 0.425 | 3.058 | 0.139 | 286.1% | 169.3 | -0.5 | 1.114 | 3.13 | 0.6 | -0.1 | 0.356 | 48.66% | -45.88 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.098 | 105 | 12 | 0 | 92.8 | 12.2 | 14.9 | 2.7 | 0.29 | 2.365 | 2.385 | 0.992 | 6.362% | 14.8 | 0.4 | 2.131 | 2.44 | 2.6 | -0.1 | 0.874 | 6.742% | -0.76 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | STM | -0.098 | 308 | 55 | 0 | 61 | 247 | 254.8 | 7.8 | 0.02 | 7.77 | 6.777 | 1.146 | 6.453% | 254.3 | 0 | 7.255 | 6.932 | 7.3 | -0.1 | 1.046 | 7.036% | -5.52 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | FOSS | -0.098 | 377 | 40 | 0 | 323 | 54 | 82.8 | 28.8 | 4.83 | 23.97 | 5.828 | 2 | 2.14% | 84.5 | 6.7 | 23.775 | 6.005 | 30.5 | -0.1 | 2 | 2.062% | -0.29 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.098 | 228 | 150 | 22 | 39.5 | 166.5 | 171.9 | 5.4 | 0.26 | 5.231 | 3.886 | 1.346 | 6.902% | 172.4 | 0.4 | 5.599 | 3.975 | 5.9 | -0.1 | 1.409 | 6.445% | -4.6 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.098 | 234 | 155 | 29 | 39.6 | 165.4 | 170.9 | 5.5 | 0 | 5.556 | 3.854 | 1.442 | 6.954% | 171.3 | 0 | 5.896 | 3.942 | 5.9 | -0.1 | 1.496 | 6.615% | -4.57 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.098 | 236 | 150 | 29 | 38.7 | 168.3 | 173.2 | 4.9 | 0.22 | 4.641 | 3.928 | 1.181 | 7.872% | 173.3 | 0.3 | 4.637 | 4.018 | 5 | -0.1 | 1.154 | 7.872% | -5.49 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.098 | 231 | 150 | 21 | 40.6 | 169.4 | 174.9 | 5.5 | 0.12 | 5.36 | 3.998 | 1.341 | 6.865% | 175.3 | 0.2 | 5.775 | 4.09 | 5.9 | -0.1 | 1.412 | 6.53% | -4.68 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.098 | 435 | 120 | 0 | 236 | 199 | 210.3 | 11.3 | 1.16 | 10.121 | 8.581 | 1.179 | 6.29% | 213.8 | 1.6 | 13.135 | 8.777 | 14.8 | -0.1 | 1.497 | 4.901% | -2.19 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.098 | 173.1 | 0 | 40 | 29.5 | 103.6 | 114.4 | 10.8 | 0.06 | 10.693 | 2.326 | 2 | 2.62% | 114 | 0.1 | 10.302 | 2.38 | 10.4 | -0.1 | 2 | 2.777% | -1.62 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.098 | 530 | 320 | 0 | 157.7 | 372.3 | 381.5 | 9.2 | 0.22 | 8.901 | 8.352 | 1.066 | 9.412% | 381.2 | 0.3 | 8.585 | 8.543 | 8.9 | -0.1 | 1.005 | 9.928% | -6.83 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.098 | 229 | 150 | 23 | 39 | 167 | 172.5 | 5.5 | 0.04 | 5.395 | 3.402 | 1.586 | 6.806% | 173 | 0 | 5.886 | 3.48 | 6 | -0.1 | 1.691 | 6.366% | -4.54 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.098 | 219 | 150 | 17 | 14.6 | 187.4 | 192.3 | 4.9 | 0.15 | 4.683 | 3.531 | 1.326 | 7.306% | 192.9 | 0.2 | 5.292 | 3.612 | 5.5 | -0.1 | 1.465 | 6.642% | -5.56 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.098 | 229 | 150 | 21 | 39.9 | 168.1 | 173.5 | 5.4 | 0.12 | 5.301 | 3.45 | 1.537 | 6.932% | 173.9 | 0.2 | 5.705 | 3.529 | 5.8 | -0.1 | 1.617 | 6.585% | -4.73 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.098 | 234 | 150 | 16 | 41.2 | 176.8 | 182.5 | 5.7 | 0.18 | 5.573 | 3.554 | 1.568 | 6.71% | 182.6 | 0.2 | 5.627 | 3.635 | 5.8 | -0.1 | 1.548 | 6.729% | -4.97 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.098 | 200 | 40 | 0 | 63 | 137 | 139 | 2 | -2.08 | 4.058 | 4.163 | 0.975 | 16.35% | 137.6 | -2.9 | 3.448 | 4.258 | 0.6 | -0.1 | 0.81 | 55.6% | -37.25 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | LIG | FOSS | -0.098 | 805 | 350 | 0 | 18.7 | 786.3 | 783.8 | -2.5 | -6.94 | 4.413 | 18.469 | 0.239 | -52.6% | 782.8 | -9.7 | 6.122 | 18.891 | -3.5 | -0.1 | 0.324 | -38.34% | 36.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | WDS | STM | -0.098 | 105 | 70 | 0 | 34.7 | 70.3 | 72.2 | 1.9 | -0.12 | 2.009 | 2.161 | 0.93 | 9.041% | 72.3 | -0.2 | 2.143 | 2.216 | 2 | -0.1 | 0.967 | 8.764% | -5.73 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | FOSS | -0.098 | 49.8 | 24 | 0 | 18 | 31.8 | 35.2 | 3.4 | 0.14 | 3.262 | 1.025 | 2 | 2.401% | 40.1 | 0.2 | 8.117 | 1.051 | 8.3 | -0.1 | 2 | 1.003% | -0.62 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.098 | 49.8 | 24 | 0 | 12.3 | 37.5 | 39.7 | 2.2 | 0.05 | 2.225 | 1.026 | 2 | 3.71% | 42.7 | 0.1 | 5.207 | 1.052 | 5.2 | -0.1 | 2 | 1.602% | -1.17 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.098 | 480.2 | 232 | 6.8 | 133.3 | 340.1 | 356.6 | 16.5 | 0.41 | 16.037 | 8.272 | 1.939 | 4.755% | 373.5 | 0.6 | 32.797 | 8.466 | 33.4 | -0.1 | 2 | 2.397% | -1.66 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 112 | 36 | 0 | 20.3 | 91.7 | 98.4 | 6.7 | 0.15 | 6.487 | 1.957 | 2 | 2.735% | 100.1 | 0.2 | 8.168 | 2.003 | 8.4 | -0.1 | 2 | 2.226% | -1.78 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.098 | 41 | 13 | 0 | 27.1 | 13.9 | 14.4 | 0.5 | -0.24 | 0.78 | 0.711 | 1.097 | 13.51% | 13.9 | -0.3 | 0.328 | 0.733 | 0 | -0.1 | 0.448 | 0% |  | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.098 | 266 | 100 | 20 | 9.2 | 236.8 | 234.6 | -2.2 | -3.54 | 1.381 | 4.298 | 0.321 | -19.76% | 235.9 | -4.9 | 4.037 | 4.399 | -0.9 | -0.1 | 0.918 | -49.29% | 42.94 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 244 | 165 | 0 | 4.8 | 239.2 | 242.5 | 3.3 | -0.04 | 3.395 | 4.263 | 0.796 | 12.09% | 246.4 | -0.1 | 7.322 | 4.364 | 7.2 | -0.1 | 1.678 | 5.652% | -5.42 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 703 | 314 | 70 | 42 | 591 | 604.8 | 13.8 | -0.28 | 14.14 | 11.06 | 1.278 | 8.323% | 610 | -0.4 | 19.353 | 11.32 | 19 | -0.1 | 1.71 | 6.168% | -5.08 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 676 | 300 | 40 | 165.4 | 470.6 | 495.1 | 24.5 | 0 | 24.457 | 11.114 | 2 | 4.508% | 493 | 0 | 22.397 | 11.375 | 22.4 | -0.1 | 1.969 | 5.031% | -3.43 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 522 | 275 | 12 | 154.6 | 355.4 | 367.6 | 12.2 | -1.41 | 13.584 | 6.772 | 2 | 5.279% | 371.2 | -2 | 17.763 | 6.847 | 15.8 | -0.074 | 2 | 4.076% | -2.77 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.074 | 582 | 220 | 0 | 89.8 | 492.2 | 496.4 | 4.2 | -2.5 | 6.651 | 10.231 | 0.65 | 17.1% | 496.5 | -3.5 | 7.774 | 10.341 | 4.3 | -0.074 | 0.752 | 16.7% | -14.11 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 231 | 170 | 0 | 38.1 | 192.9 | 196.5 | 3.6 | -0.24 | 3.832 | 3.067 | 1.249 | 7.922% | 197 | -0.3 | 4.4 | 3.101 | 4.1 | -0.074 | 1.419 | 6.956% | -5.8 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 459 | 300 | 0 | 117.4 | 341.6 | 351.1 | 9.5 | 0.07 | 9.418 | 6.095 | 1.545 | 5.962% | 351 | 0.1 | 9.318 | 6.162 | 9.4 | -0.074 | 1.512 | 6.025% | -4.48 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 202.5 | 144.5 | 0 | 38.6 | 163.9 | 168.5 | 4.6 | -0.64 | 5.216 | 2.689 | 1.94 | 5.436% | 170.3 | -0.9 | 7.264 | 2.719 | 6.4 | -0.074 | 2 | 3.907% | -3.15 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 174 | 120 | 4 | 46 | 124 | 126.3 | 2.3 | 0 | 2.259 | 2.257 | 1.001 | 9.343% | 127 | 0 | 2.971 | 2.282 | 3 | -0.074 | 1.302 | 7.163% | -5.09 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.074 | 420 | 125 | 0 | 276.9 | 143.1 | 145.8 | 2.7 | 0.73 | 1.962 | 5.134 | 0.382 | 19.2% | 151 | 1 | 6.901 | 5.189 | 7.9 | -0.074 | 1.33 | 6.561% | -2.23 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 407 | 125 | 0 | 265.9 | 141.1 | 149 | 7.9 | 0.18 | 7.769 | 4.966 | 1.564 | 6.358% | 146.3 | 0.3 | 4.997 | 5.019 | 5.2 | -0.074 | 0.996 | 9.659% | -3.34 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 113.4 | 80 | 9 | 22.9 | 81.5 | 85 | 3.5 | -0.06 | 3.565 | 1.386 | 2 | 4.004% | 86.7 | -0.1 | 5.282 | 1.402 | 5.2 | -0.074 | 2 | 2.695% | -1.93 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.074 | 746 | 93 | 0 | 651.5 | 94.5 | 104.6 | 10.1 | -0.66 | 10.686 | 6.501 | 1.644 | 9.115% | 107.2 | -0.9 | 13.539 | 6.604 | 12.7 | -0.074 | 2 | 7.249% | -0.91 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 749 | 195 | 0 | 553.2 | 195.8 | 211.4 | 15.6 | -0.14 | 15.716 | 8.463 | 1.857 | 5.925% | 210.3 | -0.2 | 14.66 | 8.597 | 14.5 | -0.074 | 1.705 | 6.375% | -1.66 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 275 | 160 | 0 | 113.8 | 161.2 | 164.9 | 3.7 | -0.06 | 3.778 | 3.652 | 1.034 | 9.174% | 165.8 | -0.1 | 4.678 | 3.692 | 4.6 | -0.074 | 1.267 | 7.379% | -4.32 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 390 | 211 | 118.9 | 9.1 | 262 | 262.1 | 0.1 | -0.24 | 0.306 | 3.6 | 0.085 | 481.3% | 262.4 | -0.3 | 0.728 | 3.64 | 0.4 | -0.074 | 0.2 | 120.3% | -80.71 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.074 | 625 | 300 | 0 | 17.2 | 607.8 | 620.8 | 13 | -1.06 | 14.041 | 9.313 | 1.508 | 5.932% | 624.8 | -1.5 | 18.464 | 9.413 | 17 | -0.074 | 1.961 | 4.536% | -4.41 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 631 | 478 | 26 | 114.4 | 490.6 | 505 | 14.4 | 1 | 13.425 | 8.033 | 1.671 | 5.406% | 504.4 | 1.4 | 12.434 | 8.123 | 13.8 | -0.074 | 1.531 | 5.641% | -4.38 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.074 | 105 | 12 | 0 | 92.8 | 12.2 | 13.8 | 1.6 | 0.28 | 1.3 | 1.829 | 0.711 | 8.111% | 13.7 | 0.4 | 1.104 | 1.848 | 1.5 | -0.074 | 0.597 | 8.652% | -0.98 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 39 | 18 | 0 | 18.8 | 20.2 | 24.8 | 4.6 | -0.1 | 4.761 | 0.518 | 2 | 1.052% | 27.9 | -0.1 | 7.866 | 0.524 | 7.7 | -0.074 | 2 | 0.6284% | -0.32 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 519.9 | 346.4 | 0 | 30 | 489.9 | 501.4 | 11.5 | -0.05 | 11.627 | 6.903 | 1.684 | 5.578% | 502.1 | -0.1 | 12.296 | 6.98 | 12.2 | -0.074 | 1.762 | 5.258% | -4.95 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 95 | 65 | 14.4 | 15.4 | 65.2 | 67.9 | 2.7 | 0.18 | 2.535 | 1.07 | 2 | 4.35% | 68.6 | 0.2 | 3.155 | 1.082 | 3.4 | -0.074 | 2 | 3.454% | -2.36 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 465 | 272 | 0 | 31.5 | 433.5 | 436.8 | 3.3 | -1.36 | 4.661 | 6.174 | 0.755 | 17.39% | 434.7 | -1.9 | 3.074 | 6.243 | 1.2 | -0.074 | 0.492 | 47.82% | -44.53 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 460 | 264 | 0 | 33.2 | 426.8 | 428.8 | 2 | -0.89 | 2.792 | 6.108 | 0.457 | 28.38% | 426.3 | -1.2 | 0.689 | 6.176 | -0.5 | -0.074 | 0.112 | -113.5% | 105.22 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 596.8 | 311.4 | 104 | 26.4 | 466.4 | 480.6 | 14.2 | -0.4 | 14.6 | 6.543 | 2 | 5.185% | 482.4 | -0.6 | 16.547 | 6.616 | 16 | -0.074 | 2 | 4.602% | -3.59 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 310 | 250 | 0 | 58 | 252 | 258 | 6 | -0.04 | 6.049 | 4.116 | 1.469 | 6.377% | 257.9 | -0.1 | 5.953 | 4.162 | 5.9 | -0.074 | 1.43 | 6.485% | -5.26 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 263.9 | 175 | 62.1 | 26.1 | 175.7 | 180.8 | 5.1 | -0.6 | 5.662 | 2.68 | 2 | 6.387% | 182.8 | -0.8 | 7.922 | 2.709 | 7.1 | -0.074 | 2 | 4.588% | -3.05 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 232 | 171 | 18 | 41.8 | 172.2 | 177.7 | 5.5 | 0.43 | 5.062 | 2.842 | 1.781 | 5.208% | 177.6 | 0.6 | 4.836 | 2.873 | 5.4 | -0.074 | 1.683 | 5.304% | -3.93 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.074 | 233 | 150 | 22 | 60.7 | 150.3 | 154.8 | 4.5 | 0.18 | 4.34 | 3.026 | 1.434 | 6.392% | 154.7 | 0.2 | 4.154 | 3.058 | 4.4 | -0.074 | 1.358 | 6.538% | -4.21 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.074 | 239 | 153.7 | 29 | 55.1 | 154.9 | 159.1 | 4.2 | 0.25 | 3.952 | 3.012 | 1.312 | 7.025% | 159.4 | 0.3 | 4.176 | 3.044 | 4.5 | -0.074 | 1.372 | 6.557% | -4.24 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.074 | 241 | 150 | 29 | 61.7 | 150.3 | 154.5 | 4.2 | -0.04 | 4.238 | 3.04 | 1.394 | 7.084% | 154.6 | -0.1 | 4.304 | 3.073 | 4.3 | -0.074 | 1.401 | 6.919% | -4.3 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.074 | 236 | 150 | 21 | 64.4 | 150.6 | 154.7 | 4.1 | 0.29 | 3.818 | 3.083 | 1.238 | 7.106% | 154.7 | 0.4 | 3.716 | 3.116 | 4.1 | -0.074 | 1.192 | 7.106% | -4.52 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 201.5 | 8.4 | 40 | 57.3 | 104.2 | 107.9 | 3.7 | 0.32 | 3.344 | 2.144 | 1.56 | 6.724% | 103.1 | 0.4 | -1.605 | 2.168 | -1.1 | -0.074 | 0 | -22.62% | 11.66 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 606 | 305 | 120 | 153.7 | 332.3 | 339.2 | 6.9 | 0.68 | 6.158 | 6.453 | 0.954 | 10.84% | 342.7 | 1 | 9.421 | 6.525 | 10.4 | -0.074 | 1.444 | 7.189% | -3.94 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 611 | 305 | 120 | 185.9 | 305.1 | 311.6 | 6.5 | -0.75 | 7.268 | 6.52 | 1.115 | 11.6% | 313.7 | -1 | 9.677 | 6.592 | 8.6 | -0.074 | 1.468 | 8.766% | -4.37 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 250 | 130 | 65 | 30.5 | 154.5 | 157.4 | 2.9 | -0.04 | 2.885 | 2.457 | 1.174 | 10.64% | 159.7 | 0 | 5.262 | 2.484 | 5.2 | -0.074 | 2 | 5.935% | -3.66 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 370 | 235 | 7 | 125.6 | 237.4 | 244.9 | 7.5 | -0.89 | 8.361 | 4.82 | 1.735 | 6.088% | 242.2 | -1.2 | 5.989 | 4.874 | 4.8 | -0.074 | 1.229 | 9.513% | -6.09 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.074 | 98 | 57 | 0 | 20.4 | 77.6 | 82.3 | 4.7 | 0 | 4.702 | 1.535 | 2 | 2.578% | 81.9 | 0 | 4.331 | 1.553 | 4.3 | -0.074 | 2 | 2.817% | -2.22 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 515 | 305 | 55.7 | 56.3 | 403 | 410.7 | 7.7 | 0.02 | 7.682 | 6.099 | 1.26 | 8.253% | 410.2 | 0 | 7.173 | 6.166 | 7.2 | -0.074 | 1.163 | 8.826% | -6.9 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.074 | 237 | 150 | 23 | 62.9 | 151.1 | 155.2 | 4.1 | 0.45 | 3.616 | 2.736 | 1.322 | 7.136% | 155.4 | 0.6 | 3.668 | 2.765 | 4.3 | -0.074 | 1.327 | 6.804% | -4.33 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.074 | 228 | 150 | 17 | 59.8 | 151.2 | 155.2 | 4 | 0.34 | 3.683 | 2.705 | 1.361 | 7.037% | 155.5 | 0.5 | 3.871 | 2.734 | 4.3 | -0.074 | 1.416 | 6.546% | -4.33 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.074 | 237 | 150 | 21 | 65 | 151 | 155.1 | 4.1 | 0.21 | 3.86 | 2.765 | 1.396 | 7.136% | 155.3 | 0.3 | 3.987 | 2.794 | 4.3 | -0.074 | 1.427 | 6.804% | -4.32 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.074 | 245 | 150 | 16 | 77.9 | 151.1 | 155.7 | 4.6 | 0.51 | 4.086 | 2.808 | 1.455 | 6.575% | 155.6 | 0.7 | 3.703 | 2.838 | 4.5 | -0.074 | 1.305 | 6.721% | -4.13 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.074 | 247 | 150 | 16 | 80 | 151 | 155.6 | 4.6 | -0.25 | 4.839 | 2.927 | 1.653 | 6.629% | 155.5 | -0.3 | 4.755 | 2.958 | 4.5 | -0.074 | 1.607 | 6.776% | -4.13 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.074 | 765 | 350 | 0 | 412.6 | 352.4 | 363.7 | 11.3 | 0.14 | 11.171 | 13.448 | 0.831 | 8.352% | 363.1 | 0.2 | 10.516 | 13.592 | 10.7 | -0.074 | 0.774 | 8.82% | -4.06 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.074 | 805 | 350 | 0 | 449.3 | 355.7 | 367.1 | 11.4 | 0.06 | 11.35 | 14.151 | 0.802 | 8.712% | 365.8 | 0.1 | 9.966 | 14.303 | 10.1 | -0.074 | 0.697 | 9.833% | -4.34 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.074 | 805 | 350 | 0 | 453.8 | 351.2 | 361.4 | 10.2 | 1.15 | 9.046 | 14.151 | 0.639 | 9.736% | 362.5 | 1.6 | 9.679 | 14.303 | 11.3 | -0.074 | 0.677 | 8.789% | -3.83 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.074 | 515 | 262 | 0 | 252.3 | 262.7 | 264.4 | 1.7 | 0.4 | 1.22 | 9.053 | 0.135 | 37.38% | 263.1 | 0.6 | -0.219 | 9.15 | 0.4 | -0.074 | 0 | 158.9% | -80.93 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.074 | 525 | 256 | 0 | 265.2 | 259.8 | 262.3 | 2.5 | -0.21 | 2.75 | 9.229 | 0.298 | 25.91% | 261.3 | -0.3 | 1.823 | 9.328 | 1.5 | -0.074 | 0.195 | 43.19% | -21.34 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.074 | 735 | 320 | 0 | 221.6 | 513.4 | 521.6 | 8.2 | -2.87 | 11.099 | 12.92 | 0.859 | 11.06% | 524.1 | -4 | 14.712 | 13.059 | 10.7 | -0.074 | 1.127 | 8.475% | -5.92 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | WDS | STM | -0.074 | 105 | 70 | 0 | 34.7 | 70.3 | 71.6 | 1.3 | 0.12 | 1.189 | 1.645 | 0.723 | 9.983% | 71.6 | 0.2 | 1.093 | 1.664 | 1.3 | -0.074 | 0.657 | 9.983% | -6.65 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.074 | 679 | 440 | 30 | 16.8 | 632.2 | 638.4 | 6.2 | -0.06 | 6.333 | 8.618 | 0.735 | 13.51% | 643.3 | -0.1 | 11.225 | 8.713 | 11.1 | -0.074 | 1.288 | 7.547% | -7.02 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 497 | 344 | 45 | 107.5 | 344.5 | 350.2 | 5.7 | 0.05 | 5.615 | 6.002 | 0.936 | 10.76% | 361.6 | 0.1 | 17.006 | 6.068 | 17.1 | -0.074 | 2 | 3.586% | -2.48 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.074 | 664.2 | 189.8 | 0 | 276 | 388.2 | 394.5 | 6.3 | -1.01 | 7.283 | 7.163 | 1.017 | 13.01% | 394.9 | -1.4 | 8.106 | 7.24 | 6.7 | -0.074 | 1.12 | 12.23% | -7.14 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 664.2 | 189.8 | 0 | 276 | 388.2 | 394.5 | 6.3 | -1.01 | 7.283 | 7.163 | 1.017 | 13.01% | 394.9 | -1.4 | 8.106 | 7.24 | 6.7 | -0.074 | 1.12 | 12.23% | -7.14 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 664.2 | 189.8 | 0 | 276 | 388.2 | 394.5 | 6.3 | -1.01 | 7.283 | 7.163 | 1.017 | 13.01% | 394.9 | -1.4 | 8.106 | 7.24 | 6.7 | -0.074 | 1.12 | 12.23% | -7.14 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 664.2 | 189.8 | 0 | 276 | 388.2 | 394.5 | 6.3 | -1.01 | 7.283 | 7.163 | 1.017 | 13.01% | 394.9 | -1.4 | 8.106 | 7.24 | 6.7 | -0.074 | 1.12 | 12.23% | -7.14 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 664.2 | 189.8 | 0 | 276 | 388.2 | 394.5 | 6.3 | -1.01 | 7.283 | 7.163 | 1.017 | 13.01% | 394.9 | -1.4 | 8.106 | 7.24 | 6.7 | -0.074 | 1.12 | 12.23% | -7.14 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 712.8 | 403.7 | 90 | 203 | 419.8 | 433.7 | 13.9 | -0.24 | 14.076 | 8.27 | 1.702 | 6.327% | 434.7 | -0.3 | 15.2 | 8.362 | 14.9 | -0.074 | 1.818 | 5.902% | -3.47 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 721.1 | 415.9 | 93 | 211.6 | 416.5 | 432.5 | 16 | 0.12 | 15.827 | 8.34 | 1.898 | 5.56% | 438 | 0.2 | 21.293 | 8.433 | 21.5 | -0.074 | 2 | 4.138% | -2.39 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 499 | 361 | 10 | 74.9 | 414.1 | 418.5 | 4.4 | -0.94 | 5.3 | 6.493 | 0.816 | 13.99% | 420.4 | -1.3 | 7.614 | 6.565 | 6.3 | -0.074 | 1.16 | 9.773% | -8.1 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 460 | 275 | 0 | 117.8 | 342.2 | 353.5 | 11.3 | 0.92 | 10.365 | 6.108 | 1.697 | 5.023% | 354.5 | 1.3 | 11.005 | 6.176 | 12.3 | -0.074 | 1.782 | 4.615% | -3.43 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 222.7 | 118 | 0 | 34.3 | 188.4 | 191.1 | 2.7 | 0.64 | 2.067 | 2.958 | 0.699 | 10.18% | 191.3 | 0.9 | 2.012 | 2.99 | 2.9 | -0.074 | 0.673 | 9.481% | -8 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.074 | 940 | 359.1 | 0 | 111.6 | 828.4 | 843.8 | 15.4 | -0.49 | 15.925 | 12.093 | 1.317 | 7.53% | 842.3 | -0.7 | 14.599 | 12.223 | 13.9 | -0.074 | 1.194 | 8.343% | -7.35 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 940 | 359.1 | 0 | 111.6 | 828.4 | 843.8 | 15.4 | -0.49 | 15.925 | 12.093 | 1.317 | 7.53% | 842.3 | -0.7 | 14.599 | 12.223 | 13.9 | -0.074 | 1.194 | 8.343% | -7.35 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 940 | 359.1 | 0 | 111.6 | 828.4 | 843.8 | 15.4 | -0.49 | 15.925 | 12.093 | 1.317 | 7.53% | 842.3 | -0.7 | 14.599 | 12.223 | 13.9 | -0.074 | 1.194 | 8.343% | -7.35 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 940 | 359.1 | 0 | 111.6 | 828.4 | 843.8 | 15.4 | -0.49 | 15.925 | 12.093 | 1.317 | 7.53% | 842.3 | -0.7 | 14.599 | 12.223 | 13.9 | -0.074 | 1.194 | 8.343% | -7.35 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.074 | 76 | 55 | 0 | 19.2 | 56.8 | 58.4 | 1.6 | 0.25 | 1.356 | 1.19 | 1.14 | 5.876% | 58.6 | 0.3 | 1.457 | 1.205 | 1.8 | -0.074 | 1.209 | 5.223% | -3.88 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.074 | 76 | 55 | 0 | 18.7 | 57.3 | 59.2 | 1.9 | -0.01 | 1.911 | 1.19 | 1.605 | 4.948% | 59.2 | 0 | 1.838 | 1.205 | 1.9 | -0.074 | 1.526 | 4.948% | -3.7 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 840 | 460 | 123.2 | 175.2 | 541.6 | 552.1 | 10.5 | -2.29 | 12.842 | 9.518 | 1.349 | 9.869% | 555.9 | -3.2 | 17.498 | 9.624 | 14.3 | -0.074 | 1.818 | 7.247% | -4.67 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 247 | 165 | 0 | 65.8 | 181.2 | 185.9 | 4.7 | -0.04 | 4.694 | 3.28 | 1.431 | 6.488% | 187.7 | -0.1 | 6.53 | 3.316 | 6.5 | -0.074 | 1.969 | 4.691% | -3.43 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 703 | 323 | 70 | 221.1 | 411.9 | 425.3 | 13.4 | 0.12 | 13.242 | 8.405 | 1.575 | 6.473% | 425.2 | 0.2 | 13.106 | 8.499 | 13.3 | -0.074 | 1.542 | 6.521% | -3.82 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 642 | 300 | 40 | 279.8 | 322.2 | 333.3 | 11.1 | -0.86 | 11.958 | 7.995 | 1.496 | 7.136% | 336.3 | -1.2 | 15.227 | 8.084 | 14.1 | -0.074 | 1.884 | 5.618% | -2.82 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.096 | 619.2 | 250.5 | 81 | 39.2 | 499 | 513.7 | 14.7 | 6.02 | 8.675 | 8.439 | 1.028 | 6.742% | 521.1 | 8.4 | 13.72 | 8.421 | 22.1 | -0.095 | 1.629 | 4.437% | -3.61 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.096 | 459 | 300 | 0 | 74.2 | 384.8 | 386.5 | 1.7 | -2.97 | 4.659 | 7.197 | 0.647 | 43.22% | 386.8 | -4.1 | 6.101 | 7.182 | 2 | -0.095 | 0.849 | 36.35% | -30.77 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.096 | 220 | 62 | 0 | 125 | 95 | 111.3 | 16.3 | 4.43 | 11.866 | 3.273 | 2 | 2.163% | 114.4 | 6.2 | 13.226 | 3.264 | 19.4 | -0.095 | 2 | 1.798% | -0.78 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.096 | 560 | 400 | 0 | 76.4 | 483.6 | 492.9 | 9.3 | -1.86 | 11.2 | 11.046 | 1.014 | 9.637% | 494.2 | -2.6 | 13.234 | 11.024 | 10.6 | -0.095 | 1.2 | 8.367% | -7.3 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.096 | 420 | 270 | 0 | 53.4 | 366.6 | 370.2 | 3.6 | -2.65 | 6.185 | 6.801 | 0.91 | 18.67% | 367.6 | -3.7 | 4.63 | 6.787 | 1 | -0.095 | 0.682 | 66.53% | -58.63 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.096 | 407 | 170 | 0 | 50.5 | 356.5 | 362 | 5.5 | -2.98 | 8.41 | 6.546 | 1.285 | 11.85% | 359 | -4.1 | 6.567 | 6.533 | 2.5 | -0.095 | 1.005 | 25.79% | -22.8 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.096 | 355 | 70 | 0 | 135.9 | 219.1 | 239.8 | 20.7 | 12.68 | 7.946 | 5.669 | 1.402 | 2.745% | 247.2 | 17.6 | 10.442 | 5.658 | 28.1 | -0.095 | 1.846 | 2.001% | -1.25 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.096 | 105 | 12 | 0 | 92.7 | 12.3 | 14.4 | 2.1 | 0.47 | 1.577 | 2.146 | 0.735 | 8.013% | 14.2 | 0.7 | 1.219 | 2.141 | 1.9 | -0.095 | 0.569 | 8.765% | -1.02 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.096 | 320 | 50 | 0 | 234.7 | 85.3 | 98 | 12.7 | 1.19 | 11.506 | 4.614 | 2 | 4.034% | 97.8 | 1.7 | 10.896 | 4.605 | 12.5 | -0.095 | 2 | 4.056% | -1.09 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.096 | 420 | 50 | 0 | 339.9 | 80.1 | 91.1 | 11 | 2.16 | 8.77 | 5.58 | 1.572 | 6.112% | 96.5 | 3 | 13.356 | 5.569 | 16.4 | -0.095 | 2 | 4.057% | -0.78 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.096 | 27 | 4 | 0 | 5.5 | 21.5 | 23.1 | 1.6 | -0.1 | 1.719 | 0.423 | 2 | 2.718% | 25.4 | -0.1 | 4.026 | 0.422 | 3.9 | -0.095 | 2 | 1.103% | -0.87 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.096 | 229 | 150 | 21 | 38.9 | 169.1 | 175.1 | 6 | -0.55 | 6.474 | 3.559 | 1.819 | 6.111% | 175.5 | -0.8 | 7.109 | 3.552 | 6.4 | -0.095 | 2 | 5.67% | -4.22 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.096 | 435 | 120 | 0 | 294.5 | 140.5 | 146.5 | 6 | -7.55 | 13.543 | 8.099 | 1.672 | 11.6% | 150.3 | -10.5 | 20.285 | 8.083 | 9.8 | -0.095 | 2 | 7.031% | -2.29 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.096 | 170.4 | 0 | 40 | 10.9 | 119.5 | 126.1 | 6.6 | -0.09 | 6.688 | 2.045 | 2 | 4.135% | 120.9 | -0.1 | 1.493 | 2.04 | 1.4 | -0.095 | 0.732 | 19.29% | -13.64 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.096 | 578.7 | 260 | 32.8 | 25.9 | 520 | 527.2 | 7.2 | 2.38 | 4.832 | 8.559 | 0.565 | 12.86% | 525.9 | 3.3 | 2.652 | 8.541 | 5.9 | -0.095 | 0.311 | 15.53% | -14.1 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.096 | 585.6 | 260 | 53.3 | 26.3 | 506 | 512.7 | 6.7 | 1.35 | 5.427 | 8.346 | 0.65 | 13.99% | 512 | 1.9 | 4.13 | 8.329 | 6 | -0.095 | 0.496 | 15.46% | -13.49 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.096 | 86 | 35 | 0 | 31.3 | 54.7 | 66.2 | 11.5 | 5.33 | 6.215 | 1.589 | 2 | 1.199% | 71 | 7.4 | 8.922 | 1.586 | 16.3 | -0.095 | 2 | 0.8371% | -0.54 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.096 | 361 | 242 | 7 | 60.7 | 293.3 | 318 | 24.7 | 6.37 | 18.415 | 5.551 | 2 | 2.34% | 317.5 | 8.9 | 15.376 | 5.539 | 24.2 | -0.095 | 2 | 2.363% | -1.94 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.096 | 491 | 318 | 0 | 81.3 | 409.7 | 422.9 | 13.2 | -0.47 | 13.674 | 7.699 | 1.776 | 5.954% | 424.5 | -0.7 | 15.471 | 7.683 | 14.8 | -0.095 | 2 | 5.255% | -4.43 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.096 | 228 | 150 | 22 | 44.1 | 161.9 | 166.3 | 4.4 | -0.71 | 5.097 | 3.065 | 1.663 | 8.297% | 168.4 | -1 | 7.512 | 3.058 | 6.5 | -0.095 | 2 | 5.558% | -3.98 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.096 | 227 | 150 | 23 | 42.8 | 161.2 | 166.4 | 5.2 | -0.82 | 6.091 | 3.032 | 2 | 6.99% | 168.3 | -1.1 | 8.273 | 3.026 | 7.1 | -0.095 | 2 | 5.066% | -3.63 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.096 | 217 | 150 | 17 | 39.4 | 160.6 | 165.7 | 5.1 | -0.45 | 5.631 | 2.984 | 1.887 | 6.813% | 166.6 | -0.6 | 6.722 | 2.978 | 6 | -0.095 | 2 | 5.731% | -4.28 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.096 | 227 | 150 | 21 | 44.2 | 161.8 | 167.2 | 5.4 | -0.93 | 6.407 | 3.064 | 2 | 6.731% | 168.6 | -1.3 | 8.173 | 3.058 | 6.8 | -0.095 | 2 | 5.29% | -3.8 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.096 | 232 | 150 | 16 | 50.8 | 165.2 | 169 | 3.8 | -1.24 | 5.046 | 3.078 | 1.639 | 9.776% | 170.5 | -1.7 | 7.077 | 3.072 | 5.3 | -0.095 | 2 | 6.936% | -4.98 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.096 | 234 | 150 | 16 | 52.9 | 165.1 | 169.9 | 4.8 | -1.99 | 6.744 | 3.243 | 2 | 7.806% | 170.9 | -2.8 | 8.501 | 3.236 | 5.8 | -0.095 | 2 | 6.393% | -4.55 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.096 | 200 | 40 | 0 | 152.6 | 47.4 | 49.5 | 2.1 | -4.45 | 6.469 | 3.991 | 1.621 | 15.25% | 48.9 | -6.2 | 7.648 | 3.983 | 1.5 | -0.095 | 1.92 | 21.13% | -5.04 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.096 | 312.3 | 134 | 48.8 | 15.1 | 248.4 | 257.2 | 8.8 | 4.45 | 4.371 | 4.132 | 1.058 | 5.681% | 258.8 | 6.2 | 4.233 | 4.124 | 10.4 | -0.095 | 1.027 | 4.757% | -3.82 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.096 | 49.8 | 24 | 0 | 15 | 34.8 | 37.4 | 2.6 | -1.25 | 3.842 | 0.92 | 2 | 3.076% | 41.7 | -1.7 | 8.662 | 0.918 | 6.9 | -0.095 | 2 | 1.147% | -0.8 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.096 | 49.8 | 24 | 0 | 10.7 | 39.1 | 40.9 | 1.8 | -0.16 | 1.975 | 0.921 | 2 | 4.442% | 43.8 | -0.2 | 4.89 | 0.919 | 4.7 | -0.095 | 2 | 1.684% | -1.33 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.096 | 463 | 232 | 4.2 | 75 | 383.8 | 397.3 | 13.5 | -0.53 | 14.035 | 7.194 | 1.951 | 5.49% | 402.4 | -0.7 | 19.325 | 7.179 | 18.6 | -0.095 | 2 | 3.943% | -3.3 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.096 | 223.7 | 170 | 20 | 6.5 | 197.2 | 199.4 | 2.2 | -0.12 | 2.335 | 3.194 | 0.731 | 16.28% | 200.4 | -0.2 | 3.35 | 3.187 | 3.2 | -0.095 | 1.051 | 11.08% | -9.85 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.096 | 109 | 45 | 0 | 50.7 | 58.3 | 68 | 9.7 | 1.6 | 8.091 | 1.709 | 2 | 1.801% | 69.4 | 2.2 | 8.867 | 1.706 | 11.1 | -0.095 | 2 | 1.557% | -0.84 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.096 | 940 | 359.1 | 0 | 19.2 | 920.8 | 928.5 | 7.7 | -1.3 | 9 | 13.673 | 0.658 | 19.54% | 928.9 | -1.8 | 9.858 | 13.645 | 8.1 | -0.095 | 0.722 | 18.38% | -18.19 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.096 | 940 | 359.1 | 0 | 19.2 | 920.8 | 928.5 | 7.7 | -1.3 | 9 | 13.673 | 0.658 | 19.54% | 928.9 | -1.8 | 9.858 | 13.645 | 8.1 | -0.095 | 0.722 | 18.38% | -18.19 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.096 | 940 | 359.1 | 0 | 19.2 | 920.8 | 928.5 | 7.7 | -1.3 | 9 | 13.673 | 0.658 | 19.54% | 928.9 | -1.8 | 9.858 | 13.645 | 8.1 | -0.095 | 0.722 | 18.38% | -18.19 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.096 | 940 | 359.1 | 0 | 19.2 | 920.8 | 928.5 | 7.7 | -1.3 | 9 | 13.673 | 0.658 | 19.54% | 928.9 | -1.8 | 9.858 | 13.645 | 8.1 | -0.095 | 0.722 | 18.38% | -18.19 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.096 | 595 | 310 | 0 | 14.7 | 580.3 | 576.1 | -4.2 | -5.97 | 1.837 | 12.278 | 0.15 | -22.67% | 579 | -8.3 | 6.974 | 12.253 | -1.3 | -0.095 | 0.569 | -72.49% | 71.4 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.096 | 41 | 13 | 0 | 26.2 | 14.8 | 15.1 | 0.3 | 0 | 0.335 | 0.61 | 0.549 | 22.06% | 14.4 | 0 | -0.371 | 0.608 | -0.4 | -0.095 | 0 | -16.37% | 5.78 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.096 | 115 | 65 | 0 | 24 | 91 | 92.1 | 1.1 | -4.25 | 5.317 | 1.803 | 2 | 16.75% | 91.5 | -5.9 | 6.442 | 1.799 | 0.5 | -0.095 | 2 | 36.47% | -29.06 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.096 | 169 | 142 | 0 | 26.4 | 142.6 | 148.4 | 5.8 | -0.42 | 6.304 | 2.348 | 2 | 4.672% | 147.9 | -0.6 | 5.968 | 2.342 | 5.3 | -0.095 | 2 | 5.059% | -4.29 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.096 | 242 | 215 | 0 | 25.7 | 216.3 | 225.5 | 9.2 | 0.63 | 8.541 | 3.316 | 2 | 4.215% | 227.5 | 0.9 | 10.282 | 3.307 | 11.2 | -0.095 | 2 | 3.426% | -3.08 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.08 | 190 | 85 | 0 | 37 | 153 | 161.1 | 8.1 | 0 | 8.125 | 3.774 | 2 | 3.131% | 167 | 0 | 14 | 3.704 | 14 | -0.078 | 2 | 1.766% | -1.46 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.08 | 635 | 250 | 5 | 23 | 607 | 617 | 10 | -2.65 | 12.611 | 10.621 | 1.187 | 8.47% | 618.5 | -3.7 | 15.193 | 10.44 | 11.5 | -0.078 | 1.455 | 7.181% | -7.04 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 459 | 300 | 0 | 46.8 | 412.2 | 421 | 8.8 | 0.3 | 8.498 | 7.738 | 1.098 | 6.958% | 421 | 0.4 | 8.341 | 7.607 | 8.8 | -0.078 | 1.097 | 6.784% | -6.24 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.08 | 230 | 60 | 0 | 168.5 | 61.5 | 66.9 | 5.4 | -0.03 | 5.431 | 3.637 | 1.493 | 5.69% | 67.9 | 0 | 6.418 | 3.556 | 6.4 | -0.078 | 1.805 | 4.681% | -1.27 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 560 | 135 | 0 | 41.5 | 518.5 | 524.7 | 6.2 | 0.48 | 5.808 | 12.408 | 0.468 | 12.05% | 526.4 | 0.7 | 7.252 | 12.203 | 7.9 | -0.078 | 0.594 | 9.219% | -8.75 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 420 | 255 | 0 | 21.7 | 398.3 | 404.2 | 5.9 | 0.06 | 5.802 | 7.411 | 0.783 | 9.496% | 403.1 | 0.1 | 4.692 | 7.289 | 4.8 | -0.078 | 0.644 | 11.38% | -11.06 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 407 | 255 | 0 | 53.6 | 353.4 | 360.1 | 6.7 | -0.67 | 7.35 | 7.012 | 1.048 | 8.104% | 358.5 | -0.9 | 5.999 | 6.896 | 5.1 | -0.078 | 0.87 | 10.38% | -9.23 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 420 | 70 | 0 | 202.6 | 217.4 | 225.1 | 7.7 | 0.25 | 7.495 | 6.802 | 1.102 | 7.276% | 224.4 | 0.3 | 6.734 | 6.689 | 7 | -0.078 | 1.007 | 7.804% | -4.14 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 355 | 70 | 0 | 114.5 | 240.5 | 246.5 | 6 | -0.2 | 6.171 | 6.49 | 0.951 | 7.894% | 247 | -0.3 | 6.725 | 6.383 | 6.5 | -0.078 | 1.054 | 7.104% | -4.93 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 212 | 130 | 14 | 41.3 | 156.7 | 166 | 9.3 | -1.17 | 10.446 | 3.338 | 2 | 3.042% | 167 | -1.6 | 11.87 | 3.281 | 10.3 | -0.078 | 2 | 2.678% | -2.03 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | STM | -0.08 | 108.8 | 18.8 | 0 | 21.5 | 87.3 | 93.6 | 6.3 | -0.15 | 6.441 | 2.379 | 2 | 2.307% | 93.5 | -0.2 | 6.406 | 2.34 | 6.2 | -0.078 | 2 | 2.286% | -1.87 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.08 | 126.2 | 19.2 | 0 | 23.1 | 103.1 | 106.9 | 3.8 | 0.05 | 3.793 | 2.754 | 1.377 | 4.436% | 107 | 0.1 | 3.854 | 2.708 | 3.9 | -0.078 | 1.423 | 4.214% | -3.52 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.08 | 309 | 55 | 0 | 60.4 | 248.6 | 256.5 | 7.9 | -0.03 | 7.914 | 6.565 | 1.205 | 5.219% | 256.6 | 0 | 8.098 | 6.457 | 8 | -0.078 | 1.254 | 5.025% | -4.14 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | FOSS | -0.08 | 234 | 47 | 0 | 7.4 | 226.6 | 232.9 | 6.3 | -3.03 | 9.384 | 3.326 | 2 | 4.961% | 232.2 | -4.2 | 9.847 | 3.252 | 5.6 | -0.078 | 2 | 5.442% | -5.39 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.08 | 209 | 150 | 5 | 39.1 | 164.9 | 170.2 | 5.3 | -0.13 | 5.426 | 3.698 | 1.467 | 5.263% | 170.2 | -0.2 | 5.495 | 3.637 | 5.3 | -0.078 | 1.511 | 5.132% | -4.14 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.08 | 217 | 150 | 12 | 38.9 | 166.1 | 171.2 | 5.1 | 0.04 | 5.111 | 3.73 | 1.37 | 5.679% | 171.5 | 0.1 | 5.401 | 3.668 | 5.4 | -0.078 | 1.472 | 5.229% | -4.1 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.08 | 209 | 150 | 5 | 38.9 | 165.1 | 170.1 | 5 | -0.05 | 5.124 | 3.7 | 1.385 | 5.579% | 170.2 | -0.1 | 5.214 | 3.639 | 5.1 | -0.078 | 1.433 | 5.333% | -4.31 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.08 | 395 | 100 | 0 | 20.4 | 374.6 | 390.8 | 16.2 | -1.17 | 17.348 | 5.273 | 2 | 3.255% | 393.7 | -1.6 | 20.745 | 5.155 | 19.1 | -0.078 | 2 | 2.691% | -2.61 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 425 | 120 | 0 | 181.5 | 243.5 | 242.2 | -1.3 | -7.7 | 6.414 | 7.896 | 0.812 | -43.61% | 241.8 | -10.7 | 9.058 | 7.765 | -1.7 | -0.078 | 1.166 | -32.52% | 19.08 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 425 | 120 | 0 | 302.5 | 122.5 | 132.4 | 9.9 | -1.74 | 11.58 | 8.586 | 1.349 | 5.727% | 137.7 | -2.4 | 17.616 | 8.444 | 15.2 | -0.078 | 2 | 3.637% | -1.07 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 44 | 20 | 0 | 16.2 | 27.8 | 29.9 | 2.1 | 1.5 | 0.599 | 0.874 | 0.686 | 2.807% | 29.9 | 2.1 | -0.001 | 0.858 | 2.1 | -0.078 | 0 | 2.737% | -1.75 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 512 | 332 | 0 | 26.6 | 485.4 | 498.6 | 13.2 | -0.41 | 13.592 | 8.632 | 1.575 | 5.174% | 500.5 | -0.6 | 15.703 | 8.485 | 15.1 | -0.078 | 1.851 | 4.41% | -4.28 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.08 | 122 | 15 | 0 | 51.9 | 70.1 | 71.7 | 1.6 | -0.44 | 2.028 | 1.9 | 1.068 | 10.2% | 72.1 | -0.6 | 2.637 | 1.857 | 2 | -0.078 | 1.42 | 7.958% | -4.64 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 118 | 15 | 0 | 11.8 | 106.2 | 107.5 | 1.3 | 0 | 1.223 | 1.776 | 0.689 | 12.15% | 103.5 | 0 | -2.769 | 1.737 | -2.7 | -0.078 | 0 | -5.702% | 5.22 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.08 | 223 | 150 | 12 | 39.9 | 171.1 | 175.6 | 4.5 | -0.01 | 4.531 | 3.431 | 1.32 | 6.614% | 175.4 | 0 | 4.321 | 3.375 | 4.3 | -0.078 | 1.28 | 6.748% | -5.3 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.08 | 221 | 150 | 12 | 38.6 | 170.4 | 174.9 | 4.5 | 0.32 | 4.253 | 3.391 | 1.254 | 6.554% | 175 | 0.4 | 4.158 | 3.335 | 4.6 | -0.078 | 1.247 | 6.252% | -4.93 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.08 | 211 | 150 | 5 | 38.8 | 167.2 | 171.6 | 4.4 | 0.11 | 4.323 | 3.325 | 1.3 | 6.4% | 171.7 | 0.2 | 4.344 | 3.27 | 4.5 | -0.078 | 1.329 | 6.102% | -4.95 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.08 | 223 | 150 | 12 | 39.9 | 171.1 | 175.8 | 4.7 | -0.18 | 4.875 | 3.431 | 1.421 | 6.332% | 175.6 | -0.3 | 4.69 | 3.374 | 4.5 | -0.078 | 1.39 | 6.449% | -5.06 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.08 | 70 | 20 | 0 | 41.3 | 28.7 | 29.9 | 1.2 | -1 | 2.192 | 1.506 | 1.455 | 7.801% | 29.6 | -1.4 | 2.231 | 1.482 | 0.9 | -0.078 | 1.506 | 10.14% | -4.22 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.08 | 200 | 40 | 0 | 61.1 | 138.9 | 141.9 | 3 | 0.01 | 3.035 | 4.012 | 0.756 | 8.898% | 141 | 0 | 2.056 | 3.946 | 2.1 | -0.078 | 0.521 | 12.39% | -8.81 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | GT | -0.08 | 103 | 35 | 0 | 39 | 64 | 65.4 | 1.4 | 0 | 1.396 | 2.046 | 0.683 | 9.83% | 69 | 0 | 4.986 | 2.008 | 5 | -0.078 | 2 | 2.684% | -1.7 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.08 | 103 | 35 | 0 | 38.2 | 64.8 | 66.5 | 1.7 | 0 | 1.727 | 2.046 | 0.844 | 8.095% | 70.1 | 0 | 5.294 | 2.008 | 5.3 | -0.078 | 2 | 2.532% | -1.62 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.08 | 510 | 210 | 0 | 28.1 | 481.9 | 488 | 6.1 | 0.35 | 5.806 | 11.3 | 0.514 | 11.15% | 491.4 | 0.5 | 9.09 | 11.113 | 9.5 | -0.078 | 0.818 | 6.982% | -6.76 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.08 | 520 | 210 | 0 | 30.6 | 489.4 | 497.4 | 8 | 0.47 | 7.522 | 11.522 | 0.653 | 8.67% | 501 | 0.6 | 10.911 | 11.331 | 11.6 | -0.078 | 0.963 | 5.83% | -5.62 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 647.5 | 243.8 | 0 | 19.5 | 628 | 637.3 | 9.3 | 0.87 | 8.441 | 9.548 | 0.884 | 9.286% | 640.2 | 1.2 | 11.059 | 9.39 | 12.2 | -0.078 | 1.178 | 6.902% | -6.86 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 647.5 | 243.8 | 0 | 19.5 | 628 | 637.3 | 9.3 | 0.87 | 8.441 | 9.548 | 0.884 | 9.286% | 640.2 | 1.2 | 11.059 | 9.39 | 12.2 | -0.078 | 1.178 | 6.902% | -6.86 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 647.5 | 243.8 | 0 | 19.5 | 628 | 637.3 | 9.3 | 0.87 | 8.441 | 9.548 | 0.884 | 9.286% | 640.2 | 1.2 | 11.059 | 9.39 | 12.2 | -0.078 | 1.178 | 6.902% | -6.86 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 647.5 | 243.8 | 0 | 19.5 | 628 | 637.3 | 9.3 | 0.87 | 8.441 | 9.548 | 0.884 | 9.286% | 640.2 | 1.2 | 11.059 | 9.39 | 12.2 | -0.078 | 1.178 | 6.902% | -6.86 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 647.5 | 243.8 | 0 | 19.5 | 628 | 637.3 | 9.3 | 0.87 | 8.441 | 9.548 | 0.884 | 9.286% | 640.2 | 1.2 | 11.059 | 9.39 | 12.2 | -0.078 | 1.178 | 6.902% | -6.86 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 86 | 50 | 0 | 24.9 | 61.1 | 61.6 | 0.5 | -1.18 | 1.689 | 1.708 | 0.989 | 22.99% | 61.5 | -1.6 | 2.013 | 1.677 | 0.4 | -0.078 | 1.201 | 28.02% | -20.3 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.08 | 47 | 12 | 0 | 22.9 | 24.1 | 34.3 | 10.2 | 5.98 | 4.204 | 0.934 | 2 | 0.6172% | 38.6 | 8.3 | 6.171 | 0.916 | 14.5 | -0.078 | 2 | 0.4233% | -0.22 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.08 | 391 | 220 | 0 | 42.1 | 348.9 | 355.4 | 6.5 | -0.12 | 6.571 | 10.03 | 0.655 | 8.021% | 356.8 | -0.2 | 8.036 | 9.892 | 7.9 | -0.078 | 0.812 | 6.434% | -5.89 | 0 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 940 | 359.1 | 0 | 47.2 | 892.8 | 902.1 | 9.3 | -0.24 | 9.521 | 14.857 | 0.641 | 13.48% | 903.1 | -0.3 | 10.654 | 14.611 | 10.3 | -0.078 | 0.729 | 11.87% | -11.55 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 940 | 359.1 | 0 | 47.2 | 892.8 | 902.1 | 9.3 | -0.24 | 9.521 | 14.857 | 0.641 | 13.48% | 903.1 | -0.3 | 10.654 | 14.611 | 10.3 | -0.078 | 0.729 | 11.87% | -11.55 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 940 | 359.1 | 0 | 47.2 | 892.8 | 902.1 | 9.3 | -0.24 | 9.521 | 14.857 | 0.641 | 13.48% | 903.1 | -0.3 | 10.654 | 14.611 | 10.3 | -0.078 | 0.729 | 11.87% | -11.55 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 940 | 359.1 | 0 | 47.2 | 892.8 | 902.1 | 9.3 | -0.24 | 9.521 | 14.857 | 0.641 | 13.48% | 903.1 | -0.3 | 10.654 | 14.611 | 10.3 | -0.078 | 0.729 | 11.87% | -11.55 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 449 | 35 | 0 | 145 | 304 | 322 | 18 | 12.75 | 5.304 | 6.245 | 0.849 | 3.329% | 338 | 17.7 | 16.231 | 6.105 | 34 | -0.078 | 2 | 1.718% | -1.19 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 41 | 13 | 0 | 27.4 | 13.6 | 13.4 | -0.2 | -0.35 | 0.135 | 0.679 | 0.199 | -27.62% | 13 | -0.5 | -0.107 | 0.664 | -0.6 | -0.078 | 0 | -8.978% | 2.93 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.08 | 155 | 80 | 0 | 20.4 | 134.6 | 137.5 | 2.9 | -0.11 | 2.965 | 3.126 | 0.949 | 7.136% | 139.6 | -0.1 | 5.124 | 3.075 | 5 | -0.078 | 1.667 | 4.036% | -3.58 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 232.4 | 130 | 0 | 19.6 | 212.8 | 217.2 | 4.4 | 0 | 4.433 | 3.918 | 1.131 | 7.049% | 216.9 | 0 | 4.149 | 3.851 | 4.1 | -0.078 | 1.077 | 7.376% | -6.91 | 0.017 | 0.058 | 5.933% | 5.163%
Hydro | WAT | HYDR | -0.08 | 22 | 0 | 0 | 4.9 | 17.1 | 17.3 | 0.2 | 0 | 0.254 | 0.487 | 0.52 | 14.81% | 17.5 | 0 | 0.429 | 0.479 | 0.4 | -0.078 | 0.894 | 7.221% | -5.63 | 0.017 | 0.05 | 0.2285% | 0.2528%
CombinedCycle | CC | COGN | -0.07 | 635 | 250 | 103 | 48 | 484 | 506.5 | 22.5 | -1.41 | 23.907 | 9.35 | 2 | 3.294% | 515.2 | -2 | 33.127 | 10.457 | 31.2 | -0.078 | 2 | 2.647% | -1.81 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.07 | 527 | 370 | 48 | 29.2 | 449.8 | 460.9 | 11.1 | -0.18 | 11.23 | 8.418 | 1.334 | 5.542% | 462.1 | -0.2 | 12.546 | 9.415 | 12.3 | -0.078 | 1.333 | 5.572% | -4.26 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.07 | 459 | 300 | 0 | 109 | 350 | 364.9 | 14.9 | 0.75 | 14.121 | 8.067 | 1.75 | 3.596% | 363 | 1 | 11.996 | 9.022 | 13 | -0.078 | 1.33 | 4.592% | -3.14 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.07 | 249 | 206 | 0 | 35.4 | 213.6 | 221.8 | 8.2 | -0.02 | 8.229 | 4.376 | 1.88 | 3.546% | 223 | 0 | 9.367 | 4.894 | 9.4 | -0.078 | 1.914 | 3.447% | -2.65 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.07 | 560 | 400 | 0 | 91.3 | 468.7 | 481.3 | 12.6 | -0.52 | 13.107 | 12.186 | 1.076 | 5.187% | 481.1 | -0.7 | 13.072 | 13.573 | 12.4 | -0.078 | 0.963 | 5.873% | -4.41 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.07 | 407 | 270 | 0 | 109.3 | 297.7 | 310.8 | 13.1 | 0.12 | 13.005 | 7.119 | 1.827 | 3.627% | 307.9 | 0.2 | 10.123 | 7.93 | 10.2 | -0.078 | 1.277 | 5.19% | -3.4 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.07 | 746 | 436 | 0 | 157.7 | 588.3 | 617.2 | 28.9 | 1.26 | 27.642 | 12.921 | 2 | 3.013% | 623.1 | 1.7 | 33.039 | 14.601 | 34.8 | -0.078 | 2 | 2.788% | -1.97 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.07 | 749 | 436 | 0 | 310.3 | 438.7 | 460.1 | 21.4 | 1 | 20.456 | 13.596 | 1.505 | 4.086% | 466.1 | 1.4 | 26.083 | 15.363 | 27.4 | -0.078 | 1.698 | 3.556% | -1.87 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.07 | 366 | 161 | 64 | 19.1 | 282.9 | 284.6 | 1.7 | -0.77 | 2.423 | 5.308 | 0.457 | 25.13% | 283.8 | -1.1 | 1.967 | 5.936 | 0.9 | -0.078 | 0.331 | 52.9% | -36.64 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.07 | 71 | 37 | 0 | 6.7 | 64.3 | 67.4 | 3.1 | 0.12 | 3.024 | 1.248 | 2 | 2.681% | 67.9 | 0.2 | 3.45 | 1.396 | 3.6 | -0.078 | 2 | 2.572% | -2.08 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.07 | 320 | 50 | 0 | 148.9 | 171.1 | 187.9 | 16.8 | 2.11 | 14.745 | 4.917 | 2 | 2.224% | 188 | 2.9 | 13.984 | 5.477 | 16.9 | -0.078 | 2 | 2.463% | -1.18 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.07 | 420 | 50 | 0 | 307.2 | 112.8 | 129.8 | 17 | 0.01 | 16.99 | 6.224 | 2 | 2.884% | 128.1 | 0 | 15.278 | 6.933 | 15.3 | -0.078 | 2 | 3.57% | -0.86 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.07 | 43 | 10 | 0 | 24 | 19 | 28.3 | 9.3 | -0.2 | 9.455 | 0.756 | 2 | 0.5425% | 30.9 | -0.3 | 12.168 | 0.845 | 11.9 | -0.078 | 2 | 0.4721% | -0.18 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.07 | 213 | 150 | 5 | 39.4 | 168.6 | 175.2 | 6.6 | 0.3 | 6.305 | 4.024 | 1.567 | 3.769% | 174.1 | 0.4 | 5.012 | 4.483 | 5.5 | -0.078 | 1.118 | 5.04% | -3.57 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.07 | 220 | 155 | 12 | 39 | 169 | 175.1 | 6.1 | 0.51 | 5.671 | 4.029 | 1.408 | 4.212% | 174 | 0.7 | 4.35 | 4.487 | 5 | -0.078 | 0.969 | 5.726% | -3.94 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.07 | 213 | 150 | 5 | 39.4 | 168.6 | 175.3 | 6.7 | 0.21 | 6.501 | 4.023 | 1.616 | 3.713% | 174.2 | 0.3 | 5.354 | 4.482 | 5.6 | -0.078 | 1.195 | 4.95% | -3.51 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.07 | 425 | 120 | 0 | 304.2 | 120.8 | 138.5 | 17.7 | 1.74 | 16.017 | 9.014 | 1.777 | 2.803% | 143.9 | 2.4 | 20.696 | 10.041 | 23.1 | -0.078 | 2 | 2.393% | -0.61 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.07 | 217.3 | 35 | 40 | 34.5 | 142.8 | 157 | 14.2 | 1.34 | 12.845 | 3.116 | 2 | 1.787% | 163.6 | 1.9 | 18.867 | 3.485 | 20.8 | -0.078 | 2 | 1.359% | -0.8 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.07 | 608 | 305 | 120 | 84.9 | 403.1 | 414.1 | 11 | 0.25 | 10.694 | 8.577 | 1.247 | 6.451% | 422.2 | 0.3 | 18.739 | 9.592 | 19.1 | -0.078 | 1.954 | 4.14% | -2.46 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.07 | 100 | 57 | 0 | 6.2 | 93.8 | 93.9 | 0.1 | 0 | 0.136 | 2.074 | 0.066 | 117% | 94.1 | 0 | 0.397 | 2.341 | 0.3 | -0.078 | 0.17 | 43.43% | -36.38 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.07 | 511 | 331 | 0 | 103 | 408 | 426.2 | 18.2 | 0.35 | 17.855 | 8.981 | 1.988 | 3.277% | 428.6 | 0.5 | 20.129 | 10.044 | 20.6 | -0.078 | 2 | 3.226% | -2.31 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.07 | 528 | 305 | 6.5 | 22.8 | 498.7 | 511.8 | 13.1 | 1.68 | 11.5 | 9.166 | 1.255 | 4.704% | 512.6 | 2.3 | 11.605 | 10.251 | 13.9 | -0.078 | 1.132 | 4.94% | -4.18 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.07 | 528 | 310.3 | 34.1 | 12.5 | 481.4 | 493.8 | 12.4 | 1.2 | 11.131 | 8.681 | 1.282 | 4.97% | 493.2 | 1.7 | 10.125 | 9.709 | 11.8 | -0.078 | 1.043 | 5.819% | -4.76 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.07 | 234 | 150 | 12 | 60.8 | 161.2 | 167.9 | 6.7 | 0.37 | 6.336 | 3.759 | 1.686 | 4.079% | 169.4 | 0.5 | 7.687 | 4.187 | 8.2 | -0.078 | 1.836 | 3.713% | -2.29 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.07 | 233 | 150 | 12 | 59.8 | 161.2 | 168.1 | 6.9 | 0.24 | 6.623 | 3.742 | 1.77 | 3.944% | 169.3 | 0.3 | 7.792 | 4.168 | 8.1 | -0.078 | 1.87 | 3.743% | -2.32 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.07 | 223 | 150 | 5 | 56.6 | 161.4 | 168.9 | 7.5 | 0.35 | 7.17 | 3.702 | 1.937 | 3.473% | 170.6 | 0.5 | 8.762 | 4.124 | 9.2 | -0.078 | 2 | 3.154% | -2.04 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.07 | 241 | 160 | 5 | 64.4 | 171.6 | 180 | 8.4 | 0.58 | 7.747 | 3.992 | 1.941 | 3.351% | 182.1 | 0.8 | 9.681 | 4.446 | 10.5 | -0.078 | 2 | 2.987% | -1.9 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.07 | 615 | 250 | 116.4 | 15.4 | 483.2 | 493.1 | 9.9 | 0.02 | 9.852 | 8.763 | 1.124 | 7.25% | 492.9 | 0 | 9.651 | 9.801 | 9.7 | -0.078 | 0.985 | 8.245% | -5.81 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.07 | 725.2 | 445 | 31.1 | 119.5 | 574.6 | 600.5 | 25.9 | 0.3 | 25.599 | 12.199 | 2 | 3.268% | 610.9 | 0.4 | 35.918 | 13.643 | 36.3 | -0.078 | 2 | 2.598% | -1.85 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.07 | 275 | 225 | 0 | 49.3 | 225.7 | 237.7 | 12 | 0.53 | 11.469 | 4.833 | 2 | 2.676% | 237.1 | 0.7 | 10.661 | 5.405 | 11.4 | -0.078 | 1.972 | 3.138% | -2.31 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.07 | 690 | 420 | 0 | 85.5 | 604.5 | 635.6 | 31.1 | 1.68 | 29.429 | 12.127 | 2 | 2.589% | 637 | 2.3 | 30.144 | 13.563 | 32.5 | -0.078 | 2 | 2.761% | -2.17 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.07 | 78 | 55 | 0 | 21 | 57 | 59.3 | 2.3 | 0.26 | 2.074 | 1.618 | 1.282 | 3.969% | 58.9 | 0.4 | 1.563 | 1.826 | 1.9 | -0.078 | 0.856 | 5.352% | -3.49 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.07 | 78 | 55 | 0 | 20.3 | 57.7 | 59.9 | 2.2 | 0.35 | 1.841 | 1.618 | 1.138 | 4.149% | 59.4 | 0.5 | 1.143 | 1.826 | 1.7 | -0.078 | 0.626 | 5.981% | -3.94 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.07 | 244 | 228 | 0 | 6.2 | 237.8 | 242.9 | 5.1 | 0.26 | 4.883 | 4.288 | 1.139 | 5.587% | 243.4 | 0.4 | 5.207 | 4.796 | 5.6 | -0.078 | 1.086 | 5.669% | -4.95 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.07 | 247 | 231 | 0 | 8.8 | 238.2 | 244.1 | 5.9 | 0.45 | 5.372 | 4.341 | 1.237 | 4.889% | 245 | 0.6 | 6.116 | 4.855 | 6.8 | -0.078 | 1.26 | 4.726% | -4.08 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.07 | 165 | 76 | 0 | 88.8 | 76.2 | 83.4 | 7.2 | -0.13 | 7.332 | 2.31 | 2 | 2.681% | 81.1 | -0.2 | 5.073 | 2.611 | 4.9 | -0.078 | 1.943 | 4.389% | -1.8 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.07 | 536 | 270 | 0 | 113.5 | 422.5 | 438.1 | 15.6 | -0.09 | 15.626 | 10.372 | 1.507 | 4.012% | 433.1 | -0.1 | 10.653 | 11.72 | 10.6 | -0.078 | 0.909 | 6.579% | -4.64 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.07 | 45 | 13 | 0 | 6 | 39 | 40.8 | 1.8 | 0.3 | 1.546 | 0.933 | 1.656 | 2.932% | 40.9 | 0.4 | 1.49 | 1.053 | 1.9 | -0.078 | 1.414 | 3.094% | -2.38 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.07 | 45 | 13 | 0 | 6 | 39 | 40.8 | 1.8 | 0.3 | 1.552 | 0.933 | 1.662 | 2.932% | 40.9 | 0.4 | 1.54 | 1.053 | 1.9 | -0.078 | 1.462 | 3.094% | -2.38 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.062 | 258.7 | 140 | 12 | 74.1 | 172.6 | 175.7 | 3.1 | 0.06 | 3.036 | 3.819 | 0.795 | 8.632% | 179.5 | 0.1 | 6.811 | 3.294 | 6.9 | -0.054 | 2 | 3.378% | -2.58 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 524 | 340 | 59 | 30.2 | 434.8 | 446.3 | 11.5 | -1 | 12.474 | 7.198 | 1.733 | 4.711% | 449.2 | -1.4 | 15.81 | 6.208 | 14.4 | -0.054 | 2 | 3.277% | -3.12 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 459 | 300 | 0 | 85 | 374 | 387 | 13 | 1.26 | 11.764 | 7.105 | 1.656 | 3.651% | 386.2 | 1.7 | 10.433 | 6.128 | 12.2 | -0.054 | 1.703 | 3.388% | -3.17 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 248 | 143 | 7 | 92.2 | 148.8 | 150.4 | 1.6 | -0.35 | 1.984 | 3.731 | 0.532 | 16.03% | 148.6 | -0.5 | 0.335 | 3.217 | -0.2 | -0.054 | 0.104 | -111.7% | 76.74 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 224 | 208 | 0 | 14.3 | 209.7 | 215 | 5.3 | 0.91 | 4.402 | 3.468 | 1.269 | 4.373% | 217 | 1.3 | 6.061 | 2.99 | 7.3 | -0.054 | 2 | 2.766% | -2.96 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 174 | 120 | 5.1 | 46.3 | 122.6 | 123.2 | 0.6 | 0.18 | 0.369 | 2.615 | 0.141 | 30.01% | 123.6 | 0.2 | 0.725 | 2.255 | 1 | -0.054 | 0.322 | 15.69% | -12.64 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.062 | 410 | 250 | 0 | 9.1 | 400.9 | 415.9 | 15 | 1.55 | 13.532 | 7.026 | 1.926 | 2.826% | 412.2 | 2.2 | 9.198 | 6.112 | 11.3 | -0.054 | 1.505 | 3.268% | -3.66 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.062 | 785 | 605 | 0 | 177.6 | 607.4 | 626.5 | 19.1 | 1.68 | 17.467 | 13.843 | 1.262 | 4.248% | 625.3 | 2.3 | 15.555 | 12.043 | 17.9 | -0.054 | 1.292 | 3.949% | -3.5 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.062 | 407 | 125 | 0 | 258.7 | 148.3 | 165.6 | 17.3 | 2.76 | 14.494 | 5.864 | 2 | 2.433% | 172 | 3.8 | 19.867 | 5.102 | 23.7 | -0.054 | 2 | 1.547% | -0.65 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.062 | 230.6 | 168 | 12 | 48 | 170.6 | 179.1 | 8.5 | 0.3 | 8.155 | 3.384 | 2 | 2.807% | 181.5 | 0.4 | 10.489 | 2.918 | 10.9 | -0.054 | 2 | 1.907% | -1.61 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 238.6 | 155 | 18 | 63.2 | 157.4 | 162.6 | 5.2 | 0.06 | 5.164 | 3.415 | 1.512 | 4.747% | 162.1 | 0.1 | 4.604 | 2.945 | 4.7 | -0.054 | 1.563 | 4.575% | -3.45 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.062 | 420 | 50 | 0 | 360 | 60 | 75.7 | 15.7 | 0.25 | 15.4 | 5.698 | 2 | 2.766% | 76.3 | 0.3 | 15.878 | 4.958 | 16.3 | -0.054 | 2 | 2.321% | -0.38 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.062 | 455 | 268 | 0 | 33.9 | 421.1 | 427.4 | 6.3 | 0.47 | 5.853 | 7.043 | 0.831 | 7.467% | 429.1 | 0.7 | 7.343 | 6.074 | 8 | -0.054 | 1.209 | 5.122% | -5.44 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 530.5 | 351.1 | 0 | 15.8 | 514.7 | 523.2 | 8.5 | 1.62 | 6.91 | 8.212 | 0.841 | 6.453% | 519.9 | 2.2 | 3.017 | 7.082 | 5.2 | -0.054 | 0.426 | 9.187% | -10.22 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 920 | 461 | 149.7 | 23.3 | 747 | 767.9 | 20.9 | 4.67 | 16.289 | 11.924 | 1.366 | 4.55% | 771 | 6.5 | 17.572 | 10.283 | 24 | -0.054 | 1.709 | 3.451% | -3.22 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 544.1 | 310 | 134.9 | 96.3 | 312.9 | 317.2 | 4.3 | 0 | 4.251 | 6.334 | 0.671 | 13.08% | 319.6 | 0 | 6.656 | 5.463 | 6.7 | -0.054 | 1.219 | 7.313% | -4.82 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.062 | 470 | 180 | 0 | 290 | 180 | 185.2 | 5.2 | 0.08 | 5.03 | 6.155 | 0.817 | 9.351% | 183.6 | 0.1 | 3.488 | 5.337 | 3.6 | -0.054 | 0.654 | 11.77% | -5.15 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.062 | 470 | 180 | 0 | 290 | 180 | 185.2 | 5.2 | 0.08 | 5.03 | 6.155 | 0.817 | 9.351% | 183.6 | 0.1 | 3.488 | 5.337 | 3.6 | -0.054 | 0.654 | 11.77% | -5.15 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.062 | 470 | 180 | 0 | 290 | 180 | 185.2 | 5.2 | 0.08 | 5.03 | 6.155 | 0.817 | 9.351% | 183.6 | 0.1 | 3.488 | 5.337 | 3.6 | -0.054 | 0.654 | 11.77% | -5.15 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.062 | 470 | 180 | 0 | 290 | 180 | 185.2 | 5.2 | 0.08 | 5.03 | 6.155 | 0.817 | 9.351% | 183.6 | 0.1 | 3.488 | 5.337 | 3.6 | -0.054 | 0.654 | 11.77% | -5.15 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.062 | 490 | 348 | 37 | 41.7 | 411.3 | 425.8 | 14.5 | -0.75 | 15.274 | 7.012 | 2 | 3.494% | 424.8 | -1 | 14.499 | 6.048 | 13.5 | -0.054 | 2 | 3.269% | -3.15 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 475 | 348 | 38 | 23.9 | 413.1 | 425.9 | 12.8 | 0.4 | 12.41 | 6.765 | 1.835 | 3.837% | 425.3 | 0.6 | 11.736 | 5.834 | 12.2 | -0.054 | 2 | 3.506% | -3.5 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.062 | 219 | 150 | 12 | 54.9 | 152.1 | 156.8 | 4.7 | 1.12 | 3.564 | 3.537 | 1.008 | 4.821% | 156.1 | 1.6 | 2.462 | 3.077 | 4 | -0.054 | 0.8 | 4.935% | -3.92 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.062 | 218 | 155 | 12 | 48.8 | 157.2 | 163.7 | 6.5 | 0.93 | 5.507 | 3.52 | 1.564 | 3.47% | 164 | 1.3 | 5.439 | 3.062 | 6.8 | -0.054 | 1.776 | 2.889% | -2.38 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.062 | 218 | 150 | 12 | 52.3 | 153.7 | 159.4 | 5.7 | 1.11 | 4.578 | 3.52 | 1.301 | 3.957% | 161.5 | 1.5 | 6.191 | 3.062 | 7.8 | -0.054 | 2 | 2.519% | -2.03 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 417.2 | 275 | 25 | 80.3 | 311.9 | 320 | 8.1 | -1.17 | 9.199 | 6.071 | 1.515 | 5.326% | 322 | -1.6 | 11.702 | 5.236 | 10.1 | -0.054 | 2 | 3.72% | -3.19 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 613 | 305 | 120 | 128.7 | 364.3 | 371.7 | 7.4 | -0.86 | 8.238 | 7.632 | 1.079 | 8.564% | 371.9 | -1.2 | 8.76 | 6.582 | 7.6 | -0.054 | 1.331 | 7.263% | -4.95 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.062 | 648 | 258 | 0 | 299.1 | 348.9 | 377.8 | 28.9 | 5.38 | 23.555 | 10.372 | 2 | 2.318% | 378.9 | 7.5 | 22.567 | 9.024 | 30 | -0.054 | 2 | 1.945% | -1.2 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.062 | 844 | 450 | 0 | 389.4 | 454.6 | 468.1 | 13.5 | 1.21 | 12.227 | 13.654 | 0.896 | 6.462% | 468.5 | 1.7 | 12.146 | 11.879 | 13.9 | -0.054 | 1.023 | 5.467% | -3.38 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.062 | 102 | 54 | 0 | 20.3 | 81.7 | 87.8 | 6.1 | 1.16 | 4.98 | 1.869 | 2 | 1.733% | 86.3 | 1.6 | 2.999 | 1.591 | 4.6 | -0.054 | 1.885 | 2.002% | -1.83 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 505 | 327 | 0 | 111 | 394 | 408.4 | 14.4 | 0.41 | 14.041 | 7.817 | 1.796 | 3.626% | 408.9 | 0.6 | 14.354 | 6.742 | 14.9 | -0.054 | 2 | 3.052% | -2.73 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 540 | 305 | 37.6 | 47.3 | 455.1 | 465.3 | 10.2 | 1.16 | 9.005 | 7.778 | 1.158 | 5.473% | 463.7 | 1.6 | 6.962 | 6.708 | 8.6 | -0.054 | 1.038 | 5.654% | -5.46 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 261.2 | 226 | 24.6 | 9.3 | 227.3 | 232.4 | 5.1 | 0.87 | 4.169 | 3.663 | 1.138 | 5.298% | 231.7 | 1.2 | 3.139 | 3.159 | 4.4 | -0.054 | 0.994 | 5.349% | -5.33 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.062 | 231 | 150 | 12 | 61.3 | 157.7 | 165.9 | 8.2 | 0.7 | 7.576 | 3.328 | 2 | 2.914% | 168 | 1 | 9.321 | 2.896 | 10.3 | -0.054 | 2 | 2.021% | -1.58 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.062 | 230 | 150 | 12 | 45 | 173 | 180.6 | 7.6 | 1.2 | 6.405 | 3.363 | 1.905 | 3.131% | 182.3 | 1.7 | 7.646 | 2.926 | 9.3 | -0.054 | 2 | 2.229% | -1.92 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.062 | 232 | 150 | 12 | 62.5 | 157.5 | 166 | 8.5 | 0.67 | 7.807 | 3.344 | 2 | 2.824% | 168.6 | 0.9 | 10.127 | 2.909 | 11.1 | -0.054 | 2 | 1.884% | -1.46 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.062 | 520 | 210 | 0 | 197.9 | 322.1 | 333.6 | 11.5 | 1.54 | 9.946 | 10.892 | 0.913 | 4.675% | 337.6 | 2.1 | 13.372 | 9.476 | 15.5 | -0.054 | 1.411 | 3.021% | -2.15 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.062 | 530 | 210 | 0 | 225.2 | 304.8 | 315.7 | 10.9 | 2.36 | 8.487 | 11.101 | 0.764 | 5.027% | 319.8 | 3.3 | 11.643 | 9.658 | 15 | -0.054 | 1.205 | 3.182% | -2.1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.062 | 795 | 300 | 0 | 134.2 | 660.8 | 665.3 | 4.5 | 0.42 | 4.016 | 16.652 | 0.241 | 18.26% | 669.5 | 0.6 | 8.049 | 14.487 | 8.7 | -0.054 | 0.556 | 8.227% | -7.85 | 0.017 | 0.05 | 6.284% | 5.784%
Hydro | NA | HYDR | -0.062 | 15 | 0 | 0 | 8.9 | 6.1 | 13.1 | 7 | 3.62 | 3.343 | 0.314 | 2 | 0.2255% | 13.1 | 5 | 1.925 | 0.273 | 7 | -0.054 | 2 | 0.1969% | -0.09 | 0.017 | 0.05 | 0.2285% | 0.2528%
CombinedCycle | CC | COGN | -0.062 | 499 | 332 | 46.5 | 113.4 | 339.1 | 351.4 | 12.3 | 3.58 | 8.688 | 7.005 | 1.24 | 4.194% | 359.3 | 5 | 15.247 | 6.041 | 20.2 | -0.054 | 2 | 2.225% | -1.73 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 756.9 | 436.7 | 44.6 | 209.4 | 502.9 | 529 | 26.1 | 3.01 | 23.095 | 11.026 | 2 | 2.998% | 532.2 | 4.2 | 25.141 | 9.509 | 29.3 | -0.054 | 2 | 2.326% | -1.77 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.062 | 66 | 35 | 0 | 28.8 | 37.2 | 39.3 | 2.1 | 0.44 | 1.714 | 1.209 | 1.418 | 3.261% | 38.9 | 0.6 | 1.177 | 1.029 | 1.7 | -0.054 | 1.143 | 3.511% | -2.24 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.062 | 68 | 37 | 0 | 30 | 38 | 40.2 | 2.2 | 0.44 | 1.713 | 1.246 | 1.375 | 3.207% | 39.8 | 0.6 | 1.203 | 1.061 | 1.8 | -0.054 | 1.135 | 3.416% | -2.17 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.062 | 390 | 181 | 1.2 | 175.3 | 213.5 | 252 | 38.5 | 8.26 | 30.258 | 6.019 | 2 | 1.047% | 265.1 | 11.5 | 40.149 | 5.191 | 51.6 | -0.054 | 2 | 0.6808% | -0.43 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 521 | 349 | 18 | 151.3 | 351.7 | 359.9 | 8.2 | 1.3 | 6.873 | 7.786 | 0.883 | 6.569% | 360.6 | 1.8 | 7.108 | 6.715 | 8.9 | -0.054 | 1.059 | 5.272% | -4.08 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.062 | 55.9 | 22.5 | 0 | 27.5 | 28.4 | 33.5 | 5.1 | 2.44 | 2.604 | 1.025 | 2 | 1.138% | 40 | 3.4 | 8.145 | 0.872 | 11.6 | -0.054 | 2 | 0.4361% | -0.25 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.062 | 55.9 | 22.5 | 0 | 27.7 | 28.2 | 33.1 | 4.9 | 2.24 | 2.619 | 1.024 | 2 | 1.185% | 39.2 | 3.1 | 7.87 | 0.872 | 11 | -0.054 | 2 | 0.4599% | -0.26 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.062 | 940 | 359.1 | 0 | 83.3 | 856.7 | 873 | 16.3 | -2.3 | 18.654 | 14.227 | 1.311 | 5.961% | 872.4 | -3.2 | 18.984 | 12.377 | 15.7 | -0.054 | 1.534 | 5.39% | -5.64 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.062 | 940 | 359.1 | 0 | 83.3 | 856.7 | 873 | 16.3 | -2.3 | 18.654 | 14.227 | 1.311 | 5.961% | 872.4 | -3.2 | 18.984 | 12.377 | 15.7 | -0.054 | 1.534 | 5.39% | -5.64 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.062 | 940 | 359.1 | 0 | 83.3 | 856.7 | 873 | 16.3 | -2.3 | 18.654 | 14.227 | 1.311 | 5.961% | 872.4 | -3.2 | 18.984 | 12.377 | 15.7 | -0.054 | 1.534 | 5.39% | -5.64 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.062 | 940 | 359.1 | 0 | 83.3 | 856.7 | 873 | 16.3 | -2.3 | 18.654 | 14.227 | 1.311 | 5.961% | 872.4 | -3.2 | 18.984 | 12.377 | 15.7 | -0.054 | 1.534 | 5.39% | -5.64 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.062 | 80 | 55 | 0 | 22.5 | 57.5 | 59.2 | 1.7 | 0.44 | 1.254 | 1.466 | 0.855 | 4.879% | 58.9 | 0.6 | 0.774 | 1.248 | 1.4 | -0.054 | 0.62 | 5.163% | -4.22 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.062 | 80 | 55 | 0 | 21.7 | 58.3 | 60 | 1.7 | 0.44 | 1.194 | 1.466 | 0.814 | 4.879% | 59.6 | 0.6 | 0.702 | 1.248 | 1.3 | -0.054 | 0.563 | 5.56% | -4.61 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.062 | 664 | 155 | 0 | 115.7 | 548.3 | 564.8 | 16.5 | -0.13 | 16.721 | 10.968 | 1.525 | 4.16% | 563.8 | -0.2 | 15.752 | 9.542 | 15.5 | -0.054 | 1.651 | 3.857% | -3.65 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.062 | 663 | 156 | 0 | 137.1 | 525.9 | 539.9 | 14 | 0.23 | 13.719 | 11.11 | 1.235 | 4.896% | 538.1 | 0.3 | 11.891 | 9.666 | 12.2 | -0.054 | 1.23 | 4.893% | -4.45 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.062 | 577 | 156 | 0 | 21.5 | 555.5 | 566.8 | 11.3 | -1.21 | 12.539 | 9.117 | 1.375 | 5.279% | 563.7 | -1.7 | 9.859 | 7.932 | 8.2 | -0.054 | 1.243 | 6.336% | -7 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.062 | 600 | 159 | 0 | 47.9 | 552.1 | 562.7 | 10.6 | 0 | 10.607 | 9.553 | 1.11 | 5.852% | 562.3 | 0 | 10.185 | 8.311 | 10.2 | -0.054 | 1.225 | 5.297% | -5.59 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.065 | 257 | 140 | 12 | 54 | 191 | 193.9 | 2.9 | 0.42 | 2.492 | 3.845 | 0.648 | 9.61% | 197.7 | 0.6 | 6.089 | 3.161 | 6.7 | -0.054 | 1.926 | 3.456% | -3.08 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 531 | 335 | 64 | 49.8 | 417.2 | 425.1 | 7.9 | -0.06 | 7.956 | 7.33 | 1.085 | 7.285% | 426.9 | -0.1 | 9.811 | 6.025 | 9.7 | -0.054 | 1.628 | 4.93% | -4.66 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 459 | 300 | 0 | 81.8 | 377.2 | 385.9 | 8.7 | 0.05 | 8.631 | 7.204 | 1.198 | 5.719% | 385.7 | 0.1 | 8.417 | 5.922 | 8.5 | -0.054 | 1.421 | 4.863% | -4.8 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 218 | 202 | 0 | 15.7 | 202.3 | 210.2 | 7.9 | 0.18 | 7.702 | 3.422 | 2 | 2.993% | 210.2 | 0.2 | 7.604 | 2.813 | 7.9 | -0.054 | 2 | 2.487% | -2.77 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 182 | 134 | 8.2 | 37.8 | 136 | 138.6 | 2.6 | -0.06 | 2.622 | 2.728 | 0.961 | 7.594% | 138.9 | -0.1 | 2.939 | 2.242 | 2.9 | -0.054 | 1.311 | 5.658% | -5.07 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.065 | 560 | 400 | 0 | 154.3 | 405.7 | 420 | 14.3 | -0.16 | 14.424 | 9.563 | 1.508 | 4.244% | 417.6 | -0.2 | 12.122 | 7.91 | 11.9 | -0.054 | 1.532 | 4.238% | -3.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 407 | 125 | 0 | 260 | 147 | 154.9 | 7.9 | 0.02 | 7.896 | 5.821 | 1.357 | 5.585% | 154.4 | 0 | 7.343 | 4.815 | 7.4 | -0.054 | 1.525 | 4.954% | -2.15 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.065 | 231.7 | 168 | 12 | 50.3 | 169.4 | 175.5 | 6.1 | -0.35 | 6.471 | 3.448 | 1.877 | 4.12% | 180.1 | -0.5 | 11.178 | 2.835 | 10.7 | -0.054 | 2 | 1.952% | -1.71 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 239.7 | 155 | 18 | 58.3 | 163.4 | 169 | 5.6 | -0.71 | 6.292 | 3.48 | 1.808 | 4.642% | 172.4 | -1 | 9.957 | 2.86 | 9 | -0.054 | 2 | 2.4% | -1.96 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 250 | 182 | 0 | 67.7 | 182.3 | 186.9 | 4.6 | 0.34 | 4.226 | 3.924 | 1.077 | 5.894% | 187.2 | 0.5 | 4.437 | 3.225 | 4.9 | -0.054 | 1.376 | 4.598% | -4.02 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 372 | 161 | 72 | 6.8 | 293.2 | 295.7 | 2.5 | -0.3 | 2.727 | 4.709 | 0.579 | 16.13% | 294.8 | -0.4 | 1.968 | 3.871 | 1.6 | -0.054 | 0.508 | 20.94% | -19.83 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.065 | 105 | 12 | 0 | 93 | 12 | 15.2 | 3.2 | 0.11 | 3.047 | 2.148 | 1.418 | 3.564% | 14.9 | 0.1 | 2.731 | 1.777 | 2.9 | -0.054 | 1.537 | 3.268% | -0.44 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.065 | 415 | 50 | 0 | 349.1 | 65.9 | 78.4 | 12.5 | 0.6 | 11.867 | 5.55 | 2 | 3.599% | 78.8 | 0.8 | 12.051 | 4.591 | 12.9 | -0.054 | 2 | 2.898% | -0.55 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.065 | 910.6 | 461 | 169.4 | 45.7 | 695.5 | 724.5 | 29 | 9.2 | 19.765 | 11.632 | 1.699 | 3.403% | 731.5 | 12.8 | 23.147 | 9.562 | 36 | -0.054 | 2 | 2.277% | -2.09 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 913.5 | 461 | 150 | 68.2 | 695.3 | 723.6 | 28.3 | 9.04 | 19.258 | 11.984 | 1.607 | 3.498% | 730.5 | 12.6 | 22.639 | 9.851 | 35.2 | -0.054 | 2 | 2.336% | -2.14 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 544.1 | 310 | 134.9 | 97.7 | 311.5 | 316.5 | 5 | 1.79 | 3.209 | 6.422 | 0.5 | 11.79% | 318.6 | 2.5 | 4.596 | 5.279 | 7.1 | -0.054 | 0.871 | 6.901% | -4.75 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.065 | 470 | 180 | 0 | 289 | 181 | 184.7 | 3.7 | 0.01 | 3.733 | 4.504 | 0.829 | 13.78% | 184.5 | 0 | 3.514 | 3.429 | 3.5 | -0.054 | 1.025 | 12.1% | -5.59 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 470 | 180 | 0 | 289 | 181 | 184.7 | 3.7 | 0.01 | 3.733 | 4.504 | 0.829 | 13.78% | 184.5 | 0 | 3.514 | 3.429 | 3.5 | -0.054 | 1.025 | 12.1% | -5.59 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 470 | 180 | 0 | 289 | 181 | 184.7 | 3.7 | 0.01 | 3.733 | 4.504 | 0.829 | 13.78% | 184.5 | 0 | 3.514 | 3.429 | 3.5 | -0.054 | 1.025 | 12.1% | -5.59 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 470 | 180 | 0 | 289 | 181 | 184.7 | 3.7 | 0.01 | 3.733 | 4.504 | 0.829 | 13.78% | 184.5 | 0 | 3.514 | 3.429 | 3.5 | -0.054 | 1.025 | 12.1% | -5.59 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | STM | -0.065 | 310.4 | 56.4 | 0 | 251.5 | 58.9 | 72.1 | 13.2 | -1.34 | 14.492 | 6.343 | 2 | 2.55% | 73.7 | -1.9 | 16.661 | 5.246 | 14.8 | -0.054 | 2 | 1.889% | -0.43 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | COGN | -0.065 | 219 | 150 | 12 | 47.5 | 159.5 | 166.8 | 7.3 | 0.34 | 6.943 | 3.49 | 1.989 | 3.254% | 169.1 | 0.5 | 9.167 | 2.887 | 9.6 | -0.054 | 2 | 2.056% | -1.8 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.065 | 219 | 155 | 12 | 50.4 | 156.6 | 161.5 | 4.9 | 0.05 | 4.915 | 3.49 | 1.408 | 4.848% | 161.9 | 0.1 | 5.314 | 2.887 | 5.3 | -0.054 | 1.84 | 3.724% | -3.2 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.065 | 219 | 150 | 12 | 44.4 | 162.6 | 167.3 | 4.7 | 0.3 | 4.497 | 3.49 | 1.289 | 5.054% | 169.4 | 0.4 | 6.385 | 2.887 | 6.8 | -0.054 | 2 | 2.903% | -2.59 | 0.017 | 0.05 | 5.933% | 5.163%
Wind | WND | WIND | -0.065 | 94.7 | 0 | 0 | 7.4 | 87.3 | 90 | 2.7 | -1.76 | 4.434 | 1.957 | 2 | 3.81% | 89.6 | -2.4 | 4.752 | 1.619 | 2.3 | -0.054 | 2 | 3.718% | -4.1 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.065 | 230.2 | 35.1 | 40 | 25 | 165.2 | 168.1 | 2.9 | 1.57 | 1.272 | 2.985 | 0.426 | 8.609% | 164.7 | 2.2 | -2.736 | 2.454 | -0.5 | -0.054 | 0 | -41.49% | 35.74 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 574 | 305 | 120 | 77.3 | 376.7 | 385.2 | 8.5 | 1.33 | 7.196 | 7.126 | 1.01 | 7.319% | 388.6 | 1.8 | 10.044 | 5.857 | 11.9 | -0.054 | 1.715 | 4.344% | -3.43 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.065 | 87 | 35 | 0 | 51 | 36 | 38.7 | 2.7 | 0.24 | 2.507 | 1.609 | 1.558 | 3.501% | 38.4 | 0.3 | 2.069 | 1.299 | 2.4 | -0.054 | 1.593 | 3.274% | -1.61 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.065 | 649 | 259 | 0 | 388.3 | 260.7 | 286.9 | 26.2 | 0.8 | 25.37 | 10.642 | 2 | 2.685% | 288.5 | 1.1 | 26.675 | 8.803 | 27.8 | -0.054 | 2 | 2.102% | -1.01 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.065 | 526 | 305 | 29 | 44.2 | 452.8 | 463.2 | 10.4 | 1.3 | 9.043 | 7.8 | 1.159 | 5.482% | 461.5 | 1.8 | 6.845 | 6.412 | 8.7 | -0.054 | 1.068 | 5.445% | -5.64 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 527.9 | 305.3 | 35.4 | 39.2 | 453.3 | 463.3 | 10 | 1.39 | 8.645 | 7.731 | 1.118 | 5.722% | 460.9 | 1.9 | 5.685 | 6.355 | 7.6 | -0.054 | 0.895 | 6.255% | -6.46 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.065 | 230 | 150 | 12 | 55.6 | 162.4 | 167.5 | 5.1 | -1.07 | 6.241 | 3.265 | 1.911 | 4.891% | 170.6 | -1.5 | 9.73 | 2.701 | 8.2 | -0.054 | 2 | 2.528% | -2.14 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.065 | 228 | 150 | 12 | 53.7 | 162.3 | 167.9 | 5.6 | -0.75 | 6.357 | 3.235 | 1.965 | 4.416% | 170.5 | -1 | 9.283 | 2.676 | 8.2 | -0.054 | 2 | 2.506% | -2.14 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.065 | 225 | 150 | 12 | 52 | 161 | 167 | 6 | 0.8 | 5.151 | 3.191 | 1.614 | 4.067% | 169.7 | 1.1 | 7.595 | 2.64 | 8.7 | -0.054 | 2 | 2.331% | -2 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.065 | 230 | 150 | 12 | 55.6 | 162.4 | 166.8 | 4.4 | -0.91 | 5.317 | 3.267 | 1.627 | 5.669% | 168.5 | -1.3 | 7.294 | 2.703 | 6.1 | -0.054 | 2 | 3.398% | -2.88 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.065 | 805 | 310 | 0 | 144.1 | 660.9 | 691.5 | 30.6 | 9.9 | 20.615 | 16.639 | 1.239 | 2.851% | 692.9 | 13.8 | 18.147 | 13.763 | 32 | -0.054 | 1.319 | 2.265% | -2.24 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.065 | 805 | 310 | 0 | 228.9 | 576.1 | 590.7 | 14.6 | 3.01 | 11.612 | 16.639 | 0.698 | 5.975% | 590.2 | 4.2 | 9.958 | 13.763 | 14.1 | -0.054 | 0.724 | 5.14% | -4.42 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.065 | 570 | 310 | 0 | 116.4 | 453.6 | 475.5 | 21.9 | 7.65 | 14.248 | 11.782 | 1.209 | 2.821% | 477.4 | 10.6 | 13.175 | 9.745 | 23.8 | -0.054 | 1.352 | 2.157% | -2.06 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.065 | 515 | 210 | 0 | 139.9 | 375.1 | 384.8 | 9.7 | 3.55 | 6.084 | 10.645 | 0.572 | 5.755% | 387.9 | 4.9 | 7.839 | 8.805 | 12.8 | -0.054 | 0.89 | 3.623% | -3.17 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.065 | 530 | 210 | 0 | 160.6 | 369.4 | 379.9 | 10.5 | 1.75 | 8.674 | 10.955 | 0.792 | 5.471% | 382.5 | 2.4 | 10.656 | 9.061 | 13.1 | -0.054 | 1.176 | 3.643% | -3.05 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.065 | 504 | 351 | 45.8 | 105.9 | 352.3 | 365.7 | 13.4 | 1.38 | 12.008 | 7.192 | 1.67 | 4.077% | 373.4 | 1.9 | 19.18 | 5.912 | 21.1 | -0.054 | 2 | 2.151% | -1.81 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.065 | 650 | 189.8 | 0 | 90.4 | 559.6 | 571.9 | 12.3 | -0.02 | 12.29 | 8.803 | 1.396 | 5.727% | 576.7 | 0 | 17.124 | 7.282 | 17.1 | -0.054 | 2 | 3.423% | -3.54 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 650 | 189.8 | 0 | 90.4 | 559.6 | 571.9 | 12.3 | -0.02 | 12.29 | 8.803 | 1.396 | 5.727% | 576.7 | 0 | 17.124 | 7.282 | 17.1 | -0.054 | 2 | 3.423% | -3.54 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 650 | 189.8 | 0 | 90.4 | 559.6 | 571.9 | 12.3 | -0.02 | 12.29 | 8.803 | 1.396 | 5.727% | 576.7 | 0 | 17.124 | 7.282 | 17.1 | -0.054 | 2 | 3.423% | -3.54 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 650 | 189.8 | 0 | 90.4 | 559.6 | 571.9 | 12.3 | -0.02 | 12.29 | 8.803 | 1.396 | 5.727% | 576.7 | 0 | 17.124 | 7.282 | 17.1 | -0.054 | 2 | 3.423% | -3.54 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 650 | 189.8 | 0 | 90.4 | 559.6 | 571.9 | 12.3 | -0.02 | 12.29 | 8.803 | 1.396 | 5.727% | 576.7 | 0 | 17.124 | 7.282 | 17.1 | -0.054 | 2 | 3.423% | -3.54 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.065 | 731.5 | 445 | 40 | 178.2 | 513.3 | 537.8 | 24.5 | -0.12 | 24.577 | 10.853 | 2 | 3.236% | 540.9 | -0.2 | 27.736 | 8.922 | 27.6 | -0.054 | 2 | 2.386% | -2.01 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 730.9 | 445 | 45.1 | 181.9 | 503.9 | 521.4 | 17.5 | -1.77 | 19.233 | 10.764 | 1.787 | 4.526% | 530.9 | -2.5 | 29.42 | 8.848 | 27 | -0.054 | 2 | 2.437% | -2.02 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 729.7 | 445 | 46.8 | 153.5 | 529.4 | 548.7 | 19.3 | -0.65 | 19.889 | 10.718 | 1.856 | 4.097% | 557.9 | -0.9 | 29.375 | 8.811 | 28.5 | -0.054 | 2 | 2.305% | -2.01 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 389.8 | 185 | 8.3 | 188.9 | 192.6 | 218.6 | 26 | -6.61 | 32.599 | 5.988 | 2 | 1.625% | 233.1 | -9.2 | 49.724 | 4.922 | 40.5 | -0.054 | 2 | 0.8669% | -0.51 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 501 | 347 | 15 | 138.7 | 347.3 | 354.4 | 7.1 | -0.06 | 7.14 | 7.628 | 0.936 | 7.648% | 355.4 | -0.1 | 8.182 | 6.27 | 8.1 | -0.054 | 1.305 | 5.57% | -4.64 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.065 | 56 | 22.5 | 0 | 31.9 | 24.1 | 26.5 | 2.4 | -0.61 | 2.96 | 1.035 | 2 | 2.54% | 32.5 | -0.8 | 9.259 | 0.835 | 8.4 | -0.054 | 2 | 0.6034% | -0.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 940 | 359.1 | 0 | 113 | 827 | 848.6 | 21.6 | -0.07 | 21.693 | 14.19 | 1.529 | 4.716% | 847 | -0.1 | 20.089 | 11.737 | 20 | -0.054 | 1.712 | 4.231% | -4.48 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 940 | 359.1 | 0 | 113 | 827 | 848.6 | 21.6 | -0.07 | 21.693 | 14.19 | 1.529 | 4.716% | 847 | -0.1 | 20.089 | 11.737 | 20 | -0.054 | 1.712 | 4.231% | -4.48 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 940 | 359.1 | 0 | 113 | 827 | 848.6 | 21.6 | -0.07 | 21.693 | 14.19 | 1.529 | 4.716% | 847 | -0.1 | 20.089 | 11.737 | 20 | -0.054 | 1.712 | 4.231% | -4.48 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 940 | 359.1 | 0 | 113 | 827 | 848.6 | 21.6 | -0.07 | 21.693 | 14.19 | 1.529 | 4.716% | 847 | -0.1 | 20.089 | 11.737 | 20 | -0.054 | 1.712 | 4.231% | -4.48 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.065 | 80 | 55 | 0 | 22.9 | 57.1 | 58.7 | 1.6 | 0.22 | 1.405 | 1.48 | 0.949 | 5.434% | 58.5 | 0.3 | 1.091 | 1.194 | 1.4 | -0.054 | 0.914 | 5.163% | -4.4 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.065 | 80 | 55 | 0 | 22.1 | 57.9 | 59.5 | 1.6 | 0.1 | 1.542 | 1.48 | 1.042 | 5.434% | 59.2 | 0.1 | 1.178 | 1.194 | 1.3 | -0.054 | 0.987 | 5.56% | -4.8 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.065 | 17 | 4 | 0 | 8.7 | 8.3 | 8.3 | 0 | 0 | 0.006 | 0.314 | 0.018 | 0% | 8.3 | 0 | 0.01 | 0.254 | 0 | -0.054 | 0.039 | 0% |  | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.065 | 860 | 460 | 0 | 177.3 | 682.7 | 690.7 | 8 | -3.66 | 11.645 | 13.498 | 0.863 | 11.65% | 691.8 | -5.1 | 14.118 | 11.095 | 9.1 | -0.054 | 1.272 | 8.509% | -8.12 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.065 | 663 | 156 | 0 | 43.6 | 619.4 | 635.6 | 16.2 | 0.31 | 15.804 | 10.478 | 1.508 | 4.435% | 634.9 | 0.4 | 15.017 | 8.667 | 15.5 | -0.054 | 1.733 | 3.852% | -4.33 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.138 | 254.4 | 140 | 12 | 19.7 | 222.7 | 227.6 | 4.9 | 0.18 | 4.745 | 6.936 | 0.684 | 11.95% | 233.7 | 0.2 | 10.748 | 6.813 | 11 | -0.136 | 1.577 | 5.245% | -4.65 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.138 | 459 | 300 | 0 | 46.5 | 412.5 | 431.9 | 19.4 | -1.04 | 20.398 | 13.134 | 1.553 | 5.443% | 431.5 | -1.4 | 20.399 | 12.901 | 19 | -0.136 | 1.581 | 5.477% | -4.99 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.138 | 412 | 70 | 0 | 86.5 | 325.5 | 341 | 15.5 | 4.67 | 10.752 | 10.368 | 1.037 | 6.117% | 341.7 | 6.5 | 9.685 | 10.154 | 16.2 | -0.136 | 0.954 | 5.768% | -4.62 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.138 | 48 | 20 | 0 | 27.6 | 20.4 | 20.9 | 0.5 | 0.03 | 0.422 | 1.616 | 0.261 | 22.14% | 22.3 | 0 | 1.812 | 1.584 | 1.9 | -0.136 | 1.144 | 5.741% | -2.45 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.138 | 48 | 20 | 0 | 27.3 | 20.7 | 24.1 | 3.4 | 0.01 | 3.373 | 1.616 | 2 | 3.255% | 27.6 | 0 | 6.882 | 1.584 | 6.9 | -0.136 | 2 | 1.581% | -0.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.138 | 560 | 400 | 0 | 51 | 509 | 531.1 | 22.1 | -0.18 | 22.266 | 20.793 | 1.071 | 5.829% | 530.4 | -0.3 | 21.56 | 20.43 | 21.4 | -0.136 | 1.055 | 5.933% | -5.47 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.138 | 785 | 600 | 0 | 76.5 | 708.5 | 746.1 | 37.6 | 0.54 | 37.077 | 27.358 | 1.355 | 4.803% | 758.4 | 0.7 | 49.225 | 26.88 | 49.9 | -0.136 | 1.831 | 3.566% | -3.27 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.138 | 407 | 260 | 0 | 88.6 | 318.4 | 337.1 | 18.7 | 2.85 | 15.838 | 11.444 | 1.384 | 5.007% | 334.8 | 4 | 12.419 | 11.244 | 16.4 | -0.136 | 1.104 | 5.627% | -4.46 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.138 | 170 | 126 | 0 | 6.1 | 163.9 | 170.1 | 6.2 | -0.24 | 6.419 | 4.865 | 1.32 | 6.311% | 170.5 | -0.3 | 6.893 | 4.778 | 6.6 | -0.136 | 1.443 | 5.843% | -5.71 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.138 | 105 | 12 | 0 | 92.2 | 12.8 | 16.3 | 3.5 | 0.4 | 3.063 | 3.863 | 0.793 | 6.908% | 16.3 | 0.6 | 2.882 | 3.795 | 3.5 | -0.136 | 0.759 | 6.808% | -0.83 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.138 | 420 | 50 | 0 | 281.4 | 138.6 | 169.1 | 30.5 | 2.85 | 27.63 | 9.954 | 2 | 3.168% | 172.7 | 4 | 30.167 | 9.781 | 34.1 | -0.136 | 2 | 2.793% | -0.93 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.138 | 150 | 75 | 0 | 25.7 | 124.3 | 138.6 | 14.3 | 0.64 | 13.739 | 5.049 | 2 | 2.415% | 141.2 | 0.9 | 16.033 | 4.951 | 16.9 | -0.136 | 2 | 2.014% | -1.69 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.138 | 150 | 75 | 0 | 25.1 | 124.9 | 139.1 | 14.2 | 0.76 | 13.428 | 5.049 | 2 | 2.432% | 141.3 | 1.1 | 15.376 | 4.951 | 16.4 | -0.136 | 2 | 2.075% | -1.75 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | SUB | FOSS | -0.138 | 580.6 | 149.7 | 0 | 39.9 | 540.7 | 569.8 | 29.1 | -0.21 | 29.272 | 15.112 | 1.937 | 4.59% | 567.7 | -0.3 | 27.276 | 14.848 | 27 | -0.136 | 1.837 | 4.875% | -4.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.138 | 580.6 | 149.7 | 0 | 39.9 | 540.7 | 569.8 | 29.1 | -0.21 | 29.272 | 15.112 | 1.937 | 4.59% | 567.7 | -0.3 | 27.276 | 14.848 | 27 | -0.136 | 1.837 | 4.875% | -4.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.138 | 418.9 | 180.3 | 0 | 40.1 | 378.8 | 392.4 | 13.6 | 0.07 | 13.533 | 15.58 | 0.869 | 7.086% | 392.6 | 0.1 | 13.701 | 15.308 | 13.8 | -0.136 | 0.895 | 6.883% | -6.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.138 | 470 | 180 | 0 | 284.8 | 185.2 | 190.3 | 5.1 | 0.07 | 5.008 | 9.506 | 0.527 | 21.21% | 189.5 | 0.1 | 4.187 | 9.31 | 4.3 | -0.136 | 0.45 | 24.79% | -9.89 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.138 | 470 | 180 | 0 | 284.8 | 185.2 | 190.3 | 5.1 | 0.07 | 5.008 | 9.506 | 0.527 | 21.21% | 189.5 | 0.1 | 4.187 | 9.31 | 4.3 | -0.136 | 0.45 | 24.79% | -9.89 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.138 | 470 | 180 | 0 | 284.8 | 185.2 | 190.3 | 5.1 | 0.07 | 5.008 | 9.506 | 0.527 | 21.21% | 189.5 | 0.1 | 4.187 | 9.31 | 4.3 | -0.136 | 0.45 | 24.79% | -9.89 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.138 | 470 | 180 | 0 | 284.8 | 185.2 | 190.3 | 5.1 | 0.07 | 5.008 | 9.506 | 0.527 | 21.21% | 189.5 | 0.1 | 4.187 | 9.31 | 4.3 | -0.136 | 0.45 | 24.79% | -9.89 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.138 | 219 | 155 | 12 | 40.1 | 166.9 | 175.6 | 8.7 | -0.94 | 9.632 | 6.339 | 1.519 | 5.793% | 174.7 | -1.3 | 9.092 | 6.228 | 7.8 | -0.136 | 1.46 | 6.368% | -4.92 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.138 | 220 | 150 | 12 | 40.1 | 167.9 | 176.6 | 8.7 | -0.81 | 9.495 | 6.39 | 1.486 | 5.819% | 175.6 | -1.1 | 8.864 | 6.278 | 7.7 | -0.136 | 1.412 | 6.48% | -5.01 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.138 | 219 | 150 | 12 | 40.3 | 166.7 | 175.2 | 8.5 | -0.99 | 9.447 | 6.336 | 1.491 | 5.929% | 175.1 | -1.4 | 9.759 | 6.225 | 8.4 | -0.136 | 1.568 | 5.913% | -4.56 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.138 | 191 | 7 | 40 | 33 | 118 | 137.1 | 19.1 | -0.17 | 19.305 | 4.321 | 2 | 2.301% | 143.2 | -0.2 | 25.477 | 4.244 | 25.2 | -0.136 | 2 | 1.719% | -1.08 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.138 | 501 | 325 | 0 | 84 | 417 | 436.7 | 19.7 | -0.59 | 20.297 | 14.336 | 1.416 | 5.851% | 442.1 | -0.8 | 25.95 | 14.082 | 25.1 | -0.136 | 1.843 | 4.525% | -3.82 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.138 | 226 | 150 | 12 | 39.5 | 174.5 | 182.1 | 7.6 | -0.72 | 8.267 | 5.887 | 1.404 | 6.843% | 181.8 | -1 | 8.257 | 5.784 | 7.3 | -0.136 | 1.427 | 7.021% | -5.49 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.138 | 231 | 150 | 12 | 40.7 | 178.3 | 186.4 | 8.1 | -0.76 | 8.883 | 6.087 | 1.459 | 6.563% | 186.1 | -1.1 | 8.914 | 5.981 | 7.8 | -0.136 | 1.49 | 6.716% | -5.25 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.138 | 242 | 160 | 12 | 42.8 | 187.2 | 196 | 8.8 | -0.96 | 9.775 | 6.256 | 1.562 | 6.328% | 194.9 | -1.3 | 8.985 | 6.147 | 7.7 | -0.136 | 1.462 | 7.127% | -5.59 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.138 | 724.3 | 414.6 | 24.5 | 91.5 | 608.3 | 638.9 | 30.6 | 0.35 | 30.232 | 20.025 | 1.51 | 5.445% | 646.6 | 0.5 | 37.822 | 19.669 | 38.3 | -0.136 | 1.923 | 4.287% | -3.65 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.138 | 718 | 419.4 | 27.7 | 88.9 | 601.4 | 623.8 | 22.4 | -2.48 | 24.863 | 19.753 | 1.259 | 7.374% | 636.5 | -3.4 | 38.555 | 19.402 | 35.1 | -0.136 | 1.987 | 4.637% | -3.94 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.138 | 49.9 | 24 | 0 | 10.9 | 39 | 43.7 | 4.7 | 0.72 | 3.938 | 1.679 | 2 | 2.448% | 45.8 | 1 | 5.808 | 1.647 | 6.8 | -0.136 | 2 | 1.667% | -1.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.138 | 49.8 | 24 | 0 | 10.9 | 38.9 | 43.9 | 5 | 0.68 | 4.336 | 1.677 | 2 | 2.296% | 45.7 | 0.9 | 5.92 | 1.645 | 6.8 | -0.136 | 2 | 1.664% | -1.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.138 | 49.9 | 24 | 0 | 11 | 38.9 | 43.2 | 4.3 | 1.14 | 3.104 | 1.68 | 1.847 | 2.676% | 45.6 | 1.6 | 5.102 | 1.648 | 6.7 | -0.136 | 2 | 1.692% | -1.33 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.138 | 494.8 | 230 | 21.4 | 80.7 | 392.7 | 409.5 | 16.8 | 3.84 | 13.026 | 13.546 | 0.962 | 6.776% | 417.4 | 5.3 | 19.378 | 13.306 | 24.7 | -0.136 | 1.456 | 4.542% | -3.66 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.138 | 940 | 359.1 | 0 | 39.6 | 900.4 | 913.9 | 13.5 | -0.24 | 13.7 | 24.806 | 0.552 | 16.02% | 913.7 | -0.3 | 13.628 | 24.373 | 13.3 | -0.136 | 0.559 | 16.02% | -15.57 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.138 | 940 | 359.1 | 0 | 39.6 | 900.4 | 913.9 | 13.5 | -0.24 | 13.7 | 24.806 | 0.552 | 16.02% | 913.7 | -0.3 | 13.628 | 24.373 | 13.3 | -0.136 | 0.559 | 16.02% | -15.57 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.138 | 940 | 359.1 | 0 | 39.6 | 900.4 | 913.9 | 13.5 | -0.24 | 13.7 | 24.806 | 0.552 | 16.02% | 913.7 | -0.3 | 13.628 | 24.373 | 13.3 | -0.136 | 0.559 | 16.02% | -15.57 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.138 | 940 | 359.1 | 0 | 39.6 | 900.4 | 913.9 | 13.5 | -0.24 | 13.7 | 24.806 | 0.552 | 16.02% | 913.7 | -0.3 | 13.628 | 24.373 | 13.3 | -0.136 | 0.559 | 16.02% | -15.57 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.138 | 703 | 308 | 70 | 35.1 | 597.9 | 628.3 | 30.4 | 1.96 | 28.457 | 18.114 | 1.571 | 5.32% | 632.8 | 2.7 | 32.215 | 17.792 | 34.9 | -0.136 | 1.811 | 4.567% | -3.94 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.138 | 689 | 300 | 40 | 144.4 | 504.6 | 540.8 | 36.2 | 16.42 | 19.819 | 18.573 | 1.067 | 4.378% | 541.4 | 22.9 | 13.984 | 18.243 | 36.8 | -0.136 | 0.767 | 4.245% | -3.15 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.111 | 46.7 | 25 | 0 | 21.7 | 25 | 27 | 2 | 0 | 1.951 | 1.254 | 1.556 | 4.334% | 29.6 | 0 | 4.57 | 1.163 | 4.6 | -0.105 | 2 | 1.783% | -1 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.111 | 259.2 | 140 | 12 | 70.9 | 176.3 | 188.5 | 12.2 | -1 | 13.173 | 5.638 | 2 | 3.933% | 199 | -1.4 | 24.108 | 5.263 | 22.7 | -0.105 | 2 | 1.999% | -1.44 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.111 | 522 | 335 | 59 | 50.6 | 412.4 | 428 | 15.6 | -0.41 | 15.998 | 10.559 | 1.515 | 6.192% | 430.7 | -0.6 | 18.903 | 9.858 | 18.3 | -0.105 | 1.918 | 4.993% | -4.17 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.111 | 459 | 300 | 0 | 47.1 | 411.9 | 426 | 14.1 | 0.64 | 13.461 | 10.468 | 1.286 | 6.024% | 425.4 | 0.9 | 12.626 | 9.772 | 13.5 | -0.105 | 1.292 | 5.952% | -5.64 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.111 | 560 | 400 | 0 | 155.6 | 404.4 | 424.5 | 20.1 | 0.22 | 19.826 | 13.734 | 1.444 | 5.156% | 421.2 | 0.3 | 16.526 | 12.84 | 16.8 | -0.105 | 1.287 | 5.835% | -4.45 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.111 | 508 | 350 | 0 | 101.7 | 406.3 | 418.1 | 11.8 | 0.02 | 11.805 | 11.586 | 1.019 | 7.967% | 420.5 | 0 | 14.146 | 10.816 | 14.2 | -0.105 | 1.308 | 6.263% | -5.29 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.111 | 105 | 12 | 0 | 92.9 | 12.1 | 15.2 | 3.1 | 0.13 | 2.985 | 3.093 | 0.965 | 6.275% | 15.1 | 0.2 | 2.799 | 2.892 | 3 | -0.105 | 0.968 | 6.134% | -0.74 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.111 | 330 | 148 | 11 | 39.9 | 279.1 | 292.2 | 13.1 | 0.25 | 12.838 | 7.275 | 1.765 | 4.662% | 291.9 | 0.4 | 12.38 | 6.792 | 12.8 | -0.105 | 1.823 | 4.514% | -4.03 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.111 | 12 | 0 | 0 | 7.1 | 4.9 | 7.8 | 2.9 | 0.41 | 2.471 | 0.322 | 2 | 0.7753% | 8.3 | 0.6 | 2.837 | 0.299 | 3.4 | -0.105 | 2 | 0.626% | -0.26 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.111 | 582.8 | 149.3 | 0 | 44 | 538.8 | 563.8 | 25 | -0.64 | 25.656 | 12.186 | 2 | 4.314% | 559.8 | -0.9 | 21.934 | 11.392 | 21 | -0.105 | 1.925 | 4.858% | -4.75 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.111 | 582.8 | 149.3 | 0 | 44 | 538.8 | 563.8 | 25 | -0.64 | 25.656 | 12.186 | 2 | 4.314% | 559.8 | -0.9 | 21.934 | 11.392 | 21 | -0.105 | 1.925 | 4.858% | -4.75 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.111 | 418.9 | 180.3 | 0 | 44.4 | 374.5 | 387 | 12.5 | -0.39 | 12.863 | 12.468 | 1.032 | 6.202% | 388 | -0.5 | 13.987 | 11.656 | 13.5 | -0.105 | 1.2 | 5.432% | -5.13 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.111 | 919.2 | 461 | 101.4 | 24.8 | 793 | 819.5 | 26.5 | 0.26 | 26.181 | 18.649 | 1.404 | 6.418% | 828.7 | 0.4 | 35.307 | 17.41 | 35.7 | -0.105 | 2 | 4.507% | -4.11 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.111 | 470 | 180 | 0 | 289.4 | 180.6 | 185.8 | 5.2 | -0.13 | 5.266 | 7.232 | 0.728 | 16.73% | 185.3 | -0.2 | 4.873 | 6.649 | 4.7 | -0.105 | 0.733 | 17.51% | -7.1 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.111 | 470 | 180 | 0 | 289.4 | 180.6 | 185.8 | 5.2 | -0.13 | 5.266 | 7.232 | 0.728 | 16.73% | 185.3 | -0.2 | 4.873 | 6.649 | 4.7 | -0.105 | 0.733 | 17.51% | -7.1 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.111 | 470 | 180 | 0 | 289.4 | 180.6 | 185.8 | 5.2 | -0.13 | 5.266 | 7.232 | 0.728 | 16.73% | 185.3 | -0.2 | 4.873 | 6.649 | 4.7 | -0.105 | 0.733 | 17.51% | -7.1 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.111 | 470 | 180 | 0 | 289.4 | 180.6 | 185.8 | 5.2 | -0.13 | 5.266 | 7.232 | 0.728 | 16.73% | 185.3 | -0.2 | 4.873 | 6.649 | 4.7 | -0.105 | 0.733 | 17.51% | -7.1 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.111 | 221 | 155 | 12 | 39.6 | 169.4 | 176.2 | 6.8 | 0.34 | 6.464 | 5.163 | 1.252 | 6.017% | 175.2 | 0.5 | 5.285 | 4.827 | 5.8 | -0.105 | 1.095 | 6.673% | -5.4 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.111 | 223 | 150 | 12 | 50.8 | 160.2 | 167.9 | 7.7 | 0.3 | 7.376 | 5.123 | 1.44 | 5.361% | 169.4 | 0.4 | 8.793 | 4.789 | 9.2 | -0.105 | 1.836 | 4.245% | -3.22 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.111 | 222 | 150 | 12 | 49.8 | 160.2 | 167.9 | 7.7 | 0.34 | 7.409 | 5.099 | 1.453 | 5.337% | 169.9 | 0.5 | 9.207 | 4.767 | 9.7 | -0.105 | 1.932 | 4.008% | -3.05 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.111 | 180 | 4.3 | 40 | 30.2 | 109.8 | 125.9 | 16.1 | 0.66 | 15.427 | 3.193 | 2 | 2.07% | 125.8 | 0.9 | 15.035 | 2.981 | 16 | -0.105 | 2 | 1.971% | -1.27 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.111 | 529 | 344 | 0 | 65.4 | 463.6 | 483 | 19.4 | -0.35 | 19.705 | 12.065 | 1.633 | 5.046% | 487.9 | -0.5 | 24.75 | 11.263 | 24.3 | -0.105 | 2 | 3.811% | -3.53 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.111 | 535 | 305 | 1.6 | 13.6 | 519.8 | 525.3 | 5.5 | 0 | 5.483 | 12.166 | 0.451 | 18% | 526 | 0 | 6.206 | 11.357 | 6.2 | -0.105 | 0.546 | 15.11% | -15.51 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.111 | 229 | 150 | 12 | 40.9 | 176.1 | 183 | 6.9 | 0.29 | 6.619 | 4.802 | 1.378 | 6.144% | 182.8 | 0.4 | 6.239 | 4.49 | 6.7 | -0.105 | 1.39 | 5.986% | -4.86 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.111 | 234 | 150 | 12 | 41.8 | 180.2 | 187.3 | 7.1 | 0.32 | 6.804 | 4.965 | 1.371 | 6.101% | 186.9 | 0.4 | 6.22 | 4.641 | 6.7 | -0.105 | 1.34 | 6.116% | -4.97 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.111 | 247 | 160 | 12 | 43.6 | 191.4 | 198.7 | 7.3 | 0.37 | 6.932 | 5.178 | 1.339 | 6.263% | 197.5 | 0.5 | 5.603 | 4.84 | 6.1 | -0.105 | 1.158 | 7.091% | -5.8 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.111 | 800 | 300 | 0 | 156.1 | 643.9 | 674.8 | 30.9 | -0.27 | 31.236 | 23.81 | 1.312 | 4.791% | 669.6 | -0.4 | 26.089 | 22.259 | 25.7 | -0.105 | 1.172 | 5.449% | -4.63 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.111 | 805 | 300 | 0 | 148.8 | 656.2 | 677.2 | 21 | 0.05 | 20.992 | 23.959 | 0.876 | 7.093% | 676.4 | 0.1 | 20.147 | 22.398 | 20.2 | -0.105 | 0.899 | 6.975% | -6.01 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.111 | 815 | 300 | 0 | 171.3 | 643.7 | 658.1 | 14.4 | -4.89 | 19.318 | 24.256 | 0.796 | 10.47% | 652.7 | -6.8 | 15.899 | 22.676 | 9 | -0.105 | 0.701 | 15.85% | -13.23 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.111 | 500 | 210 | 0 | 128.5 | 371.5 | 382.3 | 10.8 | 0.35 | 10.448 | 14.881 | 0.702 | 8.567% | 384.4 | 0.5 | 12.429 | 13.912 | 12.9 | -0.105 | 0.893 | 6.785% | -5.33 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.111 | 450 | 210 | 0 | 158.7 | 291.3 | 303.3 | 12 | -1.56 | 13.557 | 13.393 | 1.012 | 6.94% | 305 | -2.2 | 15.9 | 12.521 | 13.7 | -0.105 | 1.27 | 5.75% | -3.93 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.111 | 795 | 300 | 0 | 175.2 | 619.8 | 631.2 | 11.4 | 0.61 | 10.785 | 23.661 | 0.456 | 12.9% | 636.8 | 0.8 | 16.191 | 22.12 | 17 | -0.105 | 0.732 | 8.185% | -6.74 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.111 | 754 | 434.2 | 22.4 | 92.1 | 639.5 | 669.8 | 30.3 | 0.3 | 29.964 | 16.685 | 1.796 | 4.605% | 671.5 | 0.4 | 31.561 | 15.576 | 32 | -0.105 | 2 | 4.124% | -3.7 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.111 | 739.7 | 432.7 | 38.8 | 163.6 | 537.3 | 562.7 | 25.4 | -0.06 | 25.508 | 15.985 | 1.596 | 5.389% | 571.4 | -0.1 | 34.225 | 14.923 | 34.1 | -0.105 | 2 | 3.797% | -2.91 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.111 | 490.4 | 230 | 5.2 | 221.4 | 263.8 | 283.9 | 20.1 | 0.41 | 19.621 | 11.066 | 1.773 | 4.515% | 294.7 | 0.6 | 30.297 | 10.33 | 30.9 | -0.105 | 2 | 2.778% | -1.58 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.111 | 940 | 359.1 | 0 | 125.4 | 814.6 | 845.3 | 30.7 | -0.32 | 31.062 | 20.462 | 1.518 | 5.665% | 842.3 | -0.4 | 28.192 | 19.129 | 27.7 | -0.105 | 1.474 | 5.94% | -5.44 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.111 | 940 | 359.1 | 0 | 125.4 | 814.6 | 845.3 | 30.7 | -0.32 | 31.062 | 20.462 | 1.518 | 5.665% | 842.3 | -0.4 | 28.192 | 19.129 | 27.7 | -0.105 | 1.474 | 5.94% | -5.44 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.111 | 940 | 359.1 | 0 | 125.4 | 814.6 | 845.3 | 30.7 | -0.32 | 31.062 | 20.462 | 1.518 | 5.665% | 842.3 | -0.4 | 28.192 | 19.129 | 27.7 | -0.105 | 1.474 | 5.94% | -5.44 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.111 | 940 | 359.1 | 0 | 125.4 | 814.6 | 845.3 | 30.7 | -0.32 | 31.062 | 20.462 | 1.518 | 5.665% | 842.3 | -0.4 | 28.192 | 19.129 | 27.7 | -0.105 | 1.474 | 5.94% | -5.44 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.111 | 430 | 400 | 0 | 10.3 | 419.7 | 428.8 | 9.1 | -4.94 | 14.02 | 8.209 | 1.708 | 8.745% | 428.7 | -6.9 | 15.834 | 7.675 | 9 | -0.105 | 2 | 8.364% | -8.62 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.111 | 78 | 55 | 0 | 20 | 58 | 60.6 | 2.6 | 0.04 | 2.612 | 2.094 | 1.248 | 5.561% | 60.3 | 0.1 | 2.261 | 1.943 | 2.3 | -0.105 | 1.164 | 5.947% | -4.65 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.111 | 78 | 55 | 0 | 19.6 | 58.4 | 61.2 | 2.8 | -0.27 | 3.064 | 2.094 | 1.463 | 5.164% | 60.9 | -0.4 | 2.924 | 1.943 | 2.5 | -0.105 | 1.505 | 5.471% | -4.31 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.111 | 664 | 445 | 0 | 162.3 | 501.7 | 523.1 | 21.4 | -0.36 | 21.804 | 15.894 | 1.372 | 5.742% | 522 | -0.5 | 20.792 | 14.858 | 20.3 | -0.105 | 1.399 | 5.726% | -4.57 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.111 | 663 | 156 | 0 | 179.7 | 483.3 | 502 | 18.7 | 1.11 | 17.587 | 16.064 | 1.095 | 6.561% | 501.8 | 1.5 | 16.95 | 15.017 | 18.5 | -0.105 | 1.129 | 6.273% | -4.83 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.111 | 577 | 156 | 0 | 68.1 | 508.9 | 525.9 | 17 | -0.4 | 17.349 | 13.26 | 1.308 | 6.281% | 527 | -0.6 | 18.625 | 12.396 | 18.1 | -0.105 | 1.503 | 5.58% | -5.2 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.111 | 600 | 156 | 0 | 84.3 | 515.7 | 528.9 | 13.2 | -0.45 | 13.63 | 13.832 | 0.985 | 8.411% | 529.3 | -0.6 | 14.258 | 12.931 | 13.6 | -0.105 | 1.103 | 7.723% | -7.01 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.111 | 703 | 312 | 70 | 40 | 593 | 616.8 | 23.8 | -0.6 | 24.424 | 14.437 | 1.692 | 5.466% | 618.9 | -0.8 | 26.789 | 13.477 | 25.9 | -0.105 | 1.988 | 4.751% | -4.23 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.111 | 701 | 300 | 40 | 207.5 | 453.5 | 484.4 | 30.9 | 1.73 | 29.223 | 15.076 | 1.938 | 4.198% | 478.4 | 2.4 | 22.503 | 14.074 | 24.9 | -0.105 | 1.599 | 4.928% | -3.37 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 459 | 300 | 0 | 39 | 420 | 429 | 9 | -0.73 | 9.73 | 5.371 | 1.812 | 6.803% | 429.4 | -1 | 10.438 | 5.01 | 9.4 | -0.077 | 2 | 6.27% | -5.95 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 633 | 438 | 0 | 99.9 | 533.1 | 547.9 | 14.8 | -1.65 | 16.376 | 7.407 | 2 | 5.705% | 550.1 | -2.3 | 19.263 | 6.909 | 17 | -0.077 | 2 | 4.78% | -4.18 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.08 | 560 | 135 | 0 | 421.7 | 138.3 | 143.1 | 4.8 | 0.27 | 4.552 | 6.477 | 0.703 | 15.56% | 144.4 | 0.4 | 5.747 | 6.054 | 6.1 | -0.077 | 0.949 | 11.79% | -3.02 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 679 | 501 | 32 | 86.3 | 560.7 | 572.5 | 11.8 | 0.51 | 11.267 | 7.571 | 1.488 | 7.675% | 574.4 | 0.7 | 13.027 | 7.062 | 13.7 | -0.077 | 1.845 | 6.363% | -5.45 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 331 | 144 | 11 | 50.3 | 269.7 | 275.8 | 6.1 | -0.42 | 6.567 | 3.744 | 1.754 | 7.24% | 276.8 | -0.6 | 7.692 | 3.493 | 7.1 | -0.077 | 2 | 5.987% | -5.06 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.08 | 588 | 148.6 | 0 | 21.8 | 566.2 | 579.5 | 13.3 | -1.27 | 14.582 | 6.352 | 2 | 5.897% | 577.4 | -1.8 | 12.972 | 5.938 | 11.2 | -0.077 | 2 | 6.74% | -6.74 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 588 | 148.6 | 0 | 21.8 | 566.2 | 579.5 | 13.3 | -1.27 | 14.582 | 6.352 | 2 | 5.897% | 577.4 | -1.8 | 12.972 | 5.938 | 11.2 | -0.077 | 2 | 6.74% | -6.74 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 414.1 | 180.3 | 0 | 42.1 | 372 | 377.8 | 5.8 | -2.68 | 8.555 | 6.386 | 1.34 | 9.524% | 377.4 | -3.7 | 9.193 | 5.969 | 5.4 | -0.077 | 1.54 | 9.847% | -9.18 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 247 | 173 | 18 | 10.6 | 218.4 | 219.5 | 1.1 | 0.96 | 0.122 | 2.68 | 0.046 | 29.97% | 220 | 1.3 | 0.274 | 2.499 | 1.6 | -0.077 | 0.11 | 19.83% | -18.18 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.08 | 232 | 150 | 12 | 41.5 | 178.5 | 182.8 | 4.3 | -1.06 | 5.36 | 2.897 | 1.85 | 7.2% | 182.5 | -1.5 | 5.463 | 2.708 | 4 | -0.077 | 2 | 7.45% | -5.94 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 215.8 | 0 | 40 | 44.6 | 131.2 | 136 | 4.8 | 1.39 | 3.411 | 2.057 | 1.658 | 6% | 132.3 | 1.9 | -0.881 | 1.919 | 1.1 | -0.077 | 0 | 25.2% | -15.88 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 608 | 305 | 111 | 116.5 | 380.5 | 387.7 | 7.2 | -0.22 | 7.415 | 5.815 | 1.275 | 11.26% | 390.1 | -0.3 | 9.969 | 5.424 | 9.6 | -0.077 | 1.838 | 8.131% | -5.28 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 612 | 305 | 111 | 146 | 355 | 362 | 7 | -2.51 | 9.514 | 5.862 | 1.623 | 11.66% | 360.1 | -3.5 | 8.607 | 5.468 | 5.1 | -0.077 | 1.574 | 15.41% | -9.28 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.08 | 114 | 66 | 0 | 23.3 | 90.7 | 95 | 4.3 | -0.47 | 4.854 | 1.572 | 2 | 3.541% | 94.5 | -0.6 | 4.53 | 1.458 | 3.8 | -0.077 | 2 | 3.857% | -3.18 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 544 | 355 | 0 | 32.5 | 511.5 | 518 | 6.5 | -1.12 | 7.653 | 6.365 | 1.202 | 11.16% | 520.2 | -1.6 | 10.267 | 5.937 | 8.7 | -0.077 | 1.729 | 8.028% | -7.84 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 540 | 305 | 27 | 24.3 | 488.7 | 497.3 | 8.6 | -2.05 | 10.654 | 6.002 | 1.775 | 8.375% | 496.2 | -2.9 | 10.443 | 5.599 | 7.5 | -0.077 | 1.865 | 9.244% | -8.68 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 540 | 305.3 | 25 | 27 | 488 | 496.8 | 8.8 | -2.36 | 11.204 | 6.026 | 1.859 | 8.185% | 495.6 | -3.3 | 10.853 | 5.621 | 7.6 | -0.077 | 1.931 | 9.122% | -8.56 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | GT | -0.08 | 242 | 150 | 12 | 62.8 | 167.2 | 171 | 3.8 | -0.9 | 4.717 | 2.576 | 1.831 | 8.499% | 172.9 | -1.2 | 6.956 | 2.408 | 5.7 | -0.077 | 2 | 5.454% | -3.91 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.08 | 243 | 150 | 12 | 63.7 | 167.3 | 171.2 | 3.9 | -0.87 | 4.781 | 2.588 | 1.847 | 8.315% | 173.1 | -1.2 | 7.053 | 2.419 | 5.8 | -0.077 | 2 | 5.382% | -3.84 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.08 | 800 | 300 | 0 | 451.1 | 348.9 | 360 | 11.1 | -2.04 | 13.131 | 12.336 | 1.064 | 9.612% | 360.2 | -2.8 | 14.048 | 11.532 | 11.3 | -0.077 | 1.218 | 9.088% | -4.11 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.08 | 725 | 300 | 0 | 372.5 | 352.5 | 364.3 | 11.8 | 1.15 | 10.642 | 11.18 | 0.952 | 8.194% | 362.6 | 1.6 | 8.464 | 10.451 | 10.1 | -0.077 | 0.81 | 9.215% | -4.65 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.08 | 805 | 300 | 0 | 457.6 | 347.4 | 357.3 | 9.9 | -1.49 | 11.308 | 12.414 | 0.911 | 10.84% | 356.1 | -2.1 | 10.762 | 11.604 | 8.7 | -0.077 | 0.927 | 11.88% | -5.32 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.08 | 510 | 210 | 0 | 296 | 214 | 217.6 | 3.6 | 0.56 | 3.016 | 7.865 | 0.384 | 18.9% | 214.9 | 0.8 | 0.116 | 7.352 | 0.9 | -0.077 | 0.016 | 72.75% | -31.67 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.08 | 740 | 300 | 0 | 177.4 | 562.6 | 568.8 | 6.2 | -1.26 | 7.473 | 11.411 | 0.655 | 15.92% | 569.9 | -1.8 | 8.997 | 10.667 | 7.3 | -0.077 | 0.843 | 13.01% | -10.27 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 759.5 | 467.1 | 90 | 152.7 | 516.8 | 530.9 | 14.1 | -1.06 | 15.186 | 7.834 | 1.938 | 7.184% | 531.7 | -1.5 | 16.392 | 7.307 | 14.9 | -0.077 | 2 | 6.543% | -4.62 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 516.4 | 230 | 0 | 275.7 | 240.7 | 249.6 | 8.9 | -1.53 | 10.348 | 6.042 | 1.713 | 7.74% | 250.1 | -2.1 | 11.499 | 5.636 | 9.4 | -0.077 | 2 | 7.053% | -3.41 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 231.2 | 126 | 0 | 48.1 | 183.1 | 186.1 | 3 | -1.37 | 4.402 | 2.705 | 1.628 | 10.29% | 186 | -1.9 | 4.783 | 2.523 | 2.9 | -0.077 | 1.896 | 10.24% | -8.41 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.08 | 940 | 359.1 | 0 | 78 | 862 | 868.9 | 6.9 | 2.68 | 4.243 | 10.493 | 0.404 | 18.17% | 865.8 | 3.7 | 0.061 | 9.809 | 3.8 | -0.077 | 0.006 | 31.75% | -30.24 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 940 | 359.1 | 0 | 78 | 862 | 868.9 | 6.9 | 2.68 | 4.243 | 10.493 | 0.404 | 18.17% | 865.8 | 3.7 | 0.061 | 9.809 | 3.8 | -0.077 | 0.006 | 31.75% | -30.24 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 940 | 359.1 | 0 | 78 | 862 | 868.9 | 6.9 | 2.68 | 4.243 | 10.493 | 0.404 | 18.17% | 865.8 | 3.7 | 0.061 | 9.809 | 3.8 | -0.077 | 0.006 | 31.75% | -30.24 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 940 | 359.1 | 0 | 78 | 862 | 868.9 | 6.9 | 2.68 | 4.243 | 10.493 | 0.404 | 18.17% | 865.8 | 3.7 | 0.061 | 9.809 | 3.8 | -0.077 | 0.006 | 31.75% | -30.24 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.08 | 80 | 56 | 0 | 22.2 | 57.8 | 59.7 | 1.9 | -0.64 | 2.464 | 1.103 | 2 | 5.629% | 59.7 | -0.9 | 2.806 | 1.023 | 1.9 | -0.077 | 2 | 5.418% | -4.04 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.08 | 80 | 56 | 0 | 21.6 | 58.4 | 60.3 | 1.9 | -0.54 | 2.4 | 1.103 | 2 | 5.629% | 60.2 | -0.7 | 2.524 | 1.023 | 1.8 | -0.077 | 2 | 5.719% | -4.31 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.08 | 663 | 370 | 0 | 213.5 | 449.5 | 460.9 | 11.4 | -1.95 | 13.376 | 8.479 | 1.578 | 7.757% | 460.3 | -2.7 | 13.534 | 7.926 | 10.8 | -0.077 | 1.708 | 7.881% | -5.55 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.08 | 577 | 310 | 0 | 106.3 | 470.7 | 477.5 | 6.8 | -2 | 8.787 | 7.057 | 1.245 | 11.32% | 477.2 | -2.8 | 9.234 | 6.596 | 6.5 | -0.077 | 1.4 | 11.4% | -9.65 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.1 | 263.3 | 140 | 6 | 93.7 | 163.6 | 172.2 | 8.6 | 1.89 | 6.665 | 4.856 | 1.372 | 5.106% | 175.5 | 2.6 | 9.26 | 4.399 | 11.9 | -0.094 | 2 | 3.469% | -2.29 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.1 | 214 | 158 | 0 | 55.3 | 158.7 | 171.3 | 12.6 | -1.07 | 13.653 | 4.039 | 2 | 2.833% | 171.9 | -1.5 | 14.646 | 3.659 | 13.2 | -0.094 | 2 | 2.542% | -2 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.1 | 186 | 128 | 6.5 | 43.4 | 136.1 | 138.6 | 2.5 | 0.06 | 2.516 | 3.388 | 0.743 | 12.41% | 139.6 | 0.1 | 3.468 | 3.069 | 3.5 | -0.094 | 1.13 | 8.334% | -6.47 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.1 | 785 | 600 | 0 | 21.5 | 763.5 | 767.4 | 3.9 | 2.13 | 1.818 | 19.232 | 0.095 | 33.55% | 771.1 | 3 | 4.651 | 17.465 | 7.6 | -0.094 | 0.266 | 16.19% | -16.74 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.1 | 420 | 200 | 0 | 202.1 | 217.9 | 222.9 | 5 | -2.84 | 7.8 | 7.363 | 1.059 | 14.01% | 236.7 | -4 | 22.768 | 6.686 | 18.8 | -0.094 | 2 | 3.502% | -1.93 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.1 | 415 | 180 | 0 | 217.2 | 197.8 | 207.4 | 9.6 | -3.16 | 12.779 | 7.133 | 1.792 | 7.208% | 205.6 | -4.4 | 12.235 | 6.477 | 7.8 | -0.094 | 1.889 | 8.339% | -4.22 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.1 | 651 | 487 | 38 | 83.1 | 529.9 | 550.5 | 20.6 | 1.94 | 18.73 | 11.57 | 1.619 | 5.268% | 552.4 | 2.7 | 19.829 | 10.48 | 22.5 | -0.094 | 1.892 | 4.534% | -3.92 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.1 | 758 | 443 | 79 | 87.1 | 591.9 | 594.1 | 2.2 | 0.59 | 1.679 | 12.816 | 0.131 | 57.44% | 595.1 | 0.8 | 2.408 | 11.608 | 3.2 | -0.094 | 0.207 | 37.12% | -30.82 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.1 | 346 | 150 | 11 | 142.2 | 192.8 | 203.1 | 10.3 | -1.2 | 11.46 | 6.323 | 1.812 | 5.601% | 204.8 | -1.7 | 13.64 | 5.727 | 12 | -0.094 | 2 | 4.52% | -2.68 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.1 | 536.7 | 353.5 | 0 | 72.5 | 464.2 | 476.4 | 12.2 | -0.63 | 12.786 | 10.129 | 1.262 | 7.334% | 480.6 | -0.9 | 17.3 | 9.175 | 16.4 | -0.094 | 1.886 | 5.129% | -4.72 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.1 | 593 | 150 | 0 | 29.3 | 563.7 | 580 | 16.3 | 0.21 | 16.164 | 10.262 | 1.575 | 6.065% | 577.3 | 0.3 | 13.314 | 9.318 | 13.6 | -0.094 | 1.429 | 6.833% | -6.91 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.1 | 593 | 150 | 0 | 29.3 | 563.7 | 580 | 16.3 | 0.21 | 16.164 | 10.262 | 1.575 | 6.065% | 577.3 | 0.3 | 13.314 | 9.318 | 13.6 | -0.094 | 1.429 | 6.833% | -6.91 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.1 | 594 | 149.6 | 0 | 28.4 | 565.6 | 585.6 | 20 | 0.21 | 19.827 | 10.244 | 1.936 | 4.951% | 583.2 | 0.3 | 17.351 | 9.302 | 17.6 | -0.094 | 1.865 | 5.289% | -5.35 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.1 | 594 | 149.6 | 0 | 28.4 | 565.6 | 585.6 | 20 | 0.21 | 19.827 | 10.244 | 1.936 | 4.951% | 583.2 | 0.3 | 17.351 | 9.302 | 17.6 | -0.094 | 1.865 | 5.289% | -5.35 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.1 | 959.1 | 461 | 147.5 | 32.2 | 779.4 | 803.4 | 24 | -1.18 | 25.25 | 15.318 | 1.648 | 6.662% | 805.1 | -1.6 | 27.405 | 13.875 | 25.7 | -0.094 | 1.975 | 5.848% | -5.05 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.1 | 415.1 | 225 | 113.3 | 75.4 | 226.4 | 232.2 | 5.8 | 0.6 | 5.163 | 5.696 | 0.907 | 11.93% | 235.5 | 0.8 | 8.285 | 5.159 | 9.1 | -0.094 | 1.606 | 7.15% | -4.14 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.1 | 470 | 180 | 0 | 289 | 181 | 185.1 | 4.1 | -0.18 | 4.299 | 5.726 | 0.751 | 19.12% | 184.3 | -0.2 | 3.483 | 5.042 | 3.3 | -0.094 | 0.691 | 22.33% | -9.12 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.1 | 470 | 180 | 0 | 289 | 181 | 185.1 | 4.1 | -0.18 | 4.299 | 5.726 | 0.751 | 19.12% | 184.3 | -0.2 | 3.483 | 5.042 | 3.3 | -0.094 | 0.691 | 22.33% | -9.12 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.1 | 470 | 180 | 0 | 289 | 181 | 185.1 | 4.1 | -0.18 | 4.299 | 5.726 | 0.751 | 19.12% | 184.3 | -0.2 | 3.483 | 5.042 | 3.3 | -0.094 | 0.691 | 22.33% | -9.12 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.1 | 470 | 180 | 0 | 289 | 181 | 185.1 | 4.1 | -0.18 | 4.299 | 5.726 | 0.751 | 19.12% | 184.3 | -0.2 | 3.483 | 5.042 | 3.3 | -0.094 | 0.691 | 22.33% | -9.12 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.1 | 216 | 148.7 | 5 | 61 | 150 | 157.8 | 7.8 | -1 | 8.876 | 4.258 | 2 | 4.619% | 159.3 | -1.4 | 10.72 | 3.866 | 9.3 | -0.094 | 2 | 3.642% | -2.69 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.1 | 216 | 148.9 | 5 | 61.1 | 149.9 | 157.9 | 8 | -0.08 | 8.073 | 4.258 | 1.896 | 4.504% | 159.5 | -0.1 | 9.692 | 3.866 | 9.6 | -0.094 | 2 | 3.528% | -2.6 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.1 | 258.3 | 55.8 | 31.3 | 87.6 | 139.4 | 146.9 | 7.5 | -2.27 | 9.818 | 4.285 | 2 | 5.744% | 140.4 | -3.2 | 4.216 | 3.881 | 1 | -0.094 | 1.086 | 40.5% | -23.2 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.1 | 552.6 | 316 | 43.1 | 40.2 | 469.3 | 483.8 | 14.5 | 0.35 | 14.158 | 9.615 | 1.473 | 6.354% | 482.6 | 0.5 | 12.827 | 8.709 | 13.3 | -0.094 | 1.473 | 6.511% | -5.88 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.1 | 566.8 | 303.7 | 43 | 58 | 465.8 | 480.8 | 15 | 0.54 | 14.408 | 9.886 | 1.457 | 6.3% | 478.7 | 0.8 | 12.125 | 8.955 | 12.9 | -0.094 | 1.354 | 6.886% | -6.02 | 0.017 | 0.058 | 5.933% | 5.163%
Wind | WND | WIND | -0.1 | 193.7 | 0 | 0 | 23.4 | 170.3 | 175.6 | 5.3 | -0.19 | 5.486 | 4.792 | 1.145 | 6.097% | 175 | -0.3 | 4.973 | 4.351 | 4.7 | -0.094 | 1.143 | 6.463% | -6.03 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | GT | -0.1 | 234 | 150 | 12 | 71.5 | 150.5 | 157.2 | 6.7 | -0.08 | 6.748 | 4.011 | 1.683 | 5.825% | 159 | -0.1 | 8.573 | 3.642 | 8.5 | -0.094 | 2 | 4.316% | -2.95 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.1 | 251 | 160 | 12 | 78 | 161 | 168.2 | 7.2 | 0.29 | 6.881 | 4.264 | 1.614 | 5.814% | 169.9 | 0.4 | 8.533 | 3.872 | 8.9 | -0.094 | 2 | 4.422% | -3.01 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.1 | 259 | 151 | 28.1 | 71.5 | 159.4 | 163.5 | 4.1 | -0.69 | 4.79 | 4.357 | 1.099 | 10.54% | 167.9 | -1 | 9.454 | 3.947 | 8.5 | -0.094 | 2 | 4.777% | -3.12 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.1 | 258 | 166 | 28.1 | 57.7 | 172.2 | 177 | 4.8 | -1.33 | 6.195 | 4.339 | 1.428 | 8.964% | 181.5 | -1.8 | 11.215 | 3.93 | 9.3 | -0.094 | 2 | 4.349% | -3.08 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.1 | 650 | 189.6 | 0 | 260.4 | 389.6 | 405.3 | 15.7 | 1.08 | 14.622 | 9.813 | 1.49 | 6.902% | 405.7 | 1.5 | 14.575 | 8.911 | 16.1 | -0.094 | 1.636 | 6.327% | -4.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.1 | 650 | 189.6 | 0 | 260.4 | 389.6 | 405.3 | 15.7 | 1.08 | 14.622 | 9.813 | 1.49 | 6.902% | 405.7 | 1.5 | 14.575 | 8.911 | 16.1 | -0.094 | 1.636 | 6.327% | -4.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.1 | 650 | 189.6 | 0 | 260.4 | 389.6 | 405.3 | 15.7 | 1.08 | 14.622 | 9.813 | 1.49 | 6.902% | 405.7 | 1.5 | 14.575 | 8.911 | 16.1 | -0.094 | 1.636 | 6.327% | -4.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.1 | 650 | 189.6 | 0 | 260.4 | 389.6 | 405.3 | 15.7 | 1.08 | 14.622 | 9.813 | 1.49 | 6.902% | 405.7 | 1.5 | 14.575 | 8.911 | 16.1 | -0.094 | 1.636 | 6.327% | -4.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.1 | 650 | 189.6 | 0 | 260.4 | 389.6 | 405.3 | 15.7 | 1.08 | 14.622 | 9.813 | 1.49 | 6.902% | 405.7 | 1.5 | 14.575 | 8.911 | 16.1 | -0.094 | 1.636 | 6.327% | -4.03 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.1 | 414.5 | 190 | 36.8 | 180.2 | 197.5 | 212 | 14.5 | 0.41 | 14.022 | 7.129 | 1.967 | 4.766% | 213.5 | 0.6 | 15.404 | 6.457 | 16 | -0.094 | 2 | 4.06% | -2.06 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.1 | 380 | 221 | 0 | 19.7 | 360.3 | 369.8 | 9.5 | -0.12 | 9.549 | 9.096 | 1.05 | 6.67% | 371.4 | -0.2 | 11.214 | 8.26 | 11.1 | -0.094 | 1.358 | 5.366% | -5.41 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.1 | 940 | 360 | 0 | 41.7 | 898.3 | 910.5 | 12.2 | 0.64 | 11.524 | 16.523 | 0.697 | 12.84% | 909.2 | 0.9 | 9.969 | 15.004 | 10.9 | -0.094 | 0.664 | 13.51% | -13.73 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.1 | 940 | 360 | 0 | 41.7 | 898.3 | 910.5 | 12.2 | 0.64 | 11.524 | 16.523 | 0.697 | 12.84% | 909.2 | 0.9 | 9.969 | 15.004 | 10.9 | -0.094 | 0.664 | 13.51% | -13.73 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.1 | 940 | 360 | 0 | 41.7 | 898.3 | 910.5 | 12.2 | 0.64 | 11.524 | 16.523 | 0.697 | 12.84% | 909.2 | 0.9 | 9.969 | 15.004 | 10.9 | -0.094 | 0.664 | 13.51% | -13.73 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.1 | 940 | 360 | 0 | 41.7 | 898.3 | 910.5 | 12.2 | 0.64 | 11.524 | 16.523 | 0.697 | 12.84% | 909.2 | 0.9 | 9.969 | 15.004 | 10.9 | -0.094 | 0.664 | 13.51% | -13.73 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.1 | 155 | 80 | 0 | 10.2 | 144.8 | 148.8 | 4 | 0.11 | 3.826 | 3.462 | 1.105 | 6.465% | 150.2 | 0.2 | 5.238 | 3.144 | 5.4 | -0.094 | 1.666 | 4.502% | -4.46 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.1 | 155 | 80 | 0 | 19.2 | 135.8 | 140.8 | 5 | 0.07 | 4.884 | 3.482 | 1.403 | 5.172% | 142.6 | 0.1 | 6.703 | 3.162 | 6.8 | -0.094 | 2 | 3.575% | -3.32 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.1 | 664 | 156 | 0 | 52.5 | 611.5 | 631 | 19.5 | 1.99 | 17.5 | 12.545 | 1.395 | 5.677% | 632.6 | 2.8 | 18.383 | 11.392 | 21.1 | -0.094 | 1.614 | 4.932% | -4.83 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.1 | 663 | 156 | 0 | 93.9 | 569.1 | 588.9 | 19.8 | 1.55 | 18.33 | 12.822 | 1.43 | 5.582% | 588.9 | 2.2 | 17.711 | 11.643 | 19.8 | -0.094 | 1.521 | 5.247% | -4.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.1 | 610 | 421 | 0 | 25.5 | 584.5 | 596.8 | 12.3 | 1.15 | 11.105 | 11.25 | 0.987 | 8.268% | 597.6 | 1.6 | 11.426 | 10.216 | 13.1 | -0.094 | 1.118 | 7.297% | -7.43 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.1 | 729 | 300 | 40 | 324.1 | 364.9 | 389.9 | 25 | 0.86 | 24.077 | 13.005 | 1.851 | 4.861% | 389 | 1.2 | 22.868 | 11.78 | 24.1 | -0.094 | 1.941 | 4.74% | -2.52 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 459 | 300 | 0 | 23.9 | 435.1 | 445.6 | 10.5 | 0.55 | 10.035 | 6.171 | 1.626 | 6.341% | 446.4 | 0.8 | 10.562 | 6.438 | 11.3 | -0.089 | 1.641 | 6.028% | -5.58 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 238 | 158 | 0 | 35.5 | 202.5 | 205.5 | 3 | 1.57 | 1.466 | 3.2 | 0.458 | 11.51% | 205 | 2.2 | 0.341 | 3.338 | 2.5 | -0.089 | 0.102 | 14.13% | -11.73 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 208 | 140 | 3 | 5.8 | 199.2 | 200.6 | 1.4 | 0.18 | 1.211 | 2.756 | 0.439 | 21.56% | 201.3 | 0.2 | 1.854 | 2.875 | 2.1 | -0.089 | 0.645 | 14.71% | -13.74 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.087 | 415 | 280 | 0 | 50.6 | 364.4 | 372.4 | 8 | 0.64 | 7.427 | 5.716 | 1.299 | 7.525% | 371.5 | 0.9 | 6.257 | 5.957 | 7.1 | -0.089 | 1.05 | 8.674% | -7.44 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.087 | 420 | 70 | 0 | 349.5 | 70.5 | 78.7 | 8.2 | -0.05 | 8.244 | 5.398 | 1.527 | 7.43% | 77.6 | -0.1 | 7.135 | 5.626 | 7.1 | -0.089 | 1.268 | 8.779% | -1.44 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.087 | 265.2 | 173 | 18 | 65.4 | 181.8 | 186.5 | 4.7 | 0 | 4.712 | 3.323 | 1.418 | 8.188% | 185.7 | 0 | 3.9 | 3.467 | 3.9 | -0.089 | 1.125 | 10.09% | -6.75 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 398 | 153 | 15 | 71.9 | 311.1 | 319.4 | 8.3 | -0.35 | 8.618 | 5.149 | 1.674 | 6.956% | 316.9 | -0.5 | 6.307 | 5.372 | 5.8 | -0.089 | 1.174 | 10.18% | -7.77 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.087 | 625 | 300 | 0 | 19.3 | 605.7 | 616.7 | 11 | -3.84 | 14.839 | 9.34 | 1.589 | 8.241% | 617.4 | -5.3 | 17.022 | 9.734 | 11.7 | -0.089 | 1.749 | 7.926% | -7.5 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.087 | 694 | 517 | 23 | 118.1 | 552.9 | 569.4 | 16.5 | -0.4 | 16.973 | 9.021 | 1.881 | 6.101% | 569.4 | -0.6 | 17.13 | 9.412 | 16.5 | -0.089 | 1.82 | 6.241% | -4.86 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 1304 | 619 | 46 | 142.9 | 1115.1 | 1118.4 | 3.3 | -0.06 | 3.439 | 16.913 | 0.203 | 57.31% | 1119.6 | -0.1 | 4.625 | 17.645 | 4.5 | -0.089 | 0.262 | 42.99% | -35.92 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 365 | 158 | 11 | 47.7 | 306.3 | 314.1 | 7.8 | -0.03 | 7.855 | 4.759 | 1.65 | 6.789% | 314.2 | 0 | 7.973 | 4.965 | 7.9 | -0.089 | 1.606 | 6.857% | -5.62 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 497 | 262 | 0 | 13.4 | 483.6 | 487.7 | 4.1 | -0.12 | 4.191 | 6.682 | 0.627 | 17.58% | 487.7 | -0.2 | 4.25 | 6.971 | 4.1 | -0.089 | 0.61 | 17.99% | -17.1 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 978.7 | 461 | 103 | 52.3 | 823.4 | 844.6 | 21.2 | 0.28 | 20.842 | 11.773 | 1.77 | 6.695% | 850.1 | 0.4 | 26.286 | 12.282 | 26.7 | -0.089 | 2 | 5.438% | -4.47 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 995.4 | 461 | 94 | 77.7 | 823.7 | 844.2 | 20.5 | 0.94 | 19.561 | 12.119 | 1.614 | 7.042% | 849.4 | 1.3 | 24.309 | 12.643 | 25.7 | -0.089 | 1.923 | 5.746% | -4.65 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 611 | 285 | 65 | 42.4 | 503.6 | 518.1 | 14.5 | 2.99 | 11.419 | 7.341 | 1.555 | 6.112% | 523.2 | 4.2 | 15.377 | 7.659 | 19.6 | -0.089 | 2 | 4.626% | -3.72 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.087 | 470 | 180 | 0 | 18.9 | 451.1 | 453 | 1.9 | 0.23 | 1.699 | 3.727 | 0.456 | 35.9% | 453.1 | 0.3 | 1.756 | 3.996 | 2 | -0.089 | 0.44 | 34.89% | -32.68 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.087 | 470 | 180 | 0 | 18.9 | 451.1 | 453 | 1.9 | 0.23 | 1.699 | 3.727 | 0.456 | 35.9% | 453.1 | 0.3 | 1.756 | 3.996 | 2 | -0.089 | 0.44 | 34.89% | -32.68 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.087 | 470 | 180 | 0 | 18.9 | 451.1 | 453 | 1.9 | 0.23 | 1.699 | 3.727 | 0.456 | 35.9% | 453.1 | 0.3 | 1.756 | 3.996 | 2 | -0.089 | 0.44 | 34.89% | -32.68 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.087 | 470 | 180 | 0 | 18.9 | 451.1 | 453 | 1.9 | 0.23 | 1.699 | 3.727 | 0.456 | 35.9% | 453.1 | 0.3 | 1.756 | 3.996 | 2 | -0.089 | 0.44 | 34.89% | -32.68 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | STM | -0.087 | 98.8 | 18.8 | 0 | 15.8 | 83 | 89.5 | 6.5 | 0.53 | 5.963 | 1.718 | 2 | 2.208% | 89.6 | 0.7 | 5.799 | 1.79 | 6.6 | -0.089 | 2 | 2.225% | -1.82 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.087 | 529 | 357 | 0 | 30.9 | 498.1 | 501.4 | 3.3 | -0.03 | 3.382 | 7.112 | 0.476 | 23.25% | 502 | 0 | 3.987 | 7.42 | 3.9 | -0.089 | 0.537 | 20.13% | -18.51 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 538 | 357 | 0 | 31.4 | 506.6 | 506.6 | 0 | -0.2 | 0.207 | 7.233 | 0.029 | 0% | 507.2 | -0.3 | 0.977 | 7.546 | 0.6 | -0.089 | 0.13 | 133.1% | -122.38 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.087 | 234 | 150 | 5 | 44.6 | 184.4 | 190.1 | 5.7 | 0.03 | 5.629 | 3.509 | 1.604 | 5.958% | 189.6 | 0 | 5.078 | 3.657 | 5.2 | -0.089 | 1.389 | 6.68% | -5.14 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.087 | 234 | 150 | 5 | 44.7 | 184.3 | 190.1 | 5.8 | -0.18 | 5.973 | 3.508 | 1.703 | 5.855% | 189.5 | -0.3 | 5.394 | 3.656 | 5.2 | -0.089 | 1.475 | 6.68% | -5.13 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 195.1 | 0 | 29 | 16.1 | 150 | 156.8 | 6.8 | 0.61 | 6.278 | 2.233 | 2 | 4.164% | 154.5 | 0.8 | 3.65 | 2.33 | 4.5 | -0.089 | 1.567 | 6.437% | -4.83 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 646 | 305 | 111 | 99.6 | 435.4 | 443.3 | 7.9 | -0.17 | 8.063 | 7.193 | 1.121 | 11.86% | 443.6 | -0.2 | 8.416 | 7.504 | 8.2 | -0.089 | 1.121 | 11.69% | -7.7 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 620 | 275 | 0 | 139.9 | 480.1 | 486.5 | 6.4 | -0.2 | 6.53 | 8.336 | 0.783 | 14.05% | 490.1 | -0.3 | 10.244 | 8.696 | 10 | -0.089 | 1.178 | 9.199% | -6.96 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 620 | 280 | 0 | 140.1 | 479.9 | 487.8 | 7.9 | -0.3 | 8.252 | 8.336 | 0.99 | 11.38% | 491.6 | -0.4 | 12.121 | 8.696 | 11.7 | -0.089 | 1.394 | 7.863% | -5.95 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 580 | 317 | 0 | 21 | 559 | 568.7 | 9.7 | 0.57 | 9.14 | 7.798 | 1.172 | 8.673% | 567.4 | 0.8 | 7.6 | 8.135 | 8.4 | -0.089 | 0.934 | 10.25% | -9.65 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 580 | 328.7 | 0 | 16.2 | 563.8 | 573.6 | 9.8 | 0.26 | 9.525 | 7.798 | 1.221 | 8.585% | 573 | 0.4 | 8.816 | 8.135 | 9.2 | -0.089 | 1.084 | 9.355% | -8.88 | 0.017 | 0.058 | 5.933% | 5.163%
Wind | WND | WIND | -0.087 | 185.9 | 0 | 0 | 35.5 | 150.4 | 154 | 3.6 | 0.1 | 3.557 | 3.275 | 1.086 | 7.496% | 154.2 | 0.1 | 3.698 | 3.413 | 3.8 | -0.089 | 1.083 | 7.264% | -5.73 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | GT | -0.087 | 235 | 150 | 12 | 44 | 179 | 184.2 | 5.2 | 0.12 | 5.104 | 2.949 | 1.731 | 6.558% | 183.9 | 0.2 | 4.768 | 3.073 | 4.9 | -0.089 | 1.551 | 7.12% | -5.29 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.087 | 237 | 150 | 12 | 45.1 | 179.9 | 185.1 | 5.2 | 0.08 | 5.089 | 2.982 | 1.706 | 6.614% | 184.9 | 0.1 | 4.895 | 3.108 | 5 | -0.089 | 1.575 | 7.037% | -5.21 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.087 | 208 | 40 | 0 | 153.7 | 54.3 | 54 | -0.3 | -4.27 | 3.936 | 3.534 | 1.114 | -100.6% | 54 | -5.9 | 5.679 | 3.683 | -0.3 | -0.089 | 1.542 | -102.9% | 26.15 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | WDS | STM | -0.087 | 105 | 70 | 0 | 34.6 | 70.4 | 71.5 | 1.1 | 0 | 1.18 | 1.663 | 0.71 | 13.87% | 71.4 | 0 | 1.043 | 1.741 | 1 | -0.089 | 0.599 | 15.6% | -10.18 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.087 | 753 | 479 | 7 | 56.6 | 689.4 | 700.8 | 11.4 | 1.95 | 9.432 | 10.03 | 0.94 | 9.58% | 707.7 | 2.7 | 15.619 | 10.464 | 18.3 | -0.089 | 1.493 | 6.105% | -5.46 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 748 | 514.7 | 16.9 | 92.6 | 638.5 | 656.7 | 18.2 | -2.77 | 21.003 | 9.829 | 2 | 5.961% | 663.8 | -3.9 | 29.202 | 10.255 | 25.3 | -0.089 | 2 | 4.387% | -3.66 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 751.4 | 510 | 42.4 | 161 | 548 | 560.5 | 12.5 | -4.9 | 17.367 | 9.532 | 1.822 | 8.719% | 570.9 | -6.8 | 29.671 | 9.945 | 22.9 | -0.089 | 2 | 4.868% | -3.47 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 550.5 | 230 | 0 | 55.6 | 494.9 | 504.5 | 9.6 | -0.41 | 9.984 | 7.401 | 1.349 | 8.318% | 505 | -0.6 | 10.689 | 7.721 | 10.1 | -0.089 | 1.384 | 8.088% | -7.1 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 247.9 | 118 | 0 | 52.9 | 195 | 199.5 | 4.5 | 0.19 | 4.301 | 3.332 | 1.291 | 7.994% | 200.4 | 0.3 | 5.188 | 3.477 | 5.4 | -0.089 | 1.492 | 6.815% | -5.23 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | NG | COGN | -0.087 | 87 | 65 | 0 | 21.8 | 65.2 | 67.5 | 2.3 | -0.04 | 2.315 | 1.378 | 1.681 | 5.497% | 67.2 | -0.1 | 2.002 | 1.442 | 2 | -0.089 | 1.388 | 6.467% | -4.71 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 276 | 100 | 20 | 50.1 | 205.9 | 203 | -2.9 | -3.45 | 0.594 | 3.442 | 0.172 | -13.81% | 202.8 | -4.8 | 1.723 | 3.591 | -3.1 | -0.089 | 0.48 | -13.22% | 9.62 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 895 | 480 | 0 | 129.7 | 765.3 | 771.9 | 6.6 | 2.68 | 3.851 | 12.033 | 0.32 | 19.67% | 770.5 | 3.7 | 1.473 | 12.554 | 5.2 | -0.089 | 0.117 | 25.54% | -21.33 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 263.5 | 130 | 0 | 49.3 | 214.2 | 219.4 | 5.2 | -0.14 | 5.257 | 3.543 | 1.484 | 7.353% | 217.9 | -0.2 | 3.828 | 3.696 | 3.7 | -0.089 | 1.036 | 10.57% | -8.39 | 0.017 | 0.058 | 5.933% | 5.163%
Wind | WND | WIND | -0.087 | 27 | 0 | 0 | 7.2 | 19.8 | 19.7 | -0.1 | -0.18 | 0.121 | 0.476 | 0.254 | -39.43% | 19.5 | -0.3 | -0.073 | 0.496 | -0.3 | -0.089 | 0 | -13.44% | 9.48 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.087 | 215 | 175 | 0 | 39.1 | 175.9 | 183.9 | 8 | -0.15 | 8.138 | 2.891 | 2 | 3.9% | 183.7 | -0.2 | 7.978 | 3.016 | 7.8 | -0.089 | 2 | 4.092% | -3.27 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 735 | 300 | 40 | 184.4 | 510.6 | 517.1 | 6.5 | -6.92 | 13.418 | 9.345 | 1.436 | 16.4% | 516.5 | -9.6 | 15.484 | 9.749 | 5.9 | -0.089 | 1.588 | 18.48% | -12.54 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.038 | 591 | 220 | 0 | 367.4 | 223.6 | 230.3 | 6.7 | -0.26 | 6.99 | 7.605 | 0.919 | 5.591% | 229.1 | -0.4 | 5.81 | 6.156 | 5.5 | -0.031 | 0.944 | 5.557% | -2.57 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.038 | 548 | 345 | 49 | 154 | 345 | 353.3 | 8.3 | -0.18 | 8.486 | 4.72 | 1.798 | 4.185% | 354.2 | -0.2 | 9.418 | 3.763 | 9.2 | -0.031 | 2 | 3.081% | -2.37 | 0.017 | 0.058 | 5.933% | 5.163%
Wind | WND | WIND | -0.038 | 135.4 | 0 | 0 | 126.5 | 8.9 | 9 | 0.1 | 0 | 0.078 | 1.742 | 0.045 | 86.04% | 9 | 0 | 0.071 | 1.41 | 0.1 | -0.031 | 0.051 | 70.24% | -5.35 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.038 | 245 | 76 | 0 | 97.7 | 147.3 | 159.3 | 12 | -4.25 | 16.314 | 2.317 | 2 | 1.295% | 159.3 | -5.9 | 17.94 | 1.848 | 12 | -0.031 | 2 | 1.057% | -0.78 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 192 | 133 | 1 | 34.7 | 156.3 | 160.7 | 4.4 | 2.24 | 2.18 | 1.807 | 1.207 | 2.77% | 160.9 | 3.1 | 1.509 | 1.44 | 4.6 | -0.031 | 1.047 | 2.163% | -2.15 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.038 | 560 | 135 | 0 | 302.7 | 257.3 | 254.2 | -3.1 | -4.24 | 1.143 | 5.405 | 0.212 | -11.45% | 252.5 | -5.9 | 1.096 | 4.375 | -4.8 | -0.031 | 0.25 | -6.034% | 3.39 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 420 | 125 | 0 | 273.9 | 146.1 | 151.4 | 5.3 | 2.24 | 3.079 | 3.746 | 0.822 | 5.024% | 172.9 | 3.1 | 23.626 | 3.033 | 26.8 | -0.031 | 2 | 0.8108% | -0.34 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 415 | 125 | 0 | 268.7 | 146.3 | 158.1 | 11.8 | 3.77 | 8.072 | 3.688 | 2 | 2.23% | 159.3 | 5.2 | 7.768 | 2.986 | 13 | -0.031 | 2 | 1.652% | -0.71 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.038 | 251.6 | 160 | 18 | 69 | 164.6 | 169.5 | 4.9 | 1.24 | 3.673 | 2.209 | 1.663 | 3.258% | 168.7 | 1.7 | 2.376 | 1.762 | 4.1 | -0.031 | 1.349 | 3.177% | -2.54 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 162 | 18 | 63 | 23.4 | 75.6 | 79.1 | 3.5 | -2.18 | 5.722 | 0.936 | 2 | 2.94% | 78.7 | -3 | 6.152 | 0.747 | 3.1 | -0.031 | 2 | 2.709% | -1.54 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.038 | 640 | 300 | 0 | 179.5 | 460.5 | 474.6 | 14.1 | 0 | 14.125 | 7.223 | 1.955 | 2.877% | 468.9 | 0 | 8.4 | 5.848 | 8.4 | -0.031 | 1.437 | 3.94% | -3.47 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.038 | 678 | 495 | 40 | 120 | 518 | 535 | 17 | 0.58 | 16.444 | 6.034 | 2 | 2.528% | 531.5 | 0.8 | 12.704 | 4.811 | 13.5 | -0.031 | 2 | 2.597% | -2.43 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 544 | 337.3 | 0 | 189.2 | 354.8 | 366.1 | 11.3 | -0.36 | 11.578 | 5.145 | 2 | 3.051% | 364.6 | -0.5 | 10.212 | 4.102 | 9.8 | -0.031 | 2 | 2.871% | -2.29 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.038 | 600.2 | 158.7 | 0 | 417.7 | 182.5 | 198.1 | 15.6 | 0.96 | 14.636 | 5.368 | 2 | 2.439% | 197.3 | 1.3 | 13.469 | 4.346 | 14.8 | -0.031 | 2 | 2.097% | -0.78 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 600.2 | 158.7 | 0 | 417.7 | 182.5 | 198.1 | 15.6 | 0.96 | 14.636 | 5.368 | 2 | 2.439% | 197.3 | 1.3 | 13.469 | 4.346 | 14.8 | -0.031 | 2 | 2.097% | -0.78 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 588.2 | 158.2 | 0 | 411.8 | 176.4 | 191.6 | 15.2 | 1.7 | 13.488 | 5.28 | 2 | 2.453% | 190.8 | 2.4 | 11.997 | 4.274 | 14.4 | -0.031 | 2 | 2.112% | -0.77 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 588.2 | 158.2 | 0 | 411.8 | 176.4 | 191.6 | 15.2 | 1.7 | 13.488 | 5.28 | 2 | 2.453% | 190.8 | 2.4 | 11.997 | 4.274 | 14.4 | -0.031 | 2 | 2.112% | -0.77 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 423.8 | 180.3 | 0 | 233.6 | 190.2 | 198.8 | 8.6 | -0.24 | 8.823 | 4.703 | 1.876 | 3.124% | 197.5 | -0.3 | 7.588 | 3.807 | 7.3 | -0.031 | 1.993 | 3.003% | -1.65 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.038 | 946 | 461 | 158.6 | 66 | 721.4 | 740.2 | 18.8 | -2.62 | 21.489 | 7.447 | 2 | 3.188% | 741.4 | -3.6 | 23.64 | 5.938 | 20 | -0.031 | 2 | 2.445% | -2.28 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 294.1 | 175 | 44.9 | 73.5 | 175.7 | 179.3 | 3.6 | 0 | 3.545 | 2.357 | 1.504 | 5.182% | 178.8 | 0 | 3.039 | 1.879 | 3.1 | -0.031 | 1.617 | 4.911% | -3.58 | 0.017 | 0.058 | 5.933% | 5.163%
Wind | WND | WIND | -0.038 | 137 | 0 | 0 | 97.1 | 39.9 | 129.2 | 89.3 | -4.19 | 93.452 | 1.763 | 2 | 0.09748% | 148.7 | -5.8 | 114.629 | 1.427 | 108.8 | -0.031 | 2 | 0.06532% | -0.02 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | COGN | -0.038 | 224 | 150 | 5 | 60.7 | 158.3 | 164.1 | 5.8 | 1.75 | 4.062 | 2.299 | 1.767 | 2.451% | 166.3 | 2.4 | 5.589 | 1.861 | 8 | -0.031 | 2 | 1.45% | -1.25 | 0.017 | 0.05 | 5.933% | 5.163%
Wind | WND | WIND | -0.038 | 163.5 | 0 | 0 | 124.3 | 39.2 | 41.7 | 2.5 | 0.35 | 2.182 | 2.104 | 1.037 | 4.153% | 39.5 | 0.5 | -0.131 | 1.703 | 0.3 | -0.031 | 0 | 28.25% | -8.18 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.038 | 167.7 | 0 | 30.9 | 103.8 | 33 | 48.7 | 15.7 | 0.95 | 14.739 | 1.294 | 2 | 0.6783% | 54.3 | 1.3 | 19.99 | 1.032 | 21.3 | -0.031 | 2 | 0.4081% | -0.1 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.038 | 842 | 307 | 0 | 528.6 | 313.4 | 335.9 | 22.5 | 0.28 | 22.275 | 8.854 | 2 | 2.371% | 337 | 0.4 | 23.259 | 7.168 | 23.6 | -0.031 | 2 | 1.845% | -0.84 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.038 | 529.3 | 310 | 53.4 | 57 | 418.9 | 424.4 | 5.5 | -1.56 | 7.14 | 4.501 | 1.586 | 6.1% | 423.2 | -2.2 | 6.545 | 3.589 | 4.3 | -0.031 | 1.823 | 6.366% | -6.16 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 528.2 | 310.3 | 43.2 | 65.5 | 419.5 | 426 | 6.5 | -0.54 | 6.991 | 4.587 | 1.524 | 5.151% | 426.4 | -0.8 | 7.578 | 3.658 | 6.9 | -0.031 | 2 | 3.959% | -3.85 | 0.017 | 0.058 | 5.933% | 5.163%
Wind | WND | WIND | -0.038 | 190.4 | 0 | 0 | 15.7 | 174.7 | 177.6 | 2.9 | 0.14 | 2.813 | 2.45 | 1.148 | 4.168% | 177.4 | 0.2 | 2.548 | 1.983 | 2.7 | -0.031 | 1.285 | 3.654% | -4.09 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | LIG | FOSS | -0.038 | 770 | 300 | 0 | 468.7 | 301.3 | 310.5 | 9.2 | 0.42 | 8.831 | 9.908 | 0.891 | 5.304% | 307.3 | 0.6 | 5.445 | 8.021 | 6 | -0.031 | 0.679 | 6.635% | -3.18 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.038 | 810 | 300 | 0 | 499.6 | 310.4 | 319.7 | 9.3 | -0.03 | 9.305 | 10.423 | 0.893 | 5.519% | 317.9 | 0 | 7.507 | 8.438 | 7.5 | -0.031 | 0.89 | 5.584% | -2.62 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.038 | 523 | 210 | 0 | 308.2 | 214.8 | 216 | 1.2 | 0.56 | 0.658 | 6.73 | 0.098 | 27.63% | 214.2 | 0.8 | -1.401 | 5.448 | -0.6 | -0.031 | 0 | -45.08% | 22.63 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.038 | 760 | 300 | 0 | 356.5 | 403.5 | 414.9 | 11.4 | 2.89 | 8.569 | 9.78 | 0.876 | 4.225% | 414.8 | 4 | 7.268 | 7.917 | 11.3 | -0.031 | 0.918 | 3.477% | -2.26 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.038 | 250 | 161 | 28 | 50 | 172 | 176.6 | 4.6 | 1.7 | 2.89 | 2.1 | 1.376 | 3.448% | 180.9 | 2.4 | 6.509 | 1.674 | 8.9 | -0.031 | 2 | 1.454% | -1.22 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 522.1 | 230 | 2.9 | 237.6 | 281.6 | 309.4 | 27.8 | 13.22 | 14.589 | 4.911 | 2 | 1.19% | 323.7 | 18.4 | 23.752 | 3.915 | 42.1 | -0.031 | 2 | 0.6414% | -0.42 | 0.017 | 0.058 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.038 | 380 | 222 | 0 | 137.4 | 242.6 | 247.5 | 4.9 | -1.95 | 6.94 | 4.732 | 1.467 | 4.917% | 246.2 | -2.7 | 6.352 | 3.831 | 3.6 | -0.031 | 1.658 | 5.462% | -4.26 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 940 | 360 | 0 | 510.5 | 429.5 | 449.4 | 19.9 | 0.1 | 19.792 | 5.814 | 2 | 2.993% | 449.4 | 0.1 | 19.771 | 4.707 | 19.9 | -0.031 | 2 | 2.442% | -1.37 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 940 | 360 | 0 | 510.5 | 429.5 | 449.4 | 19.9 | 0.1 | 19.792 | 5.814 | 2 | 2.993% | 449.4 | 0.1 | 19.771 | 4.707 | 19.9 | -0.031 | 2 | 2.442% | -1.37 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 940 | 360 | 0 | 510.5 | 429.5 | 449.4 | 19.9 | 0.1 | 19.792 | 5.814 | 2 | 2.993% | 449.4 | 0.1 | 19.771 | 4.707 | 19.9 | -0.031 | 2 | 2.442% | -1.37 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 940 | 360 | 0 | 510.5 | 429.5 | 449.4 | 19.9 | 0.1 | 19.792 | 5.814 | 2 | 2.993% | 449.4 | 0.1 | 19.771 | 4.707 | 19.9 | -0.031 | 2 | 2.442% | -1.37 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.038 | 585 | 295 | 0 | 224.8 | 360.2 | 362.1 | 1.9 | -4.15 | 6.045 | 7.528 | 0.803 | 19.51% | 359.4 | -5.8 | 4.977 | 6.094 | -0.8 | -0.031 | 0.817 | -37.82% | 28.48 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.038 | 155 | 80 | 0 | 19.5 | 135.5 | 138.5 | 3 | 0.13 | 2.899 | 1.814 | 1.598 | 3.282% | 138.9 | 0.2 | 3.182 | 1.469 | 3.4 | -0.031 | 2 | 2.364% | -2.52 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.038 | 153 | 80 | 0 | 9.5 | 143.5 | 146.3 | 2.8 | 0.13 | 2.705 | 1.781 | 1.519 | 3.471% | 147 | 0.2 | 3.299 | 1.442 | 3.5 | -0.031 | 2 | 2.267% | -2.59 | 0.017 | 0.05 | 6.284% | 5.784%
Wind | WND | WIND | -0.038 | 140 | 0 | 0 | 100.4 | 39.6 | 127.4 | 87.8 | -4.31 | 92.156 | 1.802 | 2 | 0.1013% | 148.7 | -6 | 115.136 | 1.458 | 109.1 | -0.031 | 2 | 0.06656% | -0.02 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | BIT | FOSS | -0.038 | 664 | 159 | 0 | 504.5 | 159.5 | 173.2 | 13.7 | 0.52 | 13.127 | 7.991 | 1.643 | 3.072% | 170.8 | 0.7 | 10.521 | 6.469 | 11.3 | -0.031 | 1.626 | 3.038% | -0.89 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.038 | 577 | 158 | 0 | 416 | 161 | 175 | 14 | 0.53 | 13.445 | 6.862 | 1.959 | 2.612% | 172.1 | 0.7 | 10.356 | 5.555 | 11.1 | -0.031 | 1.864 | 2.688% | -0.92 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.038 | 610 | 159 | 0 | 449.8 | 160.2 | 176.2 | 16 | 0.36 | 15.708 | 7.26 | 2 | 2.416% | 171.5 | 0.5 | 10.773 | 5.877 | 11.3 | -0.031 | 1.833 | 2.792% | -0.9 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.038 | 360 | 148 | 20 | 185.2 | 154.8 | 164.1 | 9.3 | 4.32 | 4.992 | 3.216 | 1.552 | 2.455% | 167.8 | 6 | 6.963 | 2.564 | 13 | -0.031 | 2 | 1.433% | -0.75 | 0.017 | 0.058 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.066 | 511.8 | 275 | 12 | 107.4 | 392.4 | 393 | 0.6 | -2.48 | 3.076 | 4.335 | 0.709 | 93.88% | 395.3 | -3.4 | 6.38 | 3.697 | 2.9 | -0.061 | 1.726 | 17.95% | -14.87 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.066 | 217 | 62 | 0 | 146.3 | 70.7 | 74.1 | 3.4 | -1.58 | 4.89 | 1.308 | 2 | 7.037% | 74.7 | -2.2 | 6.127 | 0.951 | 4 | -0.061 | 2 | 5.53% | -1.93 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 48 | 20 | 0 | 26.9 | 21.1 | 21.2 | 0.1 | -0.1 | 0.157 | 0.492 | 0.319 | 53.08% | 21.1 | -0.1 | 0.124 | 0.414 | 0 | -0.061 | 0.3 | 0% |  | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 45.7 | 20 | 0 | 13.9 | 31.8 | 31.9 | 0.1 | -0.05 | 0.079 | 0.469 | 0.168 | 50.55% | 31.9 | -0.1 | 0.109 | 0.394 | 0.1 | -0.061 | 0.276 | 46.74% | -34.7 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.066 | 645 | 300 | 0 | 138.2 | 506.8 | 512.6 | 5.8 | -0.51 | 6.266 | 5.742 | 1.091 | 12.24% | 514.5 | -0.7 | 8.433 | 4.939 | 7.7 | -0.061 | 1.707 | 8.52% | -7.24 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 420 | 70 | 0 | 343.9 | 76.1 | 81.3 | 5.2 | -0.35 | 5.508 | 3.578 | 1.539 | 8.89% | 79.7 | -0.5 | 4.064 | 3.078 | 3.6 | -0.061 | 1.32 | 11.87% | -2.32 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.066 | 230 | 168 | 12 | 40.2 | 177.8 | 180.7 | 2.9 | -0.24 | 3.094 | 1.891 | 1.636 | 8.734% | 180.4 | -0.3 | 2.921 | 1.612 | 2.6 | -0.061 | 1.812 | 9.004% | -7.51 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.066 | 238 | 160 | 18 | 33.1 | 186.9 | 190.1 | 3.2 | -0.41 | 3.629 | 1.908 | 1.901 | 8.19% | 192.9 | -0.6 | 6.575 | 1.627 | 6 | -0.061 | 2 | 4.038% | -3.42 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.066 | 727 | 142 | 0 | 512.3 | 214.7 | 220.3 | 5.6 | -2.38 | 7.969 | 4.133 | 1.928 | 14.29% | 219.3 | -3.3 | 7.922 | 3.006 | 4.6 | -0.061 | 2 | 16.08% | -5.12 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 749 | 93 | 0 | 460 | 289 | 292.7 | 3.7 | 0.06 | 3.621 | 4.174 | 0.868 | 22.28% | 296.1 | 0.1 | 7.029 | 3.036 | 7.1 | -0.061 | 2 | 10.73% | -4.47 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.066 | 321 | 247 | 0 | 24.4 | 296.6 | 303.9 | 7.3 | -1.13 | 8.415 | 2.784 | 2 | 4.841% | 304.3 | -1.6 | 9.28 | 2.374 | 7.7 | -0.061 | 2 | 4.242% | -4.23 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.066 | 320 | 50 | 0 | 141.5 | 178.5 | 189.4 | 10.9 | 3.26 | 7.578 | 2.458 | 2 | 3.232% | 189.7 | 4.5 | 6.66 | 2.114 | 11.2 | -0.061 | 2 | 2.907% | -1.75 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.066 | 154 | 80 | 0 | 20.5 | 133.5 | 137.6 | 4.1 | -0.12 | 4.227 | 1.58 | 2 | 4.139% | 137.8 | -0.2 | 4.41 | 1.328 | 4.3 | -0.061 | 2 | 3.648% | -3.41 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.066 | 883.8 | 461 | 52.3 | 38.2 | 793.3 | 805.6 | 12.3 | -0.45 | 12.742 | 7.213 | 1.767 | 7.906% | 812.5 | -0.6 | 19.844 | 6.15 | 19.2 | -0.061 | 2 | 4.681% | -4.54 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.066 | 231 | 150 | 5 | 38.6 | 187.4 | 190 | 2.6 | 0.08 | 2.539 | 2.318 | 1.095 | 9.784% | 191 | 0.1 | 3.487 | 1.994 | 3.6 | -0.061 | 1.748 | 6.531% | -5.72 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.066 | 395 | 100 | 0 | 277.2 | 117.8 | 133 | 15.2 | -1.04 | 16.234 | 1.619 | 2 | 2.862% | 121.9 | -1.4 | 5.541 | 1.177 | 4.1 | -0.061 | 2 | 9.809% | -3.15 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 435 | 120 | 0 | 314.5 | 120.5 | 127.3 | 6.8 | 0.44 | 6.376 | 4.654 | 1.37 | 7.041% | 127.4 | 0.6 | 6.321 | 4.004 | 6.9 | -0.061 | 1.579 | 6.414% | -1.92 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.066 | 607 | 305 | 111 | 130.8 | 365.2 | 371.5 | 6.3 | -0.22 | 6.49 | 4.302 | 1.509 | 10.6% | 373.1 | -0.3 | 8.172 | 3.668 | 7.9 | -0.061 | 2 | 7.815% | -5.08 | 0.017 | 0.0578 | 5.933% | 5.163%
Solar | SUN | PVGR | -0.066 | 48 | 0 | 0 | 22.5 | 25.5 | 25.3 | -0.2 | -0.45 | 0.221 | 0.561 | 0.394 | -26.54% | 25.2 | -0.6 | 0.343 | 0.483 | -0.3 | -0.061 | 0.711 | -16.36% | 9.26 | 0.017 | 0.05 | 6.014% | 6.718%
CombinedCycle | CC | COGN | -0.066 | 519 | 336 | 0 | 28.4 | 490.6 | 497.3 | 6.7 | 0.53 | 6.194 | 4.502 | 1.376 | 8.525% | 498.4 | 0.7 | 7.061 | 3.839 | 7.8 | -0.061 | 1.839 | 6.768% | -6.92 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.066 | 520 | 309.7 | 33.8 | 35 | 451.2 | 459.4 | 8.2 | -0.38 | 8.646 | 4.217 | 2 | 6.979% | 458.8 | -0.5 | 8.203 | 3.596 | 7.6 | -0.061 | 2 | 6.96% | -6.53 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.066 | 517 | 310.3 | 8.3 | 15 | 493.7 | 496.8 | 3.1 | -0.66 | 3.829 | 4.412 | 0.868 | 18.35% | 497.2 | -0.9 | 4.442 | 3.762 | 3.5 | -0.061 | 1.181 | 15.03% | -15.51 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.066 | 234 | 150 | 12 | 9.7 | 212.3 | 216 | 3.7 | -0.53 | 4.199 | 2.101 | 1.999 | 6.964% | 216.1 | -0.7 | 4.497 | 1.807 | 3.8 | -0.061 | 2 | 6.268% | -6.14 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.066 | 237 | 150 | 5 | 11.8 | 220.2 | 224.1 | 3.9 | -0.88 | 4.805 | 2.17 | 2 | 6.692% | 224.3 | -1.2 | 5.28 | 1.867 | 4.1 | -0.061 | 2 | 5.884% | -5.9 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.066 | 246 | 110 | 12 | 10.6 | 223.4 | 227.4 | 4 | -0.63 | 4.562 | 2.195 | 2 | 6.772% | 227.5 | -0.9 | 4.942 | 1.888 | 4.1 | -0.061 | 2 | 6.107% | -5.99 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.066 | 108 | 35 | 0 | 71.3 | 36.7 | 37.9 | 1.2 | 0.47 | 0.709 | 1.108 | 0.64 | 9.924% | 39.8 | 0.7 | 2.421 | 0.932 | 3.1 | -0.061 | 2 | 3.551% | -1.29 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.066 | 820 | 300 | 0 | 52.4 | 767.6 | 775.1 | 7.5 | 1.18 | 6.313 | 9.587 | 0.659 | 12.03% | 774 | 1.6 | 4.802 | 8.247 | 6.4 | -0.061 | 0.582 | 13.03% | -13.19 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.066 | 510 | 210 | 0 | 12.4 | 497.6 | 501.3 | 3.7 | -0.37 | 4.042 | 5.963 | 0.678 | 15.17% | 507 | -0.5 | 9.905 | 5.129 | 9.4 | -0.061 | 1.931 | 5.519% | -5.82 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.066 | 702.6 | 453.8 | 36.2 | 148.7 | 517.7 | 530.8 | 13.1 | -0.65 | 13.814 | 5.78 | 2 | 5.902% | 536.9 | -0.9 | 20.125 | 4.929 | 19.2 | -0.061 | 2 | 3.722% | -2.96 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.066 | 481.3 | 230 | 0 | 125.4 | 355.9 | 368.3 | 12.4 | 0.24 | 12.184 | 4.175 | 2 | 4.272% | 378.7 | 0.3 | 22.457 | 3.56 | 22.8 | -0.061 | 2 | 2.147% | -1.72 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.066 | 114 | 45 | 0 | 65.6 | 48.4 | 54 | 5.6 | 0.08 | 5.445 | 0.989 | 2 | 2.244% | 53.7 | 0.1 | 5.176 | 0.843 | 5.3 | -0.061 | 2 | 2.192% | -1 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.066 | 708 | 420 | 0 | 112.3 | 595.7 | 606.2 | 10.5 | 0 | 10.437 | 6.141 | 1.699 | 7.42% | 606 | 0 | 10.246 | 5.236 | 10.3 | -0.061 | 1.957 | 6.991% | -6.36 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.066 | 47 | 12 | 0 | 5.4 | 41.6 | 43.2 | 1.6 | -0.01 | 1.557 | 0.482 | 2 | 3.249% | 43.8 | 0 | 2.17 | 0.405 | 2.2 | -0.061 | 2 | 2.185% | -2.07 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.066 | 47 | 12 | 0 | 5.3 | 41.7 | 42.9 | 1.2 | -0.04 | 1.245 | 0.482 | 2 | 4.332% | 42.9 | -0.1 | 1.33 | 0.405 | 1.2 | -0.061 | 2 | 4.006% | -3.8 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | SUB | FOSS | -0.066 | 940 | 322 | 0 | 26.5 | 913.5 | 920.9 | 7.4 | -2.71 | 10.1 | 7.836 | 1.289 | 13.98% | 921.4 | -3.8 | 11.722 | 6.741 | 7.9 | -0.061 | 1.739 | 12.1% | -12.72 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.066 | 940 | 322 | 0 | 26.5 | 913.5 | 920.9 | 7.4 | -2.71 | 10.1 | 7.836 | 1.289 | 13.98% | 921.4 | -3.8 | 11.722 | 6.741 | 7.9 | -0.061 | 1.739 | 12.1% | -12.72 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.066 | 940 | 322 | 0 | 26.5 | 913.5 | 920.9 | 7.4 | -2.71 | 10.1 | 7.836 | 1.289 | 13.98% | 921.4 | -3.8 | 11.722 | 6.741 | 7.9 | -0.061 | 1.739 | 12.1% | -12.72 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.066 | 940 | 322 | 0 | 26.5 | 913.5 | 920.9 | 7.4 | -2.71 | 10.1 | 7.836 | 1.289 | 13.98% | 921.4 | -3.8 | 11.722 | 6.741 | 7.9 | -0.061 | 1.739 | 12.1% | -12.72 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.066 | 80 | 57 | 0 | 22.8 | 57.2 | 59.1 | 1.9 | -0.69 | 2.577 | 0.821 | 2 | 4.646% | 59 | -1 | 2.819 | 0.69 | 1.8 | -0.061 | 2 | 4.534% | -3.48 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.066 | 84 | 57 | 0 | 25.7 | 58.3 | 59.8 | 1.5 | -0.32 | 1.788 | 0.862 | 2 | 6.179% | 59.8 | -0.5 | 1.901 | 0.725 | 1.5 | -0.061 | 2 | 5.712% | -4.26 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.066 | 840 | 440 | 0 | 130.6 | 709.4 | 712.1 | 2.7 | -0.78 | 3.493 | 7.286 | 0.479 | 34.23% | 710.1 | -1.1 | 1.807 | 6.213 | 0.7 | -0.061 | 0.291 | 122% | -111.44 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 522 | 275 | 12 | 181.7 | 328.3 | 331.7 | 3.4 | -3.31 | 6.669 | 4.737 | 1.408 | 16.64% | 335 | -4.6 | 11.305 | 4.44 | 6.7 | -0.063 | 2 | 8.185% | -5.3 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.065 | 602 | 220 | 0 | 28.2 | 573.8 | 580.7 | 6.9 | 3.85 | 3.122 | 7.511 | 0.416 | 9.456% | 579.6 | 5.4 | 0.518 | 7.063 | 5.8 | -0.063 | 0.073 | 10.9% | -10.71 | 0.017 | 0.05 | 6.284% | 5.784%
Wind | WND | WIND | -0.065 | 22.2 | 0 | 0 | 6 | 16.2 | 16.3 | 0.1 | -2.54 | 2.669 | 0.277 | 2 | 24.33% | 17.6 | -3.5 | 4.937 | 0.26 | 1.4 | -0.063 | 2 | 1.685% | -1.23 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | FOSS | -0.065 | 217 | 62 | 0 | 142.9 | 74.1 | 77.6 | 3.5 | 1.17 | 2.33 | 1.479 | 1.575 | 6.733% | 79.3 | 1.6 | 3.574 | 1.317 | 5.2 | -0.063 | 2 | 4.393% | -1.53 | 0.034 | 0.05 | 6.284% | 5.784%
Wind | WND | WIND | -0.065 | 99.8 | 0 | 0 | 87.8 | 12 | 12 | 0 | -0.06 | 0.055 | 1.245 | 0.044 | 0% | 12.3 | -0.1 | 0.396 | 1.171 | 0.3 | -0.063 | 0.339 | 35.02% | -4.24 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | SUB | FOSS | -0.065 | 420 | 125 | 0 | 283.5 | 136.5 | 140.7 | 4.2 | 0.09 | 4.115 | 3.654 | 1.126 | 10.84% | 139.6 | 0.1 | 2.979 | 3.436 | 3.1 | -0.063 | 0.867 | 14.23% | -4.76 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 417 | 125 | 0 | 281.5 | 135.5 | 138 | 2.5 | 0.1 | 2.393 | 3.633 | 0.659 | 18.08% | 135.1 | 0.1 | -0.511 | 3.416 | -0.4 | -0.063 | 0 | -109.5% | 36.63 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.065 | 236 | 172 | 18 | 42.4 | 175.6 | 178.7 | 3.1 | 0.18 | 2.97 | 2.025 | 1.467 | 8.256% | 177.4 | 0.2 | 1.554 | 1.898 | 1.8 | -0.063 | 0.819 | 13.78% | -10.55 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 511 | 352 | 0 | 156 | 355 | 361.1 | 6.1 | 0.01 | 6.039 | 4.746 | 1.272 | 9.08% | 361.5 | 0 | 6.428 | 4.449 | 6.5 | -0.063 | 1.445 | 8.259% | -5.91 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 602 | 460 | 73 | 55.9 | 473.1 | 480.3 | 7.2 | 0.24 | 6.947 | 4.914 | 1.414 | 9.062% | 483.1 | 0.3 | 9.681 | 4.606 | 10 | -0.063 | 2 | 6.324% | -5.12 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.065 | 645 | 300 | 0 | 206 | 439 | 450.9 | 11.9 | -1.06 | 12.879 | 7.084 | 1.818 | 5.874% | 448.6 | -1.5 | 11.035 | 6.661 | 9.6 | -0.063 | 1.657 | 7.058% | -4.95 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.065 | 321 | 244 | 0 | 70.7 | 250.3 | 257.3 | 7 | 0.12 | 6.879 | 2.982 | 2 | 4.972% | 257.8 | 0.2 | 7.318 | 2.795 | 7.5 | -0.063 | 2 | 4.498% | -3.61 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 445 | 268 | 12 | 39 | 394 | 401.5 | 7.5 | -0.18 | 7.698 | 4.022 | 1.914 | 6.432% | 401.8 | -0.2 | 8.089 | 3.77 | 7.8 | -0.063 | 2 | 5.994% | -5.47 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.065 | 588.7 | 149.7 | 0 | 46.6 | 542.1 | 549.7 | 7.6 | -1.59 | 9.14 | 5.219 | 1.751 | 8.395% | 548.5 | -2.2 | 8.543 | 4.907 | 6.4 | -0.063 | 1.741 | 9.663% | -9.17 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 588.7 | 149.7 | 0 | 46.6 | 542.1 | 549.7 | 7.6 | -1.59 | 9.14 | 5.219 | 1.751 | 8.395% | 548.5 | -2.2 | 8.543 | 4.907 | 6.4 | -0.063 | 1.741 | 9.663% | -9.17 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 582 | 149.6 | 0 | 14.4 | 567.6 | 575.6 | 8 | -1.38 | 9.39 | 5.103 | 1.84 | 7.885% | 574 | -1.9 | 8.406 | 4.799 | 6.4 | -0.063 | 1.752 | 9.553% | -9.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 582 | 149.6 | 0 | 14.4 | 567.6 | 575.6 | 8 | -1.38 | 9.39 | 5.103 | 1.84 | 7.885% | 574 | -1.9 | 8.406 | 4.799 | 6.4 | -0.063 | 1.752 | 9.553% | -9.6 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.065 | 913.4 | 461 | 141 | 176.7 | 595.7 | 612.5 | 16.8 | 0.26 | 16.535 | 7.174 | 2 | 5.892% | 617.3 | 0.4 | 21.187 | 6.724 | 21.6 | -0.063 | 2 | 4.441% | -2.99 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 898.4 | 461 | 141 | 159.7 | 597.7 | 617.2 | 19.5 | 1.51 | 18.038 | 7.035 | 2 | 4.993% | 617.7 | 2.1 | 17.918 | 6.594 | 20 | -0.063 | 2 | 4.718% | -3.24 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.065 | 470 | 180 | 0 | 289.8 | 180.2 | 187.2 | 7 | -0.02 | 7 | 2.034 | 2 | 7.282% | 185.8 | 0 | 5.594 | 1.811 | 5.6 | -0.063 | 2 | 8.823% | -3.48 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 470 | 180 | 0 | 289.8 | 180.2 | 187.2 | 7 | -0.02 | 7 | 2.034 | 2 | 7.282% | 185.8 | 0 | 5.594 | 1.811 | 5.6 | -0.063 | 2 | 8.823% | -3.48 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 470 | 180 | 0 | 289.8 | 180.2 | 187.2 | 7 | -0.02 | 7 | 2.034 | 2 | 7.282% | 185.8 | 0 | 5.594 | 1.811 | 5.6 | -0.063 | 2 | 8.823% | -3.48 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 470 | 180 | 0 | 289.8 | 180.2 | 187.2 | 7 | -0.02 | 7 | 2.034 | 2 | 7.282% | 185.8 | 0 | 5.594 | 1.811 | 5.6 | -0.063 | 2 | 8.823% | -3.48 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.065 | 231 | 150 | 5 | 67.2 | 158.8 | 162.8 | 4 | -0.51 | 4.514 | 2.3 | 1.962 | 6.263% | 164.5 | -0.7 | 6.441 | 2.163 | 5.7 | -0.063 | 2 | 4.26% | -3.01 | 0.017 | 0.05 | 5.933% | 5.163%
Solar | SUN | PVGR | -0.065 | 8.1 | 0 | 0 | 6.9 | 1.2 | 2 | 0.8 | 0.34 | 0.416 | 0.101 | 2 | 1.132% | 1.9 | 0.5 | 0.203 | 0.095 | 0.7 | -0.063 | 2 | 1.255% | -0.15 | 0.017 | 0.05 | 6.014% | 6.718%
CombinedCycle | CC | COGN | -0.065 | 607 | 305 | 111 | 177.1 | 318.9 | 326.4 | 7.5 | -0.88 | 8.418 | 4.607 | 1.827 | 8.772% | 327.8 | -1.2 | 10.138 | 4.318 | 8.9 | -0.063 | 2 | 7.164% | -3.88 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 620 | 305 | 111 | 202.4 | 306.6 | 316.3 | 9.7 | -0.31 | 10 | 4.728 | 2 | 6.927% | 319.1 | -0.4 | 12.966 | 4.432 | 12.5 | -0.063 | 2 | 5.21% | -2.65 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.065 | 100 | 62 | 0 | 37.8 | 62.2 | 65.6 | 3.4 | -0.23 | 3.55 | 1.098 | 2 | 3.195% | 65.8 | -0.3 | 3.874 | 1.024 | 3.6 | -0.063 | 2 | 2.925% | -1.86 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 520 | 309.7 | 23.2 | 62.6 | 434.2 | 441.1 | 6.9 | 0.4 | 6.488 | 4.615 | 1.406 | 8.168% | 439.8 | 0.6 | 5.025 | 4.326 | 5.6 | -0.063 | 1.162 | 9.755% | -8.39 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 520 | 325.6 | 7.1 | 78.8 | 434.1 | 441.1 | 7 | 0.47 | 6.501 | 4.764 | 1.365 | 8.052% | 440.4 | 0.7 | 5.577 | 4.466 | 6.3 | -0.063 | 1.249 | 8.671% | -7.46 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.065 | 240 | 150 | 5 | 83.7 | 151.3 | 156.5 | 5.2 | -0.12 | 5.364 | 2.054 | 2 | 5.005% | 155.8 | -0.2 | 4.663 | 1.932 | 4.5 | -0.063 | 2 | 5.606% | -3.64 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.065 | 760 | 300 | 0 | 446.6 | 313.4 | 322.6 | 9.2 | -0.96 | 10.163 | 9.482 | 1.072 | 8.952% | 322.7 | -1.3 | 10.625 | 8.917 | 9.3 | -0.063 | 1.192 | 8.584% | -3.65 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.065 | 820 | 300 | 0 | 506.6 | 313.4 | 322.4 | 9 | -0.96 | 10.026 | 10.231 | 0.98 | 9.874% | 322.2 | -1.3 | 10.171 | 9.621 | 8.8 | -0.063 | 1.057 | 9.787% | -3.85 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.065 | 515 | 210 | 0 | 297 | 218 | 217.8 | -0.2 | -0.56 | 0.355 | 6.426 | 0.055 | -279.1% | 220.8 | -0.8 | 3.556 | 6.042 | 2.8 | -0.063 | 0.589 | 19.32% | -8.42 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.065 | 665.6 | 427 | 40.6 | 64.7 | 560.3 | 568.6 | 8.3 | 4.25 | 4.039 | 5.805 | 0.696 | 8.691% | 574.1 | 5.9 | 7.882 | 5.441 | 13.8 | -0.063 | 1.448 | 5.066% | -4.4 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 248 | 140 | 28.6 | 73 | 146.4 | 149.7 | 3.3 | 0.24 | 3.116 | 2.038 | 1.529 | 8.15% | 153.5 | 0.3 | 6.77 | 1.91 | 7.1 | -0.063 | 2 | 3.672% | -2.23 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.065 | 650 | 189.6 | 0 | 321.6 | 328.4 | 336.9 | 8.5 | 0.76 | 7.765 | 4.78 | 1.625 | 8.288% | 337.7 | 1.1 | 8.266 | 4.495 | 9.3 | -0.063 | 1.839 | 7.342% | -3.82 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 650 | 189.6 | 0 | 321.6 | 328.4 | 336.9 | 8.5 | 0.76 | 7.765 | 4.78 | 1.625 | 8.288% | 337.7 | 1.1 | 8.266 | 4.495 | 9.3 | -0.063 | 1.839 | 7.342% | -3.82 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 650 | 189.6 | 0 | 321.6 | 328.4 | 336.9 | 8.5 | 0.76 | 7.765 | 4.78 | 1.625 | 8.288% | 337.7 | 1.1 | 8.266 | 4.495 | 9.3 | -0.063 | 1.839 | 7.342% | -3.82 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 650 | 189.6 | 0 | 321.6 | 328.4 | 336.9 | 8.5 | 0.76 | 7.765 | 4.78 | 1.625 | 8.288% | 337.7 | 1.1 | 8.266 | 4.495 | 9.3 | -0.063 | 1.839 | 7.342% | -3.82 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 650 | 189.6 | 0 | 321.6 | 328.4 | 336.9 | 8.5 | 0.76 | 7.765 | 4.78 | 1.625 | 8.288% | 337.7 | 1.1 | 8.266 | 4.495 | 9.3 | -0.063 | 1.839 | 7.342% | -3.82 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.065 | 475.2 | 230 | 0 | 201.3 | 273.9 | 282.7 | 8.8 | -4.72 | 13.535 | 4.414 | 2 | 5.853% | 296.2 | -6.6 | 28.861 | 4.137 | 22.3 | -0.063 | 2 | 2.239% | -1.33 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.065 | 55.8 | 22.5 | 0 | 33.2 | 22.6 | 24.1 | 1.5 | 0.17 | 1.341 | 0.613 | 2 | 4.049% | 29.6 | 0.2 | 6.717 | 0.571 | 7 | -0.063 | 2 | 0.841% | -0.35 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.065 | 55.9 | 22.5 | 0 | 33.3 | 22.6 | 24.3 | 1.7 | 0.07 | 1.634 | 0.613 | 2 | 3.579% | 29.9 | 0.1 | 7.228 | 0.572 | 7.3 | -0.063 | 2 | 0.8079% | -0.33 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.065 | 715 | 420 | 0 | 242 | 473 | 492.1 | 19.1 | 1.63 | 17.469 | 6.641 | 2 | 4.057% | 490.3 | 2.3 | 15.126 | 6.225 | 17.3 | -0.063 | 2 | 4.341% | -2.96 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.065 | 145.1 | 0 | 0 | 43.4 | 101.7 | 110.3 | 8.6 | 2.6 | 5.991 | 1.81 | 2 | 1.831% | 109.5 | 3.6 | 4.18 | 1.702 | 7.8 | -0.063 | 2 | 1.957% | -1.41 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.065 | 225 | 118 | 0 | 53.8 | 171.2 | 175.7 | 4.5 | -0.59 | 5.046 | 2.09 | 2 | 5.423% | 177.3 | -0.8 | 6.937 | 1.959 | 6.1 | -0.063 | 2 | 3.878% | -3.04 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.065 | 940 | 322 | 0 | 30 | 910 | 920.9 | 10.9 | -3.83 | 14.766 | 8.362 | 1.766 | 9.345% | 922.9 | -5.3 | 18.211 | 7.863 | 12.9 | -0.063 | 2 | 7.653% | -7.64 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 940 | 322 | 0 | 30 | 910 | 920.9 | 10.9 | -3.83 | 14.766 | 8.362 | 1.766 | 9.345% | 922.9 | -5.3 | 18.211 | 7.863 | 12.9 | -0.063 | 2 | 7.653% | -7.64 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 940 | 322 | 0 | 30 | 910 | 920.9 | 10.9 | -3.83 | 14.766 | 8.362 | 1.766 | 9.345% | 922.9 | -5.3 | 18.211 | 7.863 | 12.9 | -0.063 | 2 | 7.653% | -7.64 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.065 | 940 | 322 | 0 | 30 | 910 | 920.9 | 10.9 | -3.83 | 14.766 | 8.362 | 1.766 | 9.345% | 922.9 | -5.3 | 18.211 | 7.863 | 12.9 | -0.063 | 2 | 7.653% | -7.64 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.065 | 78 | 57 | 0 | 19.8 | 58.2 | 60.3 | 2.1 | -0.02 | 2.058 | 0.856 | 2 | 4.037% | 60.2 | 0 | 2.007 | 0.798 | 2 | -0.063 | 2 | 4.109% | -3.14 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.065 | 80 | 57 | 0 | 22.8 | 57.2 | 58.9 | 1.7 | 0 | 1.692 | 0.878 | 1.926 | 5.115% | 58.7 | 0 | 1.501 | 0.819 | 1.5 | -0.063 | 1.833 | 5.619% | -4.11 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.065 | 845 | 465 | 0 | 363.9 | 481.1 | 494.5 | 13.4 | 0.66 | 12.759 | 7.849 | 1.626 | 6.834% | 493.4 | 0.9 | 11.402 | 7.357 | 12.3 | -0.063 | 1.55 | 7.216% | -4.24 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.065 | 664 | 156 | 0 | 158.3 | 505.7 | 514.3 | 8.6 | -0.8 | 9.435 | 6.69 | 1.41 | 8.368% | 513.5 | -1.1 | 8.884 | 6.291 | 7.8 | -0.063 | 1.412 | 8.942% | -7.02 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.065 | 663 | 156 | 0 | 190.2 | 472.8 | 481 | 8.2 | -0.04 | 8.27 | 6.798 | 1.217 | 8.763% | 480.4 | -0.1 | 7.701 | 6.393 | 7.6 | -0.063 | 1.205 | 9.164% | -6.74 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.065 | 577 | 159 | 0 | 71.4 | 505.6 | 512.7 | 7.1 | -1.59 | 8.608 | 5.6 | 1.537 | 8.808% | 512.2 | -2.2 | 8.725 | 5.266 | 6.6 | -0.063 | 1.657 | 9.184% | -8.29 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.065 | 610 | 326 | 0 | 95.3 | 514.7 | 521.1 | 6.4 | -0.58 | 7.019 | 5.92 | 1.186 | 10.33% | 521.2 | -0.8 | 7.378 | 5.567 | 6.5 | -0.063 | 1.325 | 9.858% | -8.57 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 523.6 | 275 | 12 | 143.9 | 367.7 | 371.8 | 4.1 | -3.13 | 7.267 | 6.064 | 1.198 | 17.03% | 375.3 | -4.3 | 11.949 | 6.198 | 7.6 | -0.081 | 1.928 | 9.305% | -6.45 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 199 | 147 | 0 | 40.6 | 158.4 | 168.1 | 9.7 | 0.07 | 9.636 | 2.359 | 2 | 2.738% | 171 | 0.1 | 12.54 | 2.411 | 12.6 | -0.081 | 2 | 2.134% | -1.67 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.08 | 560 | 390 | 0 | 164.7 | 395.3 | 406.5 | 11.2 | -1.56 | 12.774 | 7.136 | 1.79 | 6.669% | 406.8 | -2.2 | 13.687 | 7.288 | 11.5 | -0.081 | 1.878 | 6.576% | -4.58 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 420 | 125 | 0 | 291.2 | 128.8 | 134.3 | 5.5 | 0.13 | 5.415 | 4.63 | 1.17 | 10.19% | 133 | 0.2 | 4.043 | 4.728 | 4.2 | -0.081 | 0.855 | 13.51% | -4.08 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 417 | 160 | 0 | 244.5 | 172.5 | 180.2 | 7.7 | -0.46 | 8.164 | 4.484 | 1.821 | 7.224% | 175.9 | -0.6 | 4.117 | 4.579 | 3.4 | -0.081 | 0.899 | 16.57% | -6.76 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 749 | 93 | 0 | 655.5 | 93.5 | 104.7 | 11.2 | -1.02 | 12.142 | 5.506 | 2 | 8.922% | 102.9 | -1.4 | 10.827 | 5.69 | 9.4 | -0.081 | 1.903 | 10.76% | -1.32 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 645 | 300 | 0 | 12.9 | 632.1 | 632.1 | 0 | -1.06 | 1.078 | 8.656 | 0.125 | 0% | 633.1 | -1.5 | 2.506 | 8.84 | 1 | -0.081 | 0.284 | 87.1% | -84.25 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 331 | 253 | 0 | 35.7 | 295.3 | 301.2 | 5.9 | -1.08 | 6.995 | 3.923 | 1.783 | 7.485% | 302 | -1.5 | 8.209 | 4.01 | 6.7 | -0.081 | 2 | 6.674% | -5.87 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.08 | 105 | 12 | 0 | 92.9 | 12.1 | 13.7 | 1.6 | 0.07 | 1.613 | 1.639 | 0.984 | 8.768% | 13.6 | 0.1 | 1.479 | 1.674 | 1.5 | -0.081 | 0.883 | 9.469% | -1.06 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 320 | 50 | 0 | 265.4 | 54.6 | 56.7 | 2.1 | -0.1 | 2.247 | 3.618 | 0.621 | 20.33% | 55.3 | -0.1 | 0.889 | 3.695 | 0.7 | -0.081 | 0.241 | 61.75% | -10.36 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 98 | 72 | 0 | 23.8 | 74.2 | 81.2 | 7 | -0.99 | 7.914 | 1.162 | 2 | 1.871% | 85.8 | -1.4 | 12.995 | 1.187 | 11.6 | -0.081 | 2 | 1.143% | -0.85 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 331 | 144 | 0 | 27.6 | 303.4 | 308.2 | 4.8 | -2.36 | 7.134 | 3.923 | 1.818 | 9.2% | 310.4 | -3.3 | 10.247 | 4.01 | 7 | -0.081 | 2 | 6.388% | -5.78 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.08 | 590.5 | 149.1 | 0 | 17.8 | 572.7 | 586 | 13.3 | -1.27 | 14.656 | 6.49 | 2 | 5.922% | 581.8 | -1.8 | 10.876 | 6.628 | 9.1 | -0.081 | 1.641 | 8.763% | -8.39 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 590.5 | 149.1 | 0 | 17.8 | 572.7 | 586 | 13.3 | -1.27 | 14.656 | 6.49 | 2 | 5.922% | 581.8 | -1.8 | 10.876 | 6.628 | 9.1 | -0.081 | 1.641 | 8.763% | -8.39 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 271 | 175 | 44 | 52 | 175 | 181.2 | 6.2 | -1.2 | 7.363 | 2.691 | 2 | 5.833% | 183.8 | -1.7 | 10.49 | 2.751 | 8.8 | -0.081 | 2 | 4.161% | -2.65 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.08 | 470 | 180 | 0 | 21.6 | 448.4 | 447.6 | -0.8 | -1.22 | 0.47 | 3.634 | 0.129 | -78.4% | 446.1 | -1.7 | -0.582 | 3.755 | -2.3 | -0.081 | 0 | -27.61% | 25.97 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 470 | 180 | 0 | 21.6 | 448.4 | 447.6 | -0.8 | -1.22 | 0.47 | 3.634 | 0.129 | -78.4% | 446.1 | -1.7 | -0.582 | 3.755 | -2.3 | -0.081 | 0 | -27.61% | 25.97 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 470 | 180 | 0 | 21.6 | 448.4 | 447.6 | -0.8 | -1.22 | 0.47 | 3.634 | 0.129 | -78.4% | 446.1 | -1.7 | -0.582 | 3.755 | -2.3 | -0.081 | 0 | -27.61% | 25.97 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 470 | 180 | 0 | 21.6 | 448.4 | 447.6 | -0.8 | -1.22 | 0.47 | 3.634 | 0.129 | -78.4% | 446.1 | -1.7 | -0.582 | 3.755 | -2.3 | -0.081 | 0 | -27.61% | 25.97 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.08 | 230 | 150 | 5 | 19 | 206 | 210.6 | 4.6 | -0.63 | 5.258 | 3.284 | 1.601 | 6.673% | 210.9 | -0.9 | 5.713 | 3.354 | 4.9 | -0.081 | 1.703 | 6.343% | -5.6 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.08 | 237 | 150 | 12 | 39.1 | 185.9 | 190.7 | 4.8 | -0.43 | 5.251 | 3.096 | 1.696 | 6.589% | 190.9 | -0.6 | 5.585 | 3.162 | 5 | -0.081 | 1.766 | 6.405% | -4.95 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.08 | 238 | 150 | 12 | 17.7 | 208.3 | 211.8 | 3.5 | -0.94 | 4.466 | 3.323 | 1.344 | 9.075% | 212.8 | -1.3 | 5.773 | 3.394 | 4.5 | -0.081 | 1.701 | 7.146% | -6.17 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.08 | 228 | 150 | 5 | 18.1 | 204.9 | 209.2 | 4.3 | -0.26 | 4.562 | 3.245 | 1.406 | 7.076% | 209.8 | -0.4 | 5.245 | 3.314 | 4.9 | -0.081 | 1.583 | 6.287% | -5.57 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 607 | 305 | 111 | 142.7 | 353.3 | 360.6 | 7.3 | -0.24 | 7.469 | 5.879 | 1.271 | 11.09% | 361.9 | -0.3 | 8.931 | 6.009 | 8.6 | -0.081 | 1.486 | 9.532% | -5.47 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 624.9 | 260 | 0 | 174.6 | 450.3 | 455.4 | 5.1 | -0.15 | 5.261 | 7.407 | 0.71 | 16.34% | 460.5 | -0.2 | 10.484 | 7.571 | 10.2 | -0.081 | 1.385 | 8.274% | -5.88 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.08 | 650 | 259 | 0 | 294.2 | 355.8 | 360.8 | 5 | -0.46 | 5.505 | 6.979 | 0.789 | 17.34% | 363.7 | -0.6 | 8.587 | 7.128 | 7.9 | -0.081 | 1.205 | 11.11% | -6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.08 | 836 | 259 | 0 | 400.3 | 435.7 | 441.4 | 5.7 | -3.14 | 8.843 | 9.649 | 0.916 | 19.56% | 441.1 | -4.4 | 9.773 | 9.854 | 5.4 | -0.081 | 0.992 | 20.91% | -10.75 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.08 | 101 | 65 | 0 | 20.5 | 80.5 | 84.2 | 3.7 | -0.23 | 3.935 | 1.413 | 2 | 3.647% | 84.3 | -0.3 | 4.149 | 1.447 | 3.8 | -0.081 | 2 | 3.596% | -2.82 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 526.9 | 309.7 | 40.5 | 21.6 | 464.8 | 473.7 | 8.9 | -1.51 | 10.404 | 5.765 | 1.805 | 7.897% | 472.4 | -2.1 | 9.667 | 5.893 | 7.6 | -0.081 | 1.641 | 9.363% | -8.15 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.08 | 237 | 150 | 12 | 9.7 | 215.3 | 217.8 | 2.5 | -0.34 | 2.912 | 2.892 | 1.007 | 12.65% | 218 | -0.5 | 3.166 | 2.954 | 2.7 | -0.081 | 1.072 | 11.86% | -10.62 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.08 | 236 | 150 | 12 | 9.7 | 214.3 | 217.8 | 3.5 | -0.28 | 3.728 | 2.871 | 1.298 | 8.999% | 218 | -0.4 | 4.097 | 2.932 | 3.7 | -0.081 | 1.397 | 8.618% | -7.71 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.08 | 234 | 150 | 12 | 10.4 | 211.6 | 215.8 | 4.2 | -0.17 | 4.376 | 2.825 | 1.549 | 7.435% | 216.2 | -0.2 | 4.821 | 2.885 | 4.6 | -0.081 | 1.671 | 6.874% | -6.13 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.08 | 236 | 150 | 12 | 7.7 | 216.3 | 218.5 | 2.2 | -0.29 | 2.457 | 2.887 | 0.851 | 14.32% | 218.6 | -0.4 | 2.702 | 2.949 | 2.3 | -0.081 | 0.916 | 13.86% | -12.53 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.08 | 251 | 110 | 12 | 10.5 | 228.5 | 232.7 | 4.2 | -0.66 | 4.895 | 3.055 | 1.602 | 7.975% | 233.1 | -0.9 | 5.56 | 3.12 | 4.6 | -0.081 | 1.782 | 7.372% | -6.62 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.08 | 660 | 300 | 0 | 45.8 | 614.2 | 614.6 | 0.4 | -3.51 | 3.959 | 10.399 | 0.381 | 220.1% | 612.7 | -4.9 | 3.397 | 10.62 | -1.5 | -0.081 | 0.32 | -59.42% | 54.58 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.08 | 710 | 300 | 0 | 42.1 | 667.9 | 689.7 | 21.8 | 2.53 | 19.182 | 11.187 | 1.715 | 4.344% | 689.3 | 3.5 | 17.861 | 11.424 | 21.4 | -0.081 | 1.563 | 4.48% | -4.16 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 650 | 189.6 | 0 | 69.6 | 580.4 | 586.4 | 6 | 0.53 | 5.557 | 6.772 | 0.821 | 14.45% | 587.7 | 0.7 | 6.633 | 6.916 | 7.3 | -0.081 | 0.959 | 12.02% | -10.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 650 | 189.6 | 0 | 69.6 | 580.4 | 586.4 | 6 | 0.53 | 5.557 | 6.772 | 0.821 | 14.45% | 587.7 | 0.7 | 6.633 | 6.916 | 7.3 | -0.081 | 0.959 | 12.02% | -10.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 650 | 189.6 | 0 | 69.6 | 580.4 | 586.4 | 6 | 0.53 | 5.557 | 6.772 | 0.821 | 14.45% | 587.7 | 0.7 | 6.633 | 6.916 | 7.3 | -0.081 | 0.959 | 12.02% | -10.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 650 | 189.6 | 0 | 69.6 | 580.4 | 586.4 | 6 | 0.53 | 5.557 | 6.772 | 0.821 | 14.45% | 587.7 | 0.7 | 6.633 | 6.916 | 7.3 | -0.081 | 0.959 | 12.02% | -10.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 650 | 189.6 | 0 | 69.6 | 580.4 | 586.4 | 6 | 0.53 | 5.557 | 6.772 | 0.821 | 14.45% | 587.7 | 0.7 | 6.633 | 6.916 | 7.3 | -0.081 | 0.959 | 12.02% | -10.6 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 713 | 461.1 | 33.8 | 121.4 | 557.8 | 580.9 | 23.1 | 4.96 | 18.204 | 8.05 | 2 | 4.117% | 588.7 | 6.9 | 24.032 | 8.228 | 30.9 | -0.081 | 2 | 3.116% | -2.41 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 480.3 | 230 | 0 | 205.4 | 274.9 | 280.2 | 5.3 | -6.08 | 11.363 | 5.693 | 1.996 | 12.09% | 288.7 | -8.5 | 22.242 | 5.819 | 13.8 | -0.081 | 2 | 4.701% | -2.65 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 462 | 275 | 0 | 54.3 | 407.7 | 430.1 | 22.4 | 2.47 | 19.92 | 5.476 | 2 | 2.751% | 431.8 | 3.4 | 20.704 | 5.597 | 24.1 | -0.081 | 2 | 2.589% | -2.25 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 222.1 | 118 | 0 | 40.6 | 181.5 | 190.3 | 8.8 | 2.29 | 6.573 | 2.632 | 2 | 3.368% | 194.6 | 3.2 | 9.917 | 2.691 | 13.1 | -0.081 | 2 | 2.291% | -1.85 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.08 | 940 | 322 | 0 | 30.6 | 909.4 | 922.5 | 13.1 | -1.19 | 14.227 | 10.552 | 1.348 | 9.57% | 926.5 | -1.7 | 18.739 | 10.777 | 17.1 | -0.081 | 1.739 | 7.423% | -7.09 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 940 | 322 | 0 | 30.6 | 909.4 | 922.5 | 13.1 | -1.19 | 14.227 | 10.552 | 1.348 | 9.57% | 926.5 | -1.7 | 18.739 | 10.777 | 17.1 | -0.081 | 1.739 | 7.423% | -7.09 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 940 | 322 | 0 | 30.6 | 909.4 | 922.5 | 13.1 | -1.19 | 14.227 | 10.552 | 1.348 | 9.57% | 926.5 | -1.7 | 18.739 | 10.777 | 17.1 | -0.081 | 1.739 | 7.423% | -7.09 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 940 | 322 | 0 | 30.6 | 909.4 | 922.5 | 13.1 | -1.19 | 14.227 | 10.552 | 1.348 | 9.57% | 926.5 | -1.7 | 18.739 | 10.777 | 17.1 | -0.081 | 1.739 | 7.423% | -7.09 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.08 | 80 | 57 | 0 | 23 | 57 | 59.1 | 2.1 | -0.33 | 2.401 | 1.119 | 2 | 5.093% | 59 | -0.5 | 2.402 | 1.146 | 2 | -0.081 | 2 | 5.414% | -3.79 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 264 | 100 | 20 | 42.1 | 201.9 | 206.7 | 4.8 | -0.27 | 5.113 | 2.892 | 1.768 | 7.339% | 211 | -0.4 | 9.48 | 2.956 | 9.1 | -0.081 | 2 | 3.92% | -2.96 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 845 | 465 | 0 | 139.9 | 705.1 | 717 | 11.9 | -0.08 | 11.974 | 10.016 | 1.196 | 9.47% | 719.4 | -0.1 | 14.394 | 10.237 | 14.3 | -0.081 | 1.406 | 7.979% | -6.57 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 684 | 300 | 40 | 205.2 | 438.8 | 456.9 | 18.1 | -0.86 | 18.905 | 7.634 | 2 | 5.04% | 454.9 | -1.2 | 17.32 | 7.802 | 16.1 | -0.081 | 2 | 5.737% | -3.63 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 517 | 275 | 12 | 121.4 | 383.6 | 387.9 | 4.3 | 1.18 | 3.119 | 5.7 | 0.547 | 14.84% | 393 | 1.6 | 7.756 | 5.986 | 9.4 | -0.076 | 1.296 | 6.97% | -5.03 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.074 | 217 | 62 | 0 | 34.6 | 182.4 | 188.3 | 5.9 | 1 | 4.907 | 2.037 | 2 | 4.546% | 188.6 | 1.4 | 4.873 | 2.195 | 6.2 | -0.076 | 2 | 4.442% | -3.62 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 560 | 390 | 0 | 40.2 | 519.8 | 525.3 | 5.5 | -0.81 | 6.361 | 8.418 | 0.756 | 12.56% | 525.1 | -1.1 | 6.459 | 8.823 | 5.3 | -0.076 | 0.732 | 13.39% | -12.09 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 420 | 170 | 0 | 78.1 | 341.9 | 347.4 | 5.5 | 0.04 | 5.511 | 4.88 | 1.129 | 9.423% | 345.7 | 0.1 | 3.8 | 5.115 | 3.8 | -0.076 | 0.743 | 14.01% | -11.09 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 410 | 70 | 0 | 110.5 | 299.5 | 306.4 | 6.9 | 3.8 | 3.057 | 5.92 | 0.516 | 7.333% | 306.1 | 5.3 | 1.297 | 6.205 | 6.6 | -0.076 | 0.209 | 7.873% | -5.59 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 327 | 243 | 0 | 32.8 | 294.2 | 301.3 | 7.1 | -0.19 | 7.287 | 3.691 | 1.974 | 5.684% | 301.9 | -0.3 | 7.949 | 3.876 | 7.7 | -0.076 | 2 | 5.383% | -4.71 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.074 | 105 | 12 | 0 | 91.8 | 13.2 | 14.1 | 0.9 | 0.61 | 0.299 | 1.564 | 0.191 | 14.42% | 14 | 0.8 | -0.048 | 1.639 | 0.8 | -0.076 | 0 | 16.66% | -2 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 428 | 50 | 0 | 32.9 | 395.1 | 408.2 | 13.1 | -0.95 | 14.008 | 5.449 | 2 | 4.032% | 406.7 | -1.3 | 12.885 | 5.711 | 11.6 | -0.076 | 2 | 4.676% | -4.2 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 330 | 138 | 0 | 11.4 | 318.6 | 324 | 5.4 | 0.19 | 5.244 | 3.725 | 1.408 | 7.542% | 325.4 | 0.3 | 6.549 | 3.911 | 6.8 | -0.076 | 1.674 | 6.151% | -5.77 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | STM | -0.074 | 316 | 55 | 0 | 60.6 | 255.4 | 261.5 | 6.1 | -0.22 | 6.282 | 4.552 | 1.38 | 6.394% | 260.5 | -0.3 | 5.375 | 4.771 | 5.1 | -0.076 | 1.127 | 7.854% | -6.17 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | FOSS | -0.074 | 234 | 47 | 0 | 99.7 | 134.3 | 137.8 | 3.5 | -4.92 | 8.464 | 2.015 | 2 | 8.262% | 136.4 | -6.8 | 9.033 | 2.171 | 2.1 | -0.076 | 2 | 14.14% | -7.86 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 385 | 40 | 0 | 171.9 | 213.1 | 211.3 | -1.8 | -3.73 | 1.953 | 3.167 | 0.617 | -26.41% | 210.7 | -5.2 | 2.834 | 3.412 | -2.4 | -0.076 | 0.83 | -20.34% | 10.93 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.074 | 228 | 150 | 5 | 16.7 | 206.3 | 207.2 | 0.9 | 0.46 | 0.444 | 3.108 | 0.143 | 31.28% | 207.4 | 0.6 | 0.496 | 3.258 | 1.1 | -0.076 | 0.152 | 26.28% | -23.1 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.074 | 234 | 150 | 12 | 16 | 206 | 208.5 | 2.5 | 0.13 | 2.401 | 3.092 | 0.777 | 11.56% | 208.7 | 0.2 | 2.499 | 3.24 | 2.7 | -0.076 | 0.771 | 10.99% | -9.4 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.074 | 236 | 150 | 12 | 16.7 | 207.3 | 210.3 | 3 | -0.09 | 3.132 | 3.132 | 1 | 9.712% | 209.8 | -0.1 | 2.661 | 3.283 | 2.5 | -0.076 | 0.811 | 11.97% | -10.22 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.074 | 226 | 150 | 5 | 19.3 | 201.7 | 204.1 | 2.4 | 0.09 | 2.273 | 3.04 | 0.748 | 11.63% | 204.5 | 0.1 | 2.649 | 3.186 | 2.8 | -0.076 | 0.831 | 10.23% | -8.87 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 153.9 | 0 | 0 | 13.9 | 140 | 140.8 | 0.8 | -4.52 | 5.402 | 1.737 | 2 | 23.76% | 135.2 | -6.3 | 1.484 | 1.824 | -4.8 | -0.076 | 0.814 | -4.067% | 3.59 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 589.6 | 260 | 0 | 16.8 | 572.8 | 572.9 | 0.1 | 0.01 | 0.017 | 6.655 | 0.003 | 727.5% | 573.2 | 0 | 0.357 | 6.988 | 0.4 | -0.076 | 0.051 | 186.8% | -176.54 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.074 | 98 | 60 | 0 | 20.3 | 77.7 | 81.1 | 3.4 | -0.23 | 3.665 | 1.306 | 2 | 3.563% | 81.5 | -0.3 | 4.149 | 1.377 | 3.8 | -0.076 | 2 | 3.274% | -2.51 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | GT | -0.074 | 233 | 150 | 12 | 8.2 | 212.8 | 213.7 | 0.9 | -0.37 | 1.252 | 2.698 | 0.464 | 31.96% | 213.7 | -0.5 | 1.346 | 2.828 | 0.9 | -0.076 | 0.476 | 32.82% | -29.13 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.074 | 232 | 150 | 12 | 10.4 | 209.6 | 211.7 | 2.1 | -0.42 | 2.541 | 2.662 | 0.955 | 13.64% | 211.9 | -0.6 | 2.953 | 2.79 | 2.3 | -0.076 | 1.058 | 12.79% | -11.23 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.074 | 230 | 150 | 12 | 11.2 | 206.8 | 209.4 | 2.6 | -0.56 | 3.186 | 2.619 | 1.217 | 10.92% | 209.6 | -0.8 | 3.554 | 2.745 | 2.8 | -0.076 | 1.295 | 10.41% | -9.1 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.074 | 232 | 150 | 12 | 8.2 | 211.8 | 212.2 | 0.4 | -0.42 | 0.901 | 2.68 | 0.336 | 71.6% | 212.7 | -0.6 | 1.49 | 2.808 | 0.9 | -0.076 | 0.53 | 32.68% | -28.99 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.074 | 235 | 150 | 5 | 9.9 | 220.1 | 223 | 2.9 | 0.48 | 2.464 | 2.767 | 0.89 | 10% | 223 | 0.7 | 2.219 | 2.9 | 2.9 | -0.076 | 0.765 | 10.27% | -9.35 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.074 | 244 | 110 | 12 | 10 | 222 | 224.2 | 2.2 | -0.58 | 2.763 | 2.792 | 0.99 | 13.69% | 224.7 | -0.8 | 3.534 | 2.926 | 2.7 | -0.076 | 1.208 | 11.46% | -10.13 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.074 | 104 | 35 | 0 | 42.4 | 61.6 | 59.2 | -2.4 | -3.01 | 0.625 | 1.386 | 0.451 | -5.356% | 60.6 | -4.2 | 3.271 | 1.461 | -1 | -0.076 | 2 | -13.2% | 7.57 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.074 | 820 | 300 | 0 | 305.2 | 514.8 | 520.8 | 6 | 0.26 | 5.684 | 12.327 | 0.461 | 16.86% | 519.3 | 0.4 | 4.058 | 12.92 | 4.5 | -0.076 | 0.314 | 23.09% | -14.1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.074 | 810 | 300 | 0 | 33.8 | 776.2 | 796.1 | 19.9 | 1.3 | 18.629 | 12.177 | 1.53 | 5.022% | 793.6 | 1.8 | 15.59 | 12.762 | 17.4 | -0.076 | 1.222 | 5.898% | -5.5 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.074 | 535 | 210 | 0 | 13.6 | 521.4 | 522.1 | 0.7 | -0.33 | 0.986 | 8.043 | 0.123 | 94.3% | 522.5 | -0.5 | 1.534 | 8.429 | 1.1 | -0.076 | 0.182 | 61.63% | -58.43 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 671 | 419 | 49 | 45.8 | 576.2 | 582.2 | 6 | -0.06 | 6.068 | 7.021 | 0.864 | 13.8% | 586.3 | -0.1 | 10.154 | 7.372 | 10.1 | -0.076 | 1.377 | 8.418% | -7.03 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 711.1 | 460.1 | 22.2 | 83.5 | 605.4 | 619.1 | 13.7 | -0.24 | 13.856 | 7.776 | 1.782 | 6.404% | 618.9 | -0.3 | 13.785 | 8.165 | 13.5 | -0.076 | 1.688 | 6.674% | -5.53 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 712.4 | 448 | 31.6 | 122.3 | 558.5 | 569.6 | 11.1 | -0.77 | 11.868 | 7.684 | 1.544 | 7.918% | 574.7 | -1.1 | 17.224 | 8.069 | 16.2 | -0.076 | 2 | 5.572% | -4.25 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.074 | 49.5 | 24 | 0 | 9.7 | 39.8 | 41.1 | 1.3 | -0.1 | 1.373 | 0.66 | 2 | 4.718% | 43.2 | -0.1 | 3.546 | 0.696 | 3.4 | -0.076 | 2 | 1.852% | -1.44 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 48.5 | 24 | 0 | 10.2 | 38.3 | 39.8 | 1.5 | 0.03 | 1.455 | 0.647 | 2 | 4.007% | 41.7 | 0 | 3.352 | 0.682 | 3.4 | -0.076 | 2 | 1.815% | -1.38 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 41.3 | 20 | 0 | 9.9 | 31.4 | 32.4 | 1 | -0.26 | 1.237 | 0.551 | 2 | 5.122% | 33.1 | -0.4 | 2.045 | 0.58 | 1.7 | -0.076 | 2 | 3.094% | -2.26 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 473.2 | 230 | 0 | 76.7 | 396.5 | 405.4 | 8.9 | 0 | 8.98 | 5.341 | 1.681 | 6.561% | 407.1 | 0 | 10.643 | 5.609 | 10.6 | -0.076 | 1.898 | 5.657% | -4.61 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 115 | 50 | 0 | 33.5 | 81.5 | 83 | 1.5 | -1.65 | 3.196 | 1.298 | 2 | 9.474% | 82.9 | -2.3 | 3.752 | 1.363 | 1.4 | -0.076 | 2 | 10.42% | -7.16 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.074 | 37 | 18 | 0 | 10.4 | 26.6 | 23.2 | -3.4 | -4.55 | 1.166 | 0.493 | 2 | -1.35% | 22.8 | -6.3 | 2.526 | 0.52 | -3.8 | -0.076 | 2 | -1.241% | 0.86 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | FOSS | -0.074 | 57 | 15 | 0 | 41.6 | 15.4 | 16.6 | 1.2 | -0.3 | 1.458 | 0.607 | 2 | 5.882% | 16.1 | -0.4 | 1.068 | 0.636 | 0.7 | -0.076 | 1.678 | 10.35% | -2.67 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 845 | 465 | 0 | 243.9 | 601.1 | 613.2 | 12.1 | -5.29 | 17.344 | 9.538 | 1.818 | 8.615% | 616.9 | -7.4 | 23.209 | 10.015 | 15.8 | -0.076 | 2 | 6.776% | -4.69 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 258 | 165 | 0 | 46.6 | 211.4 | 215.6 | 4.2 | 0 | 4.174 | 2.912 | 1.433 | 7.583% | 217.5 | 0 | 6.137 | 3.058 | 6.1 | -0.076 | 2 | 5.362% | -4.27 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 329 | 185 | 0 | 34.9 | 294.1 | 299.7 | 5.6 | -0.16 | 5.717 | 3.714 | 1.539 | 7.251% | 300.6 | -0.2 | 6.706 | 3.9 | 6.5 | -0.076 | 1.72 | 6.416% | -5.58 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 684 | 300 | 40 | 182.6 | 461.4 | 479.2 | 17.8 | 0.86 | 16.914 | 7.27 | 2 | 4.741% | 474 | 1.2 | 11.356 | 7.634 | 12.6 | -0.076 | 1.488 | 6.878% | -4.51 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.067 | 87.1 | 0 | 0 | 30.8 | 56.3 | 57.6 | 1.3 | 1.04 | 0.307 | 1.142 | 0.269 | 7.503% | 58.6 | 1.4 | 0.897 | 1.168 | 2.3 | -0.068 | 0.768 | 4.304% | -2.72 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | LIG | FOSS | -0.067 | 606 | 220 | 0 | 375.9 | 230.1 | 235.9 | 5.8 | -0.58 | 6.453 | 7.948 | 0.812 | 11.67% | 234.8 | -0.8 | 5.507 | 8.126 | 4.7 | -0.068 | 0.678 | 14.62% | -5.46 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.067 | 602 | 220 | 0 | 317 | 285 | 289.4 | 4.4 | -0.81 | 5.149 | 7.896 | 0.652 | 15.28% | 288.3 | -1.1 | 4.402 | 8.072 | 3.3 | -0.068 | 0.545 | 20.68% | -9.64 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.067 | 459 | 300 | 0 | 147.2 | 311.8 | 318.5 | 6.7 | -0.33 | 7.025 | 4.493 | 1.564 | 7.654% | 322.2 | -0.5 | 10.831 | 4.598 | 10.4 | -0.068 | 2 | 5.005% | -3.35 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.067 | 117.6 | 0 | 0 | 105.5 | 12.1 | 12.2 | 0.1 | 0.06 | 0.096 | 1.542 | 0.062 | 131.6% | 12.2 | 0.1 | 0.061 | 1.577 | 0.1 | -0.068 | 0.039 | 133.6% | -13.23 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.067 | 253 | 97 | 66 | 84.2 | 102.8 | 107.4 | 4.6 | 0 | 4.594 | 1.83 | 2 | 6.148% | 107.4 | 0 | 4.6 | 1.873 | 4.6 | -0.068 | 2 | 6.239% | -2.49 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.067 | 560 | 135 | 0 | 416.8 | 143.2 | 148.3 | 5.1 | -0.24 | 5.39 | 5.509 | 0.978 | 12.27% | 149.9 | -0.3 | 7.071 | 5.632 | 6.7 | -0.068 | 1.256 | 9.477% | -2.38 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.067 | 785 | 300 | 0 | 479.2 | 305.8 | 315.3 | 9.5 | 0.29 | 9.244 | 7.413 | 1.247 | 9.23% | 316.5 | 0.4 | 10.358 | 7.579 | 10.7 | -0.068 | 1.367 | 8.317% | -3.19 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.067 | 420 | 125 | 0 | 280.5 | 139.5 | 142.1 | 2.6 | -0.03 | 2.649 | 3.838 | 0.69 | 18.05% | 141.9 | 0 | 2.47 | 3.924 | 2.4 | -0.068 | 0.63 | 19.85% | -6.48 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.067 | 417 | 125 | 0 | 278.2 | 138.8 | 142.9 | 4.1 | 0.52 | 3.587 | 3.809 | 0.942 | 11.36% | 141.8 | 0.7 | 2.236 | 3.894 | 3 | -0.068 | 0.574 | 15.76% | -5.16 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.067 | 241 | 165 | 18 | 56.5 | 166.5 | 170 | 3.5 | 0.12 | 3.38 | 2.183 | 1.549 | 7.697% | 170.1 | 0.2 | 3.422 | 2.234 | 3.6 | -0.068 | 1.532 | 7.595% | -5.16 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.067 | 746 | 93 | 0 | 652.1 | 93.9 | 102.7 | 8.8 | -0.28 | 9.121 | 4.051 | 2 | 9.473% | 104.5 | -0.4 | 10.986 | 4.212 | 10.6 | -0.068 | 2 | 7.981% | -0.98 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.067 | 55 | 10 | 25 | 17.6 | 12.4 | 14.4 | 2 | -0.24 | 2.265 | 0.294 | 2 | 3.085% | 13 | -0.3 | 0.957 | 0.301 | 0.6 | -0.068 | 2 | 10.44% | -2.26 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.067 | 615 | 300 | 0 | 315 | 300 | 312.2 | 12.2 | -0.53 | 12.719 | 7.051 | 1.804 | 5.631% | 315.7 | -0.7 | 16.439 | 7.209 | 15.7 | -0.068 | 2 | 4.441% | -2.13 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.067 | 322 | 250 | 0 | 61.6 | 260.4 | 266.7 | 6.3 | -0.32 | 6.625 | 3.152 | 2 | 5.712% | 268.1 | -0.5 | 8.095 | 3.226 | 7.7 | -0.068 | 2 | 4.743% | -3.77 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.067 | 50 | 22 | 6 | 19.5 | 24.5 | 28.6 | 4.1 | 0.5 | 3.605 | 0.431 | 2 | 1.369% | 31.8 | 0.7 | 6.582 | 0.441 | 7.3 | -0.068 | 2 | 0.7801% | -0.37 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.067 | 211 | 143 | 12 | 53.8 | 145.2 | 146 | 0.8 | 0.18 | 0.637 | 1.948 | 0.327 | 29.49% | 145.4 | 0.2 | -0.032 | 1.993 | 0.2 | -0.068 | 0 | 119.7% | -80.93 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.067 | 590.7 | 152.7 | 0 | 435.9 | 154.8 | 165.2 | 10.4 | 0.11 | 10.275 | 5.487 | 1.873 | 6.345% | 165.2 | 0.1 | 10.318 | 5.61 | 10.4 | -0.068 | 1.839 | 6.44% | -1.66 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.067 | 590.7 | 152.7 | 0 | 435.9 | 154.8 | 165.2 | 10.4 | 0.11 | 10.275 | 5.487 | 1.873 | 6.345% | 165.2 | 0.1 | 10.318 | 5.61 | 10.4 | -0.068 | 1.839 | 6.44% | -1.66 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.067 | 595.2 | 152.7 | 0 | 421.7 | 173.5 | 182 | 8.5 | -0.63 | 9.14 | 5.476 | 1.669 | 7.823% | 182.5 | -0.9 | 9.872 | 5.599 | 9 | -0.068 | 1.763 | 7.498% | -2.15 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.067 | 595.2 | 152.7 | 0 | 421.7 | 173.5 | 182 | 8.5 | -0.63 | 9.14 | 5.476 | 1.669 | 7.823% | 182.5 | -0.9 | 9.872 | 5.599 | 9 | -0.068 | 1.763 | 7.498% | -2.15 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.067 | 419.9 | 180.3 | 0 | 234.9 | 185 | 191.5 | 6.5 | 0.85 | 5.554 | 4.75 | 1.169 | 7.218% | 191.1 | 1.2 | 4.865 | 4.856 | 6.1 | -0.068 | 1.002 | 7.806% | -3.38 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.067 | 486 | 272 | 10 | 23.1 | 452.9 | 455.5 | 2.6 | -0.06 | 2.647 | 4.659 | 0.568 | 20.88% | 455 | -0.1 | 2.182 | 4.768 | 2.1 | -0.068 | 0.458 | 26.24% | -24.07 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.067 | 274.9 | 175 | 44 | 55.2 | 175.7 | 179 | 3.3 | -0.6 | 3.89 | 2.261 | 1.721 | 9.311% | 182.8 | -0.8 | 7.922 | 2.314 | 7.1 | -0.068 | 2 | 4.392% | -2.76 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.067 | 470 | 180 | 0 | 290 | 180 | 187 | 7 | 0.04 | 6.918 | 2.225 | 2 | 7.506% | 184.5 | 0.1 | 4.417 | 2.313 | 4.5 | -0.068 | 1.909 | 11.85% | -4.45 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.067 | 470 | 180 | 0 | 290 | 180 | 187 | 7 | 0.04 | 6.918 | 2.225 | 2 | 7.506% | 184.5 | 0.1 | 4.417 | 2.313 | 4.5 | -0.068 | 1.909 | 11.85% | -4.45 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.067 | 470 | 180 | 0 | 290 | 180 | 187 | 7 | 0.04 | 6.918 | 2.225 | 2 | 7.506% | 184.5 | 0.1 | 4.417 | 2.313 | 4.5 | -0.068 | 1.909 | 11.85% | -4.45 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.067 | 470 | 180 | 0 | 290 | 180 | 187 | 7 | 0.04 | 6.918 | 2.225 | 2 | 7.506% | 184.5 | 0.1 | 4.417 | 2.313 | 4.5 | -0.068 | 1.909 | 11.85% | -4.45 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.067 | 234 | 150 | 0 | 82.4 | 151.6 | 155.7 | 4.1 | -0.3 | 4.445 | 2.504 | 1.775 | 6.38% | 156 | -0.4 | 4.844 | 2.56 | 4.4 | -0.068 | 1.892 | 6.034% | -3.84 | 0.017 | 0.05 | 5.933% | 5.163%
Wind | WND | WIND | -0.067 | 151.7 | 0 | 0 | 48.7 | 103 | 102 | -1 | -5.64 | 4.667 | 1.989 | 2 | -16.97% | 102.3 | -7.8 | 7.167 | 2.034 | -0.7 | -0.068 | 2 | -24.6% | 16.39 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.067 | 173.6 | 0 | 40 | 125.4 | 8.2 | 10.1 | 1.9 | 0.78 | 1.108 | 1.308 | 0.847 | 10.22% | 7.4 | 1.1 | -1.863 | 1.338 | -0.8 | -0.068 | 0 | -24.63% | 1.11 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.067 | 834 | 259 | 0 | 573.1 | 260.9 | 276.9 | 16 | 0 | 16.033 | 7.022 | 2 | 5.822% | 278.6 | 0 | 17.747 | 7.179 | 17.7 | -0.068 | 2 | 5.342% | -1.64 | 0.017 | 0.05 | 6.284% | 5.784%
Wind | WND | WIND | -0.067 | 87 | 0 | 0 | 10.3 | 76.7 | 79.5 | 2.8 | -0.67 | 3.457 | 1.141 | 2 | 3.48% | 80.1 | -0.9 | 4.325 | 1.166 | 3.4 | -0.068 | 2 | 2.908% | -2.51 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.067 | 42.1 | 0 | 0 | 7.8 | 34.3 | 33.9 | -0.4 | -0.42 | 0.108 | 0.552 | 0.195 | -11.82% | 33.9 | -0.6 | 0.254 | 0.564 | -0.4 | -0.068 | 0.45 | -12% | 9.5 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | GT | -0.067 | 243 | 150 | 0 | 91.3 | 151.7 | 155.9 | 4.2 | -0.12 | 4.379 | 2.239 | 1.956 | 6.467% | 155.8 | -0.2 | 4.28 | 2.289 | 4.1 | -0.068 | 1.87 | 6.724% | -4.12 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.067 | 750 | 300 | 0 | 246.2 | 503.8 | 511 | 7.2 | 0.34 | 6.855 | 9.837 | 0.697 | 11.64% | 510.6 | 0.5 | 6.325 | 10.057 | 6.8 | -0.068 | 0.629 | 12.5% | -8.27 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.067 | 805 | 300 | 0 | 413.1 | 391.9 | 393.7 | 1.8 | -3.75 | 5.52 | 10.558 | 0.523 | 49.96% | 392.1 | -5.2 | 5.399 | 10.794 | 0.2 | -0.068 | 0.5 | 456.3% | -218.67 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.067 | 316 | 208 | 22 | 85.1 | 208.9 | 212.1 | 3.2 | -0.41 | 3.605 | 2.878 | 1.253 | 11.04% | 213.5 | -0.6 | 5.16 | 2.945 | 4.6 | -0.068 | 1.752 | 7.792% | -5.06 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.067 | 51.5 | 0 | 0 | 11.8 | 39.7 | 40.2 | 0.5 | -0.03 | 0.53 | 0.675 | 0.785 | 11.56% | 40.2 | 0 | 0.551 | 0.69 | 0.5 | -0.068 | 0.798 | 11.73% | -8.81 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | SUB | FOSS | -0.067 | 650 | 189.8 | 0 | 459.4 | 190.6 | 196.3 | 5.7 | -0.64 | 6.315 | 4.841 | 1.304 | 12.74% | 199.4 | -0.9 | 9.693 | 4.95 | 8.8 | -0.068 | 1.958 | 8.374% | -2.42 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.067 | 650 | 189.8 | 0 | 459.4 | 190.6 | 196.3 | 5.7 | -0.64 | 6.315 | 4.841 | 1.304 | 12.74% | 199.4 | -0.9 | 9.693 | 4.95 | 8.8 | -0.068 | 1.958 | 8.374% | -2.42 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.067 | 650 | 189.8 | 0 | 459.4 | 190.6 | 196.3 | 5.7 | -0.64 | 6.315 | 4.841 | 1.304 | 12.74% | 199.4 | -0.9 | 9.693 | 4.95 | 8.8 | -0.068 | 1.958 | 8.374% | -2.42 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.067 | 650 | 189.8 | 0 | 459.4 | 190.6 | 196.3 | 5.7 | -0.64 | 6.315 | 4.841 | 1.304 | 12.74% | 199.4 | -0.9 | 9.693 | 4.95 | 8.8 | -0.068 | 1.958 | 8.374% | -2.42 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.067 | 650 | 189.8 | 0 | 459.4 | 190.6 | 196.3 | 5.7 | -0.64 | 6.315 | 4.841 | 1.304 | 12.74% | 199.4 | -0.9 | 9.693 | 4.95 | 8.8 | -0.068 | 1.958 | 8.374% | -2.42 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.067 | 386.5 | 190 | 2.9 | 167.8 | 215.8 | 222.7 | 6.9 | 0.53 | 6.402 | 3.755 | 1.705 | 6.259% | 223.8 | 0.7 | 7.275 | 3.843 | 8 | -0.068 | 1.893 | 5.479% | -3.01 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.067 | 704 | 420 | 0 | 254.3 | 449.7 | 457.8 | 8.1 | 0.85 | 7.211 | 6.891 | 1.046 | 9.709% | 457.6 | 1.2 | 6.743 | 7.052 | 7.9 | -0.068 | 0.956 | 10.1% | -6.35 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.067 | 139.8 | 0 | 0 | 85.9 | 53.9 | 62.8 | 8.9 | 3.42 | 5.46 | 1.834 | 2 | 1.757% | 66.2 | 4.8 | 7.495 | 1.875 | 12.3 | -0.068 | 2 | 1.29% | -0.49 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.067 | 276 | 118 | 65 | 88.4 | 122.6 | 125.1 | 2.5 | -0.36 | 2.846 | 2.065 | 1.378 | 12.34% | 128.6 | -0.5 | 6.48 | 2.114 | 6 | -0.068 | 2 | 5.218% | -2.28 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.067 | 940 | 322 | 0 | 596.3 | 343.7 | 353.9 | 10.2 | 0.19 | 10.038 | 5.181 | 1.938 | 10.29% | 358.4 | 0.3 | 14.462 | 5.296 | 14.7 | -0.068 | 2 | 7.249% | -2.61 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.067 | 940 | 322 | 0 | 596.3 | 343.7 | 353.9 | 10.2 | 0.19 | 10.038 | 5.181 | 1.938 | 10.29% | 358.4 | 0.3 | 14.462 | 5.296 | 14.7 | -0.068 | 2 | 7.249% | -2.61 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.067 | 940 | 322 | 0 | 596.3 | 343.7 | 353.9 | 10.2 | 0.19 | 10.038 | 5.181 | 1.938 | 10.29% | 358.4 | 0.3 | 14.462 | 5.296 | 14.7 | -0.068 | 2 | 7.249% | -2.61 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.067 | 940 | 322 | 0 | 596.3 | 343.7 | 353.9 | 10.2 | 0.19 | 10.038 | 5.181 | 1.938 | 10.29% | 358.4 | 0.3 | 14.462 | 5.296 | 14.7 | -0.068 | 2 | 7.249% | -2.61 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.067 | 620 | 295 | 0 | 283.2 | 336.8 | 340.6 | 3.8 | -0.16 | 3.98 | 8.132 | 0.489 | 18.23% | 340.9 | -0.2 | 4.308 | 8.314 | 4.1 | -0.068 | 0.518 | 17.15% | -9.17 | 0.017 | 0.05 | 6.284% | 5.784%
Wind | WND | WIND | -0.067 | 149 | 0 | 0 | 5.7 | 143.3 | 143 | -0.3 | -1.02 | 0.734 | 1.954 | 0.376 | -55.56% | 143.3 | -1.4 | 1.436 | 1.997 | 0 | -0.068 | 0.719 | 0% |  | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | BIT | FOSS | -0.067 | 664 | 156 | 0 | 468.7 | 195.3 | 205.1 | 9.8 | 0.79 | 8.983 | 8.04 | 1.117 | 7.569% | 205.6 | 1.1 | 9.192 | 8.22 | 10.3 | -0.068 | 1.118 | 7.309% | -2.11 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.067 | 663 | 156 | 0 | 435.6 | 227.4 | 236.7 | 9.3 | -0.21 | 9.464 | 7.934 | 1.193 | 7.964% | 236.7 | -0.3 | 9.626 | 8.111 | 9.3 | -0.068 | 1.187 | 8.083% | -2.73 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.067 | 577 | 159 | 0 | 417.3 | 159.7 | 170.3 | 10.6 | -0.4 | 11.047 | 7.009 | 1.576 | 6.081% | 170.2 | -0.6 | 11.087 | 7.166 | 10.5 | -0.068 | 1.547 | 6.231% | -1.7 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.067 | 592 | 307 | 0 | 284 | 308 | 315.2 | 7.2 | 0.02 | 7.191 | 6.721 | 1.07 | 9.185% | 315.1 | 0 | 7.03 | 6.872 | 7.1 | -0.068 | 1.023 | 9.454% | -4.84 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.067 | 690 | 300 | 40 | 341.4 | 308.6 | 316.7 | 8.1 | 0 | 8.032 | 6.363 | 1.262 | 9.516% | 318.7 | 0 | 10.047 | 6.512 | 10.1 | -0.068 | 1.543 | 7.745% | -3.41 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.112 | 513.6 | 275 | 12 | 123.3 | 378.3 | 392 | 13.7 | 0 | 13.711 | 10.306 | 1.33 | 7% | 405.1 | 0 | 26.78 | 10.022 | 26.8 | -0.11 | 2 | 3.514% | -2.63 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.112 | 459 | 300 | 0 | 17.7 | 441.3 | 453 | 11.7 | -0.11 | 11.792 | 9.43 | 1.25 | 7.325% | 452.6 | -0.2 | 11.431 | 9.171 | 11.3 | -0.11 | 1.246 | 7.449% | -7.29 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.112 | 253 | 91 | 25 | 15.1 | 212.9 | 214.1 | 1.2 | -0.94 | 2.107 | 4.684 | 0.45 | 39.38% | 215.8 | -1.3 | 4.171 | 4.556 | 2.9 | -0.11 | 0.916 | 16% | -13.69 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.112 | 204 | 153 | 0 | 40.7 | 163.3 | 168 | 4.7 | -0.17 | 4.825 | 4.191 | 1.151 | 8.108% | 167.3 | -0.2 | 4.272 | 4.076 | 4 | -0.11 | 1.048 | 9.357% | -7.61 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.112 | 560 | 405 | 0 | 138.6 | 421.4 | 434.7 | 13.3 | -1.39 | 14.607 | 12.827 | 1.139 | 7.862% | 442.6 | -1.9 | 23.06 | 12.482 | 21.2 | -0.11 | 1.848 | 4.844% | -3.71 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.112 | 670 | 300 | 0 | 16 | 654 | 669.7 | 15.7 | 1.06 | 14.603 | 15.829 | 0.923 | 7.968% | 676.2 | 1.5 | 20.697 | 15.403 | 22.2 | -0.11 | 1.344 | 5.534% | -5.5 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.112 | 420 | 180 | 0 | 177.4 | 242.6 | 255.6 | 13 | 2.91 | 10.074 | 8.122 | 1.24 | 6.033% | 256.9 | 4 | 10.223 | 7.904 | 14.3 | -0.11 | 1.293 | 5.387% | -3.16 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.112 | 417 | 180 | 0 | 218.9 | 198.1 | 208.4 | 10.3 | -0.22 | 10.519 | 7.786 | 1.351 | 7.56% | 211.3 | -0.3 | 13.497 | 7.576 | 13.2 | -0.11 | 1.781 | 5.794% | -2.8 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.112 | 236.7 | 165 | 18 | 52.1 | 166.6 | 173.5 | 6.9 | 0.47 | 6.421 | 4.493 | 1.429 | 6.408% | 172.5 | 0.7 | 5.286 | 4.37 | 5.9 | -0.11 | 1.21 | 7.36% | -5.27 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.112 | 746 | 93 | 0 | 651 | 95 | 111.1 | 16.1 | 0.08 | 15.944 | 11.587 | 1.376 | 8.653% | 111.8 | 0.1 | 16.655 | 11.191 | 16.8 | -0.11 | 1.488 | 8.144% | -1.05 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.112 | 321 | 244 | 0 | 37.6 | 283.4 | 291.8 | 8.4 | -0.29 | 8.705 | 6.595 | 1.32 | 7.137% | 295.8 | -0.4 | 12.838 | 6.414 | 12.4 | -0.11 | 2 | 4.748% | -4.26 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.112 | 48 | 20 | 6 | 19.9 | 22.1 | 27.6 | 5.5 | 0.5 | 4.984 | 0.863 | 2 | 1.634% | 28.6 | 0.7 | 5.766 | 0.839 | 6.5 | -0.11 | 2 | 1.358% | -0.63 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.112 | 475 | 272 | 10 | 12.1 | 452.9 | 456.5 | 3.6 | 0.06 | 3.5 | 9.554 | 0.366 | 24.64% | 456.3 | 0.1 | 3.289 | 9.291 | 3.4 | -0.11 | 0.354 | 25.62% | -24.86 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.112 | 231 | 150 | 0 | 38.9 | 192.1 | 196.9 | 4.8 | 0 | 4.778 | 5.523 | 0.865 | 8.989% | 198.2 | 0 | 6.098 | 5.375 | 6.1 | -0.11 | 1.135 | 6.947% | -5.87 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.112 | 237 | 150 | 0 | 44.4 | 192.6 | 203.2 | 10.6 | 3.52 | 7.083 | 5.675 | 1.248 | 4.176% | 204.6 | 4.9 | 7.061 | 5.522 | 12 | -0.11 | 1.279 | 3.623% | -2.99 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.112 | 239 | 150 | 0 | 30.4 | 208.6 | 213.7 | 5.1 | -0.42 | 5.544 | 5.998 | 0.924 | 8.753% | 214.2 | -0.6 | 6.194 | 5.837 | 5.6 | -0.11 | 1.061 | 7.829% | -6.95 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.112 | 169.2 | 0 | 24 | 27.9 | 117.3 | 131.2 | 13.9 | 0.52 | 13.396 | 2.984 | 2 | 2.274% | 138.6 | 0.7 | 20.509 | 2.902 | 21.3 | -0.11 | 2 | 1.458% | -1.03 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.112 | 834 | 259 | 0 | 557.6 | 276.4 | 307.7 | 31.3 | -0.13 | 31.441 | 14.418 | 2 | 4.975% | 308.6 | -0.2 | 32.351 | 14.03 | 32.2 | -0.11 | 2 | 4.749% | -1.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.112 | 836 | 258 | 0 | 550 | 286 | 317.9 | 31.9 | -2.98 | 34.923 | 14.89 | 2 | 4.893% | 320.5 | -4.1 | 38.663 | 14.489 | 34.5 | -0.11 | 2 | 4.443% | -1.55 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.112 | 99 | 64 | 0 | 20.5 | 78.5 | 84.5 | 6 | 0 | 5.992 | 2.395 | 2 | 3.085% | 84.7 | 0 | 6.189 | 2.323 | 6.2 | -0.11 | 2 | 2.932% | -2.36 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.112 | 522 | 339 | 0 | 63.2 | 458.8 | 476.7 | 17.9 | -0.41 | 18.292 | 10.725 | 1.706 | 5.445% | 485.6 | -0.6 | 27.36 | 10.43 | 26.8 | -0.11 | 2 | 3.572% | -3.19 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.112 | 518 | 310 | 40.4 | 24.4 | 453.2 | 467 | 13.8 | -0.12 | 13.881 | 9.813 | 1.415 | 7.009% | 465.8 | -0.2 | 12.73 | 9.543 | 12.6 | -0.11 | 1.334 | 7.539% | -6.71 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.112 | 519 | 316.6 | 32.4 | 33.2 | 453.4 | 466.5 | 13.1 | 0.14 | 12.961 | 9.998 | 1.296 | 7.398% | 465.2 | 0.2 | 11.586 | 9.723 | 11.8 | -0.11 | 1.192 | 8.066% | -7.17 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.112 | 237 | 150 | 0 | 38 | 199 | 206.1 | 7.1 | -0.08 | 7.13 | 4.844 | 1.472 | 6.235% | 206.4 | -0.1 | 7.475 | 4.713 | 7.4 | -0.11 | 1.586 | 5.875% | -5.02 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.112 | 246 | 110 | 0 | 21.9 | 224.1 | 229.3 | 5.2 | 0.02 | 5.225 | 5.349 | 0.977 | 8.836% | 229.9 | 0 | 5.793 | 5.205 | 5.8 | -0.11 | 1.113 | 7.781% | -7.21 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.112 | 755 | 300 | 0 | 124.8 | 630.2 | 640.4 | 10.2 | -5.56 | 15.735 | 20.288 | 0.776 | 13.82% | 637 | -7.7 | 14.528 | 19.742 | 6.8 | -0.11 | 0.736 | 20.36% | -17.3 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.112 | 825 | 300 | 0 | 212.9 | 612.1 | 616 | 3.9 | -7.3 | 11.215 | 22.169 | 0.506 | 39.49% | 612.6 | -10.2 | 10.677 | 21.573 | 0.5 | -0.11 | 0.495 | 302.6% | -228.46 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.112 | 805 | 300 | 0 | 66.4 | 738.6 | 752.2 | 13.6 | -5.92 | 19.581 | 21.631 | 0.905 | 11.05% | 749 | -8.2 | 18.631 | 21.05 | 10.4 | -0.11 | 0.885 | 14.19% | -13.25 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.112 | 805 | 300 | 0 | 181.1 | 623.9 | 633.2 | 9.3 | 0.65 | 8.645 | 21.631 | 0.4 | 16.16% | 637.5 | 0.9 | 12.77 | 21.05 | 13.6 | -0.11 | 0.607 | 10.85% | -8.56 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.112 | 650 | 189.8 | 0 | 407.5 | 242.5 | 261.1 | 18.6 | 0.05 | 18.452 | 9.559 | 1.93 | 6.525% | 262.1 | 0.1 | 19.506 | 9.302 | 19.6 | -0.11 | 2 | 6.081% | -2.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.112 | 650 | 189.8 | 0 | 407.5 | 242.5 | 261.1 | 18.6 | 0.05 | 18.452 | 9.559 | 1.93 | 6.525% | 262.1 | 0.1 | 19.506 | 9.302 | 19.6 | -0.11 | 2 | 6.081% | -2.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.112 | 650 | 189.8 | 0 | 407.5 | 242.5 | 261.1 | 18.6 | 0.05 | 18.452 | 9.559 | 1.93 | 6.525% | 262.1 | 0.1 | 19.506 | 9.302 | 19.6 | -0.11 | 2 | 6.081% | -2.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.112 | 650 | 189.8 | 0 | 407.5 | 242.5 | 261.1 | 18.6 | 0.05 | 18.452 | 9.559 | 1.93 | 6.525% | 262.1 | 0.1 | 19.506 | 9.302 | 19.6 | -0.11 | 2 | 6.081% | -2.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.112 | 650 | 189.8 | 0 | 407.5 | 242.5 | 261.1 | 18.6 | 0.05 | 18.452 | 9.559 | 1.93 | 6.525% | 262.1 | 0.1 | 19.506 | 9.302 | 19.6 | -0.11 | 2 | 6.081% | -2.31 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.112 | 484.3 | 230 | 0 | 130.2 | 354.1 | 371.3 | 17.2 | -3.72 | 20.979 | 9.95 | 2 | 5.258% | 394.1 | -5.2 | 45.215 | 9.677 | 40 | -0.11 | 2 | 2.22% | -1.65 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.112 | 704 | 420 | 0 | 95.9 | 608.1 | 634.7 | 26.6 | 0.16 | 26.447 | 14.464 | 1.828 | 4.941% | 634.9 | 0.2 | 26.613 | 14.066 | 26.8 | -0.11 | 1.892 | 4.817% | -4.23 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.112 | 218.7 | 118 | 0 | 9.6 | 209.1 | 214.9 | 5.8 | -0.27 | 5.99 | 4.493 | 1.333 | 7.044% | 215.2 | -0.4 | 6.429 | 4.37 | 6.1 | -0.11 | 1.471 | 6.578% | -6.39 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.112 | 81.6 | 0 | 0 | 5.8 | 75.8 | 77.8 | 2 | -0.12 | 2.128 | 2.193 | 0.97 | 7.63% | 78.7 | -0.2 | 3.043 | 2.134 | 2.9 | -0.11 | 1.426 | 5.168% | -4.87 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.112 | 264 | 100 | 20 | 77.3 | 166.7 | 174 | 7.3 | -1.54 | 8.799 | 5.013 | 1.755 | 6.755% | 179.3 | -2.1 | 14.722 | 4.875 | 12.6 | -0.11 | 2 | 3.844% | -2.47 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.112 | 850 | 465 | 122.5 | 123.9 | 603.6 | 621.9 | 18.3 | -0.54 | 18.861 | 14.947 | 1.262 | 8.672% | 628.9 | -0.8 | 26.033 | 14.535 | 25.3 | -0.11 | 1.791 | 6.161% | -4.45 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.112 | 678 | 300 | 40 | 181.6 | 456.4 | 483 | 26.6 | -3.46 | 30.015 | 13.109 | 2 | 4.759% | 479.9 | -4.8 | 28.255 | 12.749 | 23.5 | -0.11 | 2 | 5.291% | -3.62 | 0.017 | 0.0578 | 5.933% | 5.163%
Hydro | WAT | HYDR | -0.08 | 30 | 24 | 0 | 5.3 | 24.7 | 25.3 | 0.6 | -0.14 | 0.687 | 0.355 | 1.933 | 6.761% | 26 | -0.2 | 1.458 | 0.354 | 1.3 | -0.08 | 2 | 3.121% | -2.49 | 0.034 | 0.05 | 0.2285% | 0.2528%
CombinedCycle | CC | COGN | -0.08 | 629.7 | 252 | 15 | 65.6 | 549.1 | 559.1 | 10 | -0.84 | 10.891 | 8.112 | 1.343 | 8.399% | 560.7 | -1.2 | 12.828 | 8.092 | 11.6 | -0.08 | 1.585 | 7.24% | -6.31 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 511.8 | 275 | 12 | 136.5 | 363.3 | 369.1 | 5.8 | -5.31 | 11.063 | 6.596 | 1.677 | 11.77% | 372.3 | -7.4 | 16.356 | 6.579 | 9 | -0.08 | 2 | 7.585% | -5.38 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.08 | 74.1 | 0 | 0 | 5.3 | 68.8 | 69.3 | 0.5 | -0.1 | 0.695 | 1.294 | 0.537 | 19.82% | 70.2 | -0.1 | 1.63 | 1.291 | 1.4 | -0.08 | 1.263 | 7.077% | -6.53 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.08 | 225 | 165 | 10 | 44.6 | 170.4 | 174.7 | 4.3 | 0.18 | 4.063 | 2.837 | 1.432 | 6.983% | 174.8 | 0.2 | 4.125 | 2.83 | 4.4 | -0.08 | 1.458 | 6.825% | -5.16 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.08 | 560 | 135 | 0 | 100.3 | 459.7 | 470.5 | 10.8 | -0.08 | 10.917 | 8.965 | 1.218 | 6.916% | 471.1 | -0.1 | 11.536 | 8.943 | 11.4 | -0.08 | 1.29 | 6.552% | -5.37 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 420 | 175 | 0 | 108.4 | 311.6 | 316.8 | 5.2 | -0.06 | 5.259 | 5.57 | 0.944 | 10.77% | 315.8 | -0.1 | 4.237 | 5.557 | 4.2 | -0.08 | 0.763 | 13.34% | -9.89 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 420 | 70 | 0 | 104.5 | 315.5 | 319.5 | 4 | -0.42 | 4.421 | 6.518 | 0.678 | 14.01% | 320.2 | -0.6 | 5.281 | 6.503 | 4.7 | -0.08 | 0.812 | 11.92% | -8.94 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 410 | 70 | 0 | 98.1 | 311.9 | 316.9 | 5 | 0 | 5.013 | 6.881 | 0.729 | 10.94% | 315.9 | 0 | 4.021 | 6.864 | 4 | -0.08 | 0.586 | 13.67% | -10.39 | 0.017 | 0.05 | 6.284% | 5.784%
Wind | WND | WIND | -0.08 | 73 | 0 | 0 | 5.7 | 67.3 | 67.4 | 0.1 | -4.72 | 4.809 | 1.276 | 2 | 97.62% | 67 | -6.6 | 6.282 | 1.273 | -0.3 | -0.08 | 2 | -32.54% | 29.82 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.08 | 316 | 237 | 0 | 44.5 | 271.5 | 279.2 | 7.7 | -0.1 | 7.854 | 4.17 | 1.883 | 5.476% | 280.9 | -0.1 | 9.554 | 4.16 | 9.4 | -0.08 | 2 | 4.485% | -3.85 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.08 | 105 | 12 | 0 | 92.5 | 12.5 | 14.1 | 1.6 | 0.58 | 1.044 | 1.818 | 0.575 | 8.768% | 14.1 | 0.8 | 0.785 | 1.813 | 1.6 | -0.08 | 0.433 | 8.768% | -1.02 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 315 | 50 | 0 | 28 | 287 | 300.6 | 13.6 | -0.43 | 13.958 | 4.486 | 2 | 3.09% | 301.1 | -0.6 | 14.652 | 4.475 | 14.1 | -0.08 | 2 | 2.981% | -2.71 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 420 | 50 | 0 | 27.5 | 392.5 | 404 | 11.5 | 0.35 | 11.184 | 6.227 | 1.796 | 4.872% | 404.1 | 0.5 | 11.094 | 6.212 | 11.6 | -0.08 | 1.786 | 4.83% | -4.51 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.08 | 148 | 80 | 0 | 41.8 | 106.2 | 111 | 4.8 | -0.02 | 4.843 | 2.304 | 2 | 4.117% | 111.1 | 0 | 4.934 | 2.298 | 4.9 | -0.08 | 2 | 4.033% | -2.88 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.08 | 327 | 136 | 0 | 42.6 | 284.4 | 290.6 | 6.2 | 0.21 | 6.07 | 4.315 | 1.407 | 7.037% | 292.3 | 0.3 | 7.644 | 4.305 | 7.9 | -0.08 | 1.776 | 5.523% | -4.8 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | STM | -0.08 | 316.1 | 54.9 | 0 | 60.8 | 255.3 | 261.4 | 6.1 | -0.01 | 6.142 | 5.292 | 1.161 | 6.914% | 261 | 0 | 5.682 | 5.279 | 5.7 | -0.08 | 1.076 | 7.399% | -5.97 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | COGN | -0.08 | 225 | 150 | 0 | 23 | 202 | 203 | 1 | 0.13 | 0.958 | 3.6 | 0.266 | 30.03% | 203.2 | 0.2 | 1.051 | 3.592 | 1.2 | -0.08 | 0.293 | 25.02% | -22.42 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.08 | 231 | 150 | 0 | 28.1 | 202.9 | 207 | 4.1 | -0.13 | 4.213 | 3.706 | 1.137 | 7.519% | 207.2 | -0.2 | 4.495 | 3.697 | 4.3 | -0.08 | 1.216 | 7.169% | -6.28 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.08 | 232 | 150 | 0 | 29 | 203 | 207.3 | 4.3 | -0.15 | 4.484 | 3.723 | 1.204 | 7.2% | 207.4 | -0.2 | 4.575 | 3.714 | 4.4 | -0.08 | 1.232 | 7.037% | -6.15 | 0.017 | 0.05 | 5.933% | 5.163%
Wind | WND | WIND | -0.08 | 45.4 | 0 | 0 | 9.3 | 36.1 | 36.8 | 0.7 | -2.36 | 3.041 | 0.794 | 2 | 8.688% | 37 | -3.3 | 4.135 | 0.792 | 0.9 | -0.08 | 2 | 6.757% | -5.32 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | FOSS | -0.08 | 435 | 120 | 0 | 274.6 | 160.4 | 170.6 | 10.2 | 0 | 10.246 | 6.737 | 1.521 | 5.689% | 170 | 0 | 9.6 | 6.72 | 9.6 | -0.08 | 1.428 | 6.045% | -2.22 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.08 | 834 | 259 | 0 | 85.7 | 748.3 | 761.6 | 13.3 | -0.32 | 13.639 | 9.802 | 1.391 | 8.363% | 763.1 | -0.4 | 15.235 | 9.779 | 14.8 | -0.08 | 1.558 | 7.515% | -6.74 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.08 | 836 | 259 | 0 | 30.8 | 805.2 | 830.6 | 25.4 | 0.05 | 25.437 | 10.205 | 2 | 4.39% | 832.2 | 0.1 | 26.99 | 10.18 | 27 | -0.08 | 2 | 4.129% | -3.98 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 511 | 331 | 0 | 15.5 | 495.5 | 501.1 | 5.6 | 0.53 | 5.121 | 6.743 | 0.759 | 12.17% | 501.5 | 0.7 | 5.275 | 6.727 | 6 | -0.08 | 0.784 | 11.36% | -11.01 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.08 | 118 | 15 | 0 | 101.5 | 16.5 | 17.8 | 1.3 | 0 | 1.246 | 1.172 | 1.063 | 12.15% | 18.2 | 0 | 1.662 | 1.168 | 1.7 | -0.08 | 1.423 | 9.288% | -1.26 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.08 | 228 | 150 | 0 | 21.8 | 206.2 | 210.5 | 4.3 | -0.21 | 4.458 | 3.202 | 1.392 | 7.076% | 210.7 | -0.3 | 4.743 | 3.195 | 4.5 | -0.08 | 1.485 | 6.762% | -6.1 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.08 | 227 | 150 | 0 | 22.9 | 204.1 | 208.3 | 4.2 | 0 | 4.154 | 3.174 | 1.309 | 7.213% | 208.7 | 0 | 4.547 | 3.166 | 4.6 | -0.08 | 1.436 | 6.586% | -5.91 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.08 | 224 | 150 | 0 | 23.6 | 200.4 | 204.4 | 4 | -0.12 | 4.145 | 3.108 | 1.334 | 7.474% | 204.8 | -0.2 | 4.581 | 3.1 | 4.4 | -0.08 | 1.478 | 6.794% | -6.07 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.08 | 227 | 150 | 0 | 20.9 | 206.1 | 210.2 | 4.1 | 0.01 | 4.036 | 3.188 | 1.266 | 7.389% | 210.8 | 0 | 4.68 | 3.18 | 4.7 | -0.08 | 1.472 | 6.446% | -5.84 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.08 | 229 | 150 | 0 | 16.5 | 212.5 | 216.3 | 3.8 | 0.04 | 3.755 | 3.154 | 1.19 | 8.043% | 216.6 | 0.1 | 4.05 | 3.147 | 4.1 | -0.08 | 1.287 | 7.454% | -6.9 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.08 | 238 | 110 | 0 | 22.5 | 215.5 | 220.2 | 4.7 | 0.17 | 4.52 | 3.3 | 1.37 | 6.758% | 220.2 | 0.2 | 4.46 | 3.292 | 4.7 | -0.08 | 1.355 | 6.758% | -6.11 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.08 | 205 | 40 | 0 | 60.2 | 144.8 | 145 | 0.2 | -1.17 | 1.435 | 3.236 | 0.444 | 136.8% | 143.8 | -1.6 | 0.694 | 3.228 | -1 | -0.08 | 0.215 | -27.36% | 19.28 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | LIG | FOSS | -0.08 | 740 | 300 | 0 | 99.6 | 640.4 | 656.6 | 16.2 | 0.46 | 15.678 | 12.931 | 1.212 | 6.092% | 652.8 | 0.6 | 11.766 | 12.9 | 12.4 | -0.08 | 0.912 | 7.959% | -6.88 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.08 | 535 | 210 | 0 | 13.8 | 521.2 | 522.2 | 1 | -0.54 | 1.601 | 9.349 | 0.171 | 71.36% | 519.5 | -0.7 | -0.903 | 9.326 | -1.7 | -0.08 | 0 | -41.98% | 40.86 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.08 | 795 | 300 | 0 | 52 | 743 | 748.8 | 5.8 | -0.68 | 6.406 | 13.892 | 0.461 | 18.28% | 750 | -0.9 | 7.937 | 13.859 | 7 | -0.08 | 0.573 | 15.15% | -14.15 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | WDS | STM | -0.08 | 105 | 70 | 0 | 34.5 | 70.5 | 72.5 | 2 | 0 | 1.997 | 1.634 | 1.222 | 7.014% | 72.6 | 0 | 2.129 | 1.63 | 2.1 | -0.08 | 1.306 | 6.68% | -4.46 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.08 | 328.3 | 204.4 | 12.2 | 54.1 | 262 | 269.5 | 7.5 | -1.3 | 8.815 | 4.171 | 2 | 5.84% | 276.7 | -1.8 | 16.492 | 4.161 | 14.7 | -0.08 | 2 | 2.98% | -2.37 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 706.1 | 443.4 | 30.6 | 126 | 549.5 | 564.4 | 14.9 | 0.12 | 14.73 | 8.914 | 1.652 | 6.32% | 571.2 | 0.2 | 21.522 | 8.892 | 21.7 | -0.08 | 2 | 4.34% | -3.38 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.08 | 55.8 | 22.5 | 0 | 20 | 35.8 | 37.8 | 2 | 0.15 | 1.869 | 0.869 | 2 | 3.734% | 44.2 | 0.2 | 8.204 | 0.866 | 8.4 | -0.08 | 2 | 0.8891% | -0.56 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 55.8 | 22.5 | 0 | 20.1 | 35.7 | 37.5 | 1.8 | 0.02 | 1.797 | 0.868 | 2 | 4.149% | 42.1 | 0 | 6.448 | 0.866 | 6.4 | -0.08 | 2 | 1.167% | -0.74 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 264 | 100 | 20 | 20.6 | 223.4 | 226.8 | 3.4 | -0.82 | 4.205 | 3.22 | 1.306 | 10.36% | 227.3 | -1.1 | 5.006 | 3.212 | 3.9 | -0.08 | 1.559 | 9.033% | -7.63 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 256 | 165 | 35 | 12.2 | 208.8 | 213.4 | 4.6 | -0.2 | 4.8 | 2.916 | 1.646 | 7.426% | 216.1 | -0.3 | 7.673 | 2.909 | 7.3 | -0.08 | 2 | 4.68% | -3.81 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.08 | 169 | 27 | 0 | 45.8 | 123.2 | 131.9 | 8.7 | 0.6 | 8.117 | 1.884 | 2 | 2.597% | 129.5 | 0.8 | 5.493 | 1.877 | 6.3 | -0.08 | 2 | 3.586% | -2.6 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 169 | 27 | 0 | 43.9 | 125.1 | 127.6 | 2.5 | 0.51 | 1.96 | 1.888 | 1.038 | 9.036% | 131.3 | 0.7 | 5.475 | 1.881 | 6.2 | -0.08 | 2 | 3.644% | -2.68 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.08 | 238 | 105 | 0 | 23.9 | 214.1 | 218.3 | 4.2 | -0.45 | 4.686 | 2.603 | 1.8 | 7.569% | 217.9 | -0.6 | 4.454 | 2.594 | 3.8 | -0.08 | 1.717 | 8.366% | -7.5 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 671 | 300 | 40 | 177.1 | 453.9 | 469.1 | 15.2 | 0 | 15.241 | 8.328 | 1.83 | 5.888% | 468.1 | 0 | 14.233 | 8.307 | 14.2 | -0.08 | 1.713 | 6.302% | -4.26 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.08 | 45 | 13 | 0 | 18.1 | 26.9 | 28.3 | 1.4 | 0.06 | 1.331 | 0.7 | 1.9 | 4.306% | 28.4 | 0.1 | 1.389 | 0.699 | 1.5 | -0.08 | 1.989 | 4.019% | -2.37 | 0.017 | 0.05 | 6.335% | 5.367%
Wind | WND | WIND | -0.038 | 98.5 | 0 | 0 | 10.1 | 88.4 | 90.5 | 2.1 | 0.59 | 1.591 | 1.248 | 1.275 | 2.984% | 90.6 | 0.8 | 1.452 | 1.066 | 2.2 | -0.032 | 1.362 | 2.401% | -2.53 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.038 | 522 | 275 | 12 | 138.9 | 371.1 | 380.3 | 9.2 | 2.01 | 7.234 | 4.747 | 1.524 | 3.597% | 383.4 | 2.8 | 9.537 | 4.011 | 12.3 | -0.032 | 2 | 2.266% | -1.91 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.038 | 602 | 220 | 0 | 293 | 309 | 316.8 | 7.8 | 0 | 7.844 | 7.626 | 1.029 | 4.892% | 316.7 | 0 | 7.789 | 6.516 | 7.7 | -0.032 | 1.195 | 4.173% | -2.54 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.038 | 459 | 300 | 0 | 77.3 | 381.7 | 388.4 | 6.7 | 0.12 | 6.567 | 4.272 | 1.537 | 4.343% | 393.7 | 0.2 | 11.873 | 3.61 | 12 | -0.032 | 2 | 2.042% | -2.01 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.038 | 119 | 0 | 0 | 82.5 | 36.5 | 38.9 | 2.4 | 0.18 | 2.295 | 1.507 | 1.523 | 3.152% | 39 | 0.2 | 2.282 | 1.288 | 2.5 | -0.032 | 1.772 | 2.55% | -0.91 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.038 | 517 | 234 | 25 | 248.3 | 243.7 | 251.1 | 7.4 | 0.47 | 6.952 | 4.579 | 1.518 | 4.429% | 250.6 | 0.7 | 6.257 | 3.87 | 6.9 | -0.032 | 1.617 | 4% | -2.23 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 205 | 152 | 0 | 51.8 | 153.2 | 157.7 | 4.5 | -0.72 | 5.228 | 1.908 | 2 | 2.891% | 158.1 | -1 | 5.871 | 1.612 | 4.9 | -0.032 | 2 | 2.237% | -1.97 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 176 | 107.9 | 16.8 | 51.3 | 107.9 | 109.2 | 1.3 | -0.12 | 1.377 | 1.482 | 0.93 | 8.596% | 109.5 | -0.2 | 1.764 | 1.252 | 1.6 | -0.032 | 1.409 | 5.884% | -4.25 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.038 | 560 | 135 | 0 | 411.6 | 148.4 | 157 | 8.6 | 1.75 | 6.801 | 5.32 | 1.278 | 4.127% | 159.3 | 2.4 | 8.406 | 4.546 | 10.9 | -0.032 | 1.849 | 2.743% | -0.86 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 420 | 125 | 0 | 272.3 | 147.7 | 150 | 2.3 | 0.13 | 2.142 | 3.691 | 0.58 | 11.58% | 150.4 | 0.2 | 2.52 | 3.154 | 2.7 | -0.032 | 0.799 | 8.307% | -3.45 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 417 | 125 | 0 | 273.2 | 143.8 | 150.8 | 7 | -0.47 | 7.445 | 3.663 | 2 | 3.777% | 154.8 | -0.6 | 11.636 | 3.13 | 11 | -0.032 | 2 | 2.024% | -0.83 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.038 | 420 | 70 | 0 | 349.2 | 70.8 | 76.8 | 6 | -0.11 | 6.118 | 3.883 | 1.576 | 4.438% | 76.2 | -0.2 | 5.468 | 3.318 | 5.4 | -0.032 | 1.648 | 4.153% | -0.83 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.038 | 228.1 | 168 | 12 | 40.9 | 175.2 | 178.4 | 3.2 | -0.06 | 3.254 | 2.011 | 1.618 | 4.523% | 178.2 | -0.1 | 3.089 | 1.7 | 3 | -0.032 | 1.818 | 4.065% | -3.69 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 238.1 | 165 | 18 | 49.4 | 170.7 | 174 | 3.3 | 0.53 | 2.815 | 2.049 | 1.374 | 4.578% | 173.9 | 0.7 | 2.504 | 1.731 | 3.2 | -0.032 | 1.446 | 3.977% | -3.37 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.038 | 746 | 95 | 0 | 647.3 | 98.7 | 106.6 | 7.9 | 2.06 | 5.822 | 4.743 | 1.227 | 5.988% | 106.9 | 2.9 | 5.389 | 3.72 | 8.2 | -0.032 | 1.448 | 4.859% | -0.76 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.038 | 683 | 141 | 0 | 537.4 | 145.6 | 152.6 | 7 | -0.68 | 7.655 | 4.984 | 1.536 | 6.188% | 158.7 | -0.9 | 14.047 | 3.909 | 13.1 | -0.032 | 2 | 2.785% | -0.7 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.038 | 241 | 154 | 0 | 83.4 | 157.6 | 160.7 | 3.1 | 0.01 | 3.142 | 2.243 | 1.401 | 4.933% | 161 | 0 | 3.457 | 1.896 | 3.4 | -0.032 | 1.824 | 3.789% | -2.93 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 55 | 4 | 20 | 29.5 | 5.5 | 12.5 | 7 | 0.59 | 6.476 | 0.326 | 2 | 0.5017% | 12.1 | 0.8 | 5.829 | 0.275 | 6.6 | -0.032 | 2 | 0.4487% | -0.05 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.038 | 645 | 300 | 0 | 287.9 | 357.1 | 372.7 | 15.6 | 3.84 | 11.704 | 7.204 | 1.625 | 2.62% | 372.9 | 5.3 | 10.428 | 6.156 | 15.8 | -0.032 | 1.694 | 2.179% | -1.43 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.038 | 321 | 248 | 0 | 70.6 | 250.4 | 257.9 | 7.5 | 0.04 | 7.415 | 2.988 | 2 | 2.714% | 258.7 | 0.1 | 8.277 | 2.525 | 8.3 | -0.032 | 2 | 2.066% | -1.91 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.038 | 105 | 12 | 0 | 92.8 | 12.2 | 14.5 | 2.3 | -0.55 | 2.888 | 1.317 | 2 | 2.904% | 14.1 | -0.8 | 2.678 | 1.126 | 1.9 | -0.032 | 2 | 2.962% | -0.39 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.038 | 1154 | 546 | 278 | 39.4 | 836.6 | 839 | 2.4 | 2.07 | 0.359 | 8.153 | 0.044 | 30.46% | 840 | 2.9 | 0.519 | 6.89 | 3.4 | -0.032 | 0.075 | 18.11% | -15.58 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 85 | 62 | 4 | 16.8 | 64.2 | 68.4 | 4.2 | 0.3 | 3.918 | 0.754 | 2 | 1.288% | 72.2 | 0.4 | 7.65 | 0.637 | 8 | -0.032 | 2 | 0.5702% | -0.5 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 331 | 143 | 0 | 183.5 | 147.5 | 154 | 6.5 | 0.02 | 6.491 | 3.081 | 2 | 3.229% | 154.8 | 0 | 7.259 | 2.603 | 7.3 | -0.032 | 2 | 2.422% | -1.28 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 520.7 | 347.2 | 0 | 12.4 | 508.3 | 514.2 | 5.9 | 1.97 | 3.908 | 4.846 | 0.806 | 5.594% | 514.9 | 2.7 | 3.821 | 4.095 | 6.6 | -0.032 | 0.933 | 4.212% | -4.87 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.038 | 416 | 180.3 | 0 | 25 | 391 | 400.3 | 9.3 | 0.78 | 8.486 | 5.27 | 1.61 | 2.836% | 399.5 | 1.1 | 7.414 | 4.503 | 8.5 | -0.032 | 1.647 | 2.614% | -2.91 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.038 | 470 | 264 | 19 | 10.7 | 440.3 | 448.5 | 8.2 | 0.89 | 7.243 | 4.198 | 1.725 | 3.634% | 447.5 | 1.2 | 5.94 | 3.547 | 7.2 | -0.032 | 1.674 | 3.485% | -3.87 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 878.8 | 461 | 141 | 208.8 | 529 | 548.7 | 19.7 | 0.66 | 19.062 | 6.867 | 2 | 2.827% | 550.9 | 0.9 | 20.969 | 5.803 | 21.9 | -0.032 | 2 | 2.141% | -1.53 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 875.4 | 461 | 141 | 229.2 | 505.2 | 525 | 19.8 | 1.11 | 18.688 | 6.836 | 2 | 2.802% | 525.4 | 1.5 | 18.631 | 5.777 | 20.2 | -0.032 | 2 | 2.313% | -1.58 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 395.9 | 215 | 85 | 94.6 | 216.3 | 219.7 | 3.4 | -0.6 | 4.016 | 2.894 | 1.388 | 7.383% | 220.3 | -0.8 | 4.883 | 2.446 | 4 | -0.032 | 1.997 | 5.286% | -3.42 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 480 | 348 | 50 | 49.1 | 380.9 | 393 | 12.1 | 0.08 | 12.071 | 4.002 | 2 | 2.515% | 393.5 | 0.1 | 12.527 | 3.382 | 12.6 | -0.032 | 2 | 2.034% | -1.91 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.038 | 232 | 150 | 0 | 80.1 | 151.9 | 154.9 | 3 | 0.04 | 2.961 | 2.397 | 1.235 | 4.907% | 154.7 | 0.1 | 2.754 | 2.049 | 2.8 | -0.032 | 1.344 | 4.429% | -3.43 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.038 | 238 | 150 | 0 | 86.3 | 151.7 | 154.3 | 2.6 | 0.03 | 2.551 | 2.459 | 1.037 | 5.808% | 154.5 | 0 | 2.75 | 2.102 | 2.8 | -0.032 | 1.309 | 4.543% | -3.42 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.038 | 240 | 150 | 0 | 88.6 | 151.4 | 154.1 | 2.7 | 0.07 | 2.612 | 2.48 | 1.053 | 5.64% | 154.1 | 0.1 | 2.673 | 2.119 | 2.7 | -0.032 | 1.261 | 4.751% | -3.54 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.038 | 231 | 150 | 0 | 79.6 | 151.4 | 154.3 | 2.9 | 0.05 | 2.846 | 2.387 | 1.192 | 5.055% | 154.3 | 0.1 | 2.888 | 2.04 | 2.9 | -0.032 | 1.416 | 4.258% | -3.3 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 171.1 | 0 | 40 | 40.2 | 90.9 | 93.4 | 2.5 | 1.14 | 1.396 | 1.22 | 1.144 | 4.346% | 91.2 | 1.6 | -1.31 | 1.031 | 0.3 | -0.032 | 0 | 30.51% | -19.1 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 290 | 165 | 40 | 72.2 | 177.8 | 181.7 | 3.9 | -0.44 | 4.368 | 2.327 | 1.877 | 4.717% | 181 | -0.6 | 3.85 | 1.966 | 3.2 | -0.032 | 1.958 | 4.842% | -3.51 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 597.7 | 450 | 0 | 144.2 | 453.5 | 454.6 | 1.1 | -0.03 | 1.154 | 5.562 | 0.207 | 34.44% | 456.1 | 0 | 2.668 | 4.701 | 2.6 | -0.032 | 0.568 | 12.27% | -11.04 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 580 | 450 | 0 | 126.9 | 453.1 | 454.5 | 1.4 | -0.46 | 1.875 | 5.398 | 0.347 | 26.26% | 457.2 | -0.6 | 4.751 | 4.562 | 4.1 | -0.032 | 1.042 | 7.552% | -6.99 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.038 | 834 | 258 | 0 | 468.4 | 365.6 | 383.1 | 17.5 | -0.29 | 17.811 | 7.189 | 2 | 3.02% | 383.5 | -0.4 | 18.379 | 6.143 | 17.9 | -0.032 | 2 | 2.486% | -1.29 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.038 | 836 | 259 | 0 | 470 | 366 | 374.9 | 8.9 | 1.1 | 7.793 | 7.456 | 1.045 | 5.952% | 374.7 | 1.5 | 7.216 | 6.371 | 8.7 | -0.032 | 1.133 | 5.128% | -2.66 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.038 | 493.8 | 309.7 | 57.5 | 57.7 | 378.6 | 387.8 | 9.2 | 0.68 | 8.468 | 4.061 | 2 | 3.402% | 387.8 | 1 | 8.276 | 3.432 | 9.2 | -0.032 | 2 | 2.866% | -2.6 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 512.2 | 310.3 | 56.3 | 77.5 | 378.4 | 388.4 | 10 | -0.12 | 10.079 | 4.243 | 2 | 3.247% | 387.8 | -0.2 | 9.478 | 3.586 | 9.4 | -0.032 | 2 | 2.909% | -2.55 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.038 | 237 | 150 | 0 | 84.5 | 152.5 | 154.7 | 2.2 | 0.21 | 2.081 | 2.21 | 0.942 | 6.836% | 154.9 | 0.3 | 2.173 | 1.888 | 2.4 | -0.032 | 1.151 | 5.278% | -4.01 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.038 | 236 | 150 | 0 | 83.4 | 152.6 | 155.2 | 2.6 | -0.05 | 2.667 | 2.2 | 1.213 | 5.76% | 156.1 | -0.1 | 3.573 | 1.88 | 3.5 | -0.032 | 1.901 | 3.604% | -2.75 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.038 | 234 | 150 | 0 | 81.4 | 152.6 | 155 | 2.4 | -0.2 | 2.591 | 2.181 | 1.188 | 6.187% | 155.2 | -0.3 | 2.878 | 1.864 | 2.6 | -0.032 | 1.544 | 4.811% | -3.71 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.038 | 236 | 150 | 0 | 83.1 | 152.9 | 155.7 | 2.8 | 0 | 2.723 | 2.199 | 1.238 | 5.348% | 156.6 | 0 | 3.656 | 1.879 | 3.7 | -0.032 | 1.946 | 3.409% | -2.61 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.038 | 241 | 150 | 0 | 86.3 | 154.7 | 158.7 | 4 | -0.19 | 4.167 | 2.141 | 1.947 | 3.823% | 158.2 | -0.3 | 3.755 | 1.829 | 3.5 | -0.032 | 2 | 3.68% | -2.79 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.038 | 250 | 110 | 0 | 96.5 | 153.5 | 157 | 3.5 | 0 | 3.578 | 2.301 | 1.555 | 4.532% | 157.1 | 0 | 3.617 | 1.966 | 3.6 | -0.032 | 1.84 | 3.712% | -2.69 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.038 | 750 | 300 | 0 | 448.9 | 301.1 | 308.2 | 7.1 | -0.29 | 7.37 | 9.5 | 0.776 | 6.694% | 307.4 | -0.4 | 6.706 | 8.118 | 6.3 | -0.032 | 0.826 | 6.354% | -3.02 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.038 | 825 | 300 | 0 | 523.6 | 301.4 | 306.5 | 5.1 | -0.21 | 5.284 | 10.451 | 0.506 | 10.25% | 305.3 | -0.3 | 4.179 | 8.93 | 3.9 | -0.032 | 0.468 | 11.29% | -4.89 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.038 | 510 | 210 | 0 | 298.8 | 211.2 | 218.8 | 7.6 | 2.19 | 5.395 | 6.46 | 0.835 | 4.254% | 222.1 | 3.1 | 7.807 | 5.52 | 10.9 | -0.032 | 1.414 | 2.498% | -1.22 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | WDS | STM | -0.038 | 105 | 70 | 0 | 34.6 | 70.4 | 72.1 | 1.7 | 0 | 1.732 | 1.158 | 1.496 | 3.928% | 71.9 | 0 | 1.529 | 0.964 | 1.5 | -0.032 | 1.586 | 3.752% | -2.95 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.038 | 668 | 440 | 48 | 141.9 | 478.1 | 484.7 | 6.6 | 0.94 | 5.671 | 5.77 | 0.983 | 6.414% | 488.7 | 1.3 | 9.279 | 4.877 | 10.6 | -0.032 | 1.903 | 3.364% | -2.85 | 0.017 | 0.0578 | 5.933% | 5.163%
Hydro | NA | HYDR | -0.038 | 34 | 0 | 0 | 20.1 | 13.9 | 34.3 | 20.4 | 0 | 20.387 | 0.431 | 2 | 0.1069% | 34.3 | 0 | 20.382 | 0.368 | 20.4 | -0.032 | 2 | 0.09028% | -0.04 | 0.017 | 0.05 | 0.2285% | 0.2528%
CombinedCycle | CC | COGN | -0.038 | 500 | 312 | 45.6 | 136.1 | 318.3 | 321.2 | 2.9 | -0.46 | 3.376 | 4.229 | 0.798 | 10.93% | 328 | -0.6 | 10.412 | 3.574 | 9.7 | -0.032 | 2 | 2.752% | -2.08 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 495 | 337 | 45.5 | 107 | 342.5 | 345 | 2.5 | 1.51 | 1.028 | 4.184 | 0.246 | 12.55% | 351.5 | 2.1 | 6.913 | 3.536 | 9 | -0.032 | 1.955 | 2.936% | -2.41 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.038 | 650 | 189.8 | 0 | 437.2 | 212.8 | 225.8 | 13 | -0.15 | 13.162 | 4.599 | 2 | 3.169% | 224.4 | -0.2 | 11.782 | 3.929 | 11.6 | -0.032 | 2 | 2.991% | -1.16 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 650 | 189.8 | 0 | 437.2 | 212.8 | 225.8 | 13 | -0.15 | 13.162 | 4.599 | 2 | 3.169% | 224.4 | -0.2 | 11.782 | 3.929 | 11.6 | -0.032 | 2 | 2.991% | -1.16 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 650 | 189.8 | 0 | 437.2 | 212.8 | 225.8 | 13 | -0.15 | 13.162 | 4.599 | 2 | 3.169% | 224.4 | -0.2 | 11.782 | 3.929 | 11.6 | -0.032 | 2 | 2.991% | -1.16 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 650 | 189.8 | 0 | 437.2 | 212.8 | 225.8 | 13 | -0.15 | 13.162 | 4.599 | 2 | 3.169% | 224.4 | -0.2 | 11.782 | 3.929 | 11.6 | -0.032 | 2 | 2.991% | -1.16 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 650 | 189.8 | 0 | 437.2 | 212.8 | 225.8 | 13 | -0.15 | 13.162 | 4.599 | 2 | 3.169% | 224.4 | -0.2 | 11.782 | 3.929 | 11.6 | -0.032 | 2 | 2.991% | -1.16 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.038 | 716.9 | 440 | 90 | 144.3 | 482.6 | 505.3 | 22.7 | 4.48 | 18.199 | 5.835 | 2 | 2.001% | 509.7 | 6.2 | 20.853 | 4.931 | 27.1 | -0.032 | 2 | 1.412% | -1.13 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 483.4 | 230 | 8.3 | 228.9 | 246.2 | 260.9 | 14.7 | 1.06 | 13.634 | 4.422 | 2 | 2.085% | 263.7 | 1.5 | 16.065 | 3.737 | 17.5 | -0.032 | 2 | 1.475% | -0.89 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 692 | 420 | 0 | 141.5 | 550.5 | 571 | 20.5 | 4.56 | 15.879 | 6.441 | 2 | 2.139% | 571.3 | 6.3 | 14.46 | 5.443 | 20.8 | -0.032 | 2 | 1.776% | -1.67 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.038 | 145.6 | 0 | 0 | 5.6 | 140 | 140 | 0 | -0.12 | 0.06 | 1.844 | 0.032 | 0% | 140 | -0.2 | 0.121 | 1.576 | 0 | -0.032 | 0.077 | 0% |  | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.038 | 221.6 | 118 | 0 | 40.5 | 181.1 | 185.3 | 4.2 | -0.12 | 4.366 | 2.063 | 2 | 3.348% | 184.6 | -0.2 | 3.743 | 1.743 | 3.5 | -0.032 | 2 | 3.385% | -3.27 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.038 | 340 | 220 | 0 | 75.1 | 264.9 | 270.8 | 5.9 | 0 | 5.878 | 4.168 | 1.41 | 3.655% | 270.5 | 0 | 5.6 | 3.561 | 5.6 | -0.032 | 1.572 | 3.243% | -2.99 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 940 | 322 | 0 | 90.9 | 849.1 | 869.4 | 20.3 | 2.35 | 17.865 | 8.56 | 2 | 2.934% | 874 | 3.3 | 21.546 | 7.314 | 24.9 | -0.032 | 2 | 2.015% | -2.16 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 940 | 322 | 0 | 90.9 | 849.1 | 869.4 | 20.3 | 2.35 | 17.865 | 8.56 | 2 | 2.934% | 874 | 3.3 | 21.546 | 7.314 | 24.9 | -0.032 | 2 | 2.015% | -2.16 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 940 | 322 | 0 | 90.9 | 849.1 | 869.4 | 20.3 | 2.35 | 17.865 | 8.56 | 2 | 2.934% | 874 | 3.3 | 21.546 | 7.314 | 24.9 | -0.032 | 2 | 2.015% | -2.16 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.038 | 940 | 322 | 0 | 90.9 | 849.1 | 869.4 | 20.3 | 2.35 | 17.865 | 8.56 | 2 | 2.934% | 874 | 3.3 | 21.546 | 7.314 | 24.9 | -0.032 | 2 | 2.015% | -2.16 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.038 | 78 | 57 | 0 | 19.7 | 58.3 | 59.1 | 0.8 | -0.08 | 0.88 | 0.86 | 1.023 | 6.21% | 59.1 | -0.1 | 0.917 | 0.716 | 0.8 | -0.032 | 1.28 | 5.235% | -4.58 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.038 | 78 | 57 | 0 | 18.7 | 59.3 | 60 | 0.7 | -0.01 | 0.764 | 0.86 | 0.889 | 7.098% | 60.1 | 0 | 0.825 | 0.716 | 0.8 | -0.032 | 1.152 | 5.235% | -4.66 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 840 | 465 | 122.6 | 252.4 | 465 | 474.6 | 9.6 | -1.09 | 10.666 | 6.677 | 1.598 | 5.545% | 473.1 | -1.5 | 9.609 | 5.642 | 8.1 | -0.032 | 1.703 | 5.534% | -3.63 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 261 | 165 | 35 | 59.6 | 166.4 | 172.3 | 5.9 | -0.01 | 5.89 | 2.103 | 2 | 2.806% | 174.8 | 0 | 8.454 | 1.778 | 8.4 | -0.032 | 2 | 1.661% | -1.25 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.038 | 664 | 156 | 0 | 191.6 | 472.4 | 482.3 | 9.9 | 0.31 | 9.651 | 6.893 | 1.4 | 4.251% | 481.8 | 0.4 | 9.011 | 5.89 | 9.4 | -0.032 | 1.53 | 3.77% | -3.18 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.038 | 499 | 156 | 0 | 57.7 | 441.3 | 453.3 | 12 | 1.21 | 10.757 | 5.26 | 2 | 2.636% | 453.8 | 1.7 | 10.789 | 4.494 | 12.5 | -0.032 | 2 | 2.131% | -2.23 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.038 | 577 | 159 | 0 | 120.1 | 456.9 | 462.7 | 5.8 | 0.78 | 4.994 | 5.844 | 0.855 | 6.305% | 462.4 | 1.1 | 4.415 | 4.993 | 5.5 | -0.032 | 0.884 | 5.6% | -5.26 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.038 | 592 | 307 | 0 | 104.9 | 487.1 | 494.9 | 7.8 | 2.25 | 5.567 | 5.917 | 0.941 | 4.81% | 495.7 | 3.1 | 5.551 | 5.056 | 8.6 | -0.032 | 1.098 | 3.675% | -3.58 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.038 | 683 | 300 | 40 | 207.7 | 435.3 | 457.1 | 21.8 | 3.46 | 18.37 | 5.985 | 2 | 1.986% | 460.8 | 4.8 | 20.725 | 5.058 | 25.5 | -0.032 | 2 | 1.43% | -1.08 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.038 | 1085 | 379 | 175 | 121.4 | 788.6 | 803.7 | 15.1 | 0.63 | 14.494 | 8.47 | 1.711 | 4.553% | 801.5 | 0.9 | 12.044 | 7.158 | 12.9 | -0.032 | 1.683 | 4.488% | -3.87 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.066 | 300 | 55 | 0 | 150.4 | 149.6 | 151.3 | 1.7 | -0.51 | 2.226 | 2.064 | 1.078 | 19.45% | 150.8 | -0.7 | 1.868 | 2.378 | 1.2 | -0.07 | 0.786 | 29.21% | -13.67 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.066 | 508.4 | 275 | 12 | 124.5 | 371.9 | 381.4 | 9.5 | -3.13 | 12.612 | 5.481 | 2 | 5.89% | 385.2 | -4.3 | 17.61 | 6.014 | 13.3 | -0.07 | 2 | 4.462% | -3.07 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.066 | 226 | 165 | 10 | 45.5 | 170.5 | 175.2 | 4.7 | -0.59 | 5.261 | 2.385 | 2 | 5.295% | 175.1 | -0.8 | 5.385 | 2.617 | 4.6 | -0.07 | 2 | 5.738% | -4.07 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.066 | 230 | 60 | 0 | 91.8 | 138.2 | 140.9 | 2.7 | 0.51 | 2.186 | 1.891 | 1.156 | 9.391% | 141.2 | 0.7 | 2.373 | 2.178 | 3 | -0.07 | 1.09 | 8.963% | -5.05 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 412 | 70 | 0 | 23.3 | 388.7 | 397.6 | 8.9 | -4.25 | 13.166 | 2.96 | 2 | 5.099% | 397.3 | -5.9 | 14.514 | 3.411 | 8.6 | -0.07 | 2 | 5.596% | -4.97 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.066 | 560 | 400 | 0 | 139.5 | 420.5 | 427.4 | 6.9 | -0.25 | 7.191 | 7.013 | 1.025 | 8.932% | 428 | -0.4 | 7.848 | 7.667 | 7.5 | -0.07 | 1.024 | 8.715% | -6.16 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.066 | 420 | 260 | 0 | 109.5 | 310.5 | 316.3 | 5.8 | 1.15 | 4.69 | 4.686 | 1.001 | 7.97% | 315.9 | 1.6 | 3.877 | 5.123 | 5.4 | -0.07 | 0.757 | 9.079% | -6.32 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 420 | 70 | 0 | 124.9 | 295.1 | 298 | 2.9 | 2.24 | 0.634 | 5.47 | 0.116 | 15.94% | 298.3 | 3.1 | 0.083 | 5.98 | 3.2 | -0.07 | 0.014 | 15.32% | -10.14 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 410 | 70 | 0 | 112.4 | 297.6 | 302.4 | 4.8 | 1.94 | 2.853 | 5.772 | 0.494 | 9.402% | 302.4 | 2.7 | 2.005 | 6.31 | 4.8 | -0.07 | 0.318 | 9.971% | -6.81 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.066 | 319 | 231 | 0 | 43.6 | 275.4 | 281.4 | 6 | -0.22 | 6.255 | 3.522 | 1.776 | 5.853% | 283.1 | -0.3 | 8.027 | 3.865 | 7.7 | -0.07 | 2 | 4.837% | -3.93 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.066 | 105 | 12 | 0 | 92.8 | 12.2 | 13.3 | 1.1 | 0.06 | 1.113 | 1.532 | 0.727 | 10.53% | 14.2 | 0.1 | 1.95 | 1.675 | 2 | -0.07 | 1.165 | 6.139% | -0.66 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 315 | 50 | 0 | 17.4 | 297.6 | 308.5 | 10.9 | 1.62 | 9.265 | 3.756 | 2 | 3.181% | 306.5 | 2.3 | 6.609 | 4.106 | 8.9 | -0.07 | 1.609 | 4.132% | -3.68 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 420 | 50 | 0 | 14.4 | 405.6 | 413.5 | 7.9 | -0.37 | 8.3 | 5.223 | 1.589 | 5.852% | 413.4 | -0.5 | 8.341 | 5.71 | 7.8 | -0.07 | 1.461 | 6.286% | -5.72 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.066 | 328 | 133 | 0 | 19.3 | 308.7 | 314.5 | 5.8 | -0.49 | 6.302 | 3.622 | 1.74 | 6.226% | 315 | -0.7 | 7.018 | 3.974 | 6.3 | -0.07 | 1.766 | 6.079% | -5.39 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.066 | 212 | 130 | 0 | 39.2 | 172.8 | 176.9 | 4.1 | 1.26 | 2.813 | 2.341 | 1.202 | 5.695% | 176.9 | 1.8 | 2.346 | 2.568 | 4.1 | -0.07 | 0.914 | 6.039% | -4.63 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | STM | -0.066 | 135.2 | 20.2 | 0 | 113.4 | 21.8 | 22.6 | 0.8 | -0.47 | 1.291 | 1.983 | 0.651 | 18.63% | 22.7 | -0.7 | 1.564 | 2.168 | 0.9 | -0.07 | 0.721 | 17.56% | -2.63 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.066 | 316 | 55 | 0 | 61.2 | 254.8 | 259.9 | 5.1 | 0.07 | 5.021 | 4.458 | 1.126 | 6.821% | 260.1 | 0.1 | 5.195 | 4.873 | 5.3 | -0.07 | 1.066 | 6.961% | -5.28 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | FOSS | -0.066 | 385 | 40 | 0 | 342.9 | 42.1 | 50.1 | 8 | -1.84 | 9.858 | 3.153 | 2 | 5.301% | 52.4 | -2.6 | 12.899 | 3.632 | 10.3 | -0.07 | 2 | 4.366% | -0.44 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.066 | 223 | 150 | 0 | 23 | 200 | 203.3 | 3.3 | -0.63 | 3.976 | 2.989 | 1.33 | 7.442% | 203.7 | -0.9 | 4.605 | 3.267 | 3.7 | -0.07 | 1.409 | 7.039% | -5.94 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.066 | 230 | 150 | 0 | 29 | 201 | 204.7 | 3.7 | -0.72 | 4.404 | 3.092 | 1.425 | 6.845% | 204.7 | -1 | 4.722 | 3.38 | 3.7 | -0.07 | 1.397 | 7.26% | -5.97 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.066 | 231 | 150 | 0 | 29 | 202 | 205 | 3 | -0.72 | 3.727 | 3.113 | 1.197 | 8.479% | 205.3 | -1 | 4.359 | 3.404 | 3.3 | -0.07 | 1.281 | 8.175% | -6.72 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.066 | 221 | 150 | 0 | 22.1 | 198.9 | 202.2 | 3.3 | -0.64 | 3.906 | 2.953 | 1.323 | 7.375% | 203 | -0.9 | 4.906 | 3.228 | 4.1 | -0.07 | 1.52 | 6.296% | -5.33 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.066 | 395 | 100 | 0 | 19.3 | 375.7 | 389.8 | 14.1 | -0.91 | 14.982 | 2.893 | 2 | 3.086% | 392.4 | -1.3 | 17.982 | 3.333 | 16.7 | -0.07 | 2 | 2.763% | -2.47 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 335 | 120 | 0 | 210.6 | 124.4 | 132.7 | 8.3 | 0.29 | 7.933 | 4.495 | 1.765 | 4.443% | 133.5 | 0.4 | 8.703 | 4.914 | 9.1 | -0.07 | 1.771 | 4.298% | -1.5 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 425 | 120 | 0 | 304.8 | 120.2 | 128.2 | 8 | 0.58 | 7.385 | 5.721 | 1.291 | 5.847% | 131.3 | 0.8 | 10.304 | 6.254 | 11.1 | -0.07 | 1.647 | 4.47% | -1.19 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.066 | 834 | 258 | 0 | 56 | 778 | 795.1 | 17.1 | 0.9 | 16.161 | 8.08 | 2 | 5.367% | 797.9 | 1.3 | 18.558 | 8.833 | 19.9 | -0.07 | 2 | 4.891% | -4.3 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.066 | 98 | 58 | 0 | 5 | 93 | 93 | 0 | 0 | 0.012 | 1.278 | 0.01 | 0% | 93 | 0 | 0 | 1.412 | 0 | -0.07 | 0 | 0% |  | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.066 | 392 | 57 | 0 | 334.5 | 57.5 | 59.9 | 2.4 | 0.08 | 2.345 | 4.844 | 0.484 | 17.98% | 58.8 | 0.1 | 1.206 | 5.296 | 1.3 | -0.07 | 0.228 | 35.2% | -4.84 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 122 | 15 | 0 | 106.8 | 15.2 | 17.4 | 2.2 | -0.65 | 2.777 | 1.468 | 1.892 | 6.113% | 19.1 | -0.9 | 4.786 | 1.604 | 3.9 | -0.07 | 2 | 3.657% | -0.42 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.066 | 226 | 150 | 0 | 21.8 | 204.2 | 207.5 | 3.3 | -0.94 | 4.281 | 2.664 | 1.607 | 7.542% | 208.2 | -1.3 | 5.26 | 2.912 | 4 | -0.07 | 1.806 | 6.599% | -5.61 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.066 | 225 | 150 | 0 | 23.3 | 201.7 | 205.3 | 3.6 | -0.83 | 4.468 | 2.637 | 1.694 | 6.883% | 205.4 | -1.1 | 4.889 | 2.883 | 3.7 | -0.07 | 1.696 | 7.102% | -5.99 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.066 | 222 | 150 | 0 | 24.4 | 197.6 | 200.7 | 3.1 | -0.78 | 3.889 | 2.58 | 1.507 | 7.887% | 201.5 | -1.1 | 5.03 | 2.82 | 3.9 | -0.07 | 1.783 | 6.648% | -5.57 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.066 | 225 | 150 | 0 | 21.5 | 203.5 | 207.2 | 3.7 | -0.91 | 4.549 | 2.648 | 1.718 | 6.697% | 207.4 | -1.3 | 5.166 | 2.894 | 3.9 | -0.07 | 1.785 | 6.738% | -5.73 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.066 | 226 | 150 | 0 | 17.5 | 208.5 | 213 | 4.5 | -0.99 | 5.433 | 2.595 | 2 | 5.531% | 213.9 | -1.4 | 6.735 | 2.837 | 5.4 | -0.07 | 2 | 4.888% | -4.24 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.066 | 235 | 110 | 0 | 23.5 | 211.5 | 215.7 | 4.2 | -0.91 | 5.139 | 2.719 | 1.89 | 6.162% | 216.9 | -1.3 | 6.673 | 2.973 | 5.4 | -0.07 | 2 | 5.082% | -4.3 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.066 | 102 | 35 | 0 | 53.9 | 48.1 | 51 | 2.9 | 0.4 | 2.497 | 1.33 | 1.878 | 3.879% | 52.3 | 0.6 | 3.63 | 1.47 | 4.2 | -0.07 | 2 | 2.84% | -1.25 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | WDS | STM | -0.066 | 105 | 70 | 0 | 34.6 | 70.4 | 71.9 | 1.5 | -0.06 | 1.63 | 1.369 | 1.191 | 7.719% | 72.1 | -0.1 | 1.825 | 1.513 | 1.7 | -0.07 | 1.206 | 7.223% | -4.54 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.066 | 700.3 | 439.1 | 20.2 | 68.1 | 612 | 623.9 | 11.9 | -0.18 | 12.071 | 7.509 | 1.607 | 6.476% | 630.3 | -0.2 | 18.546 | 8.239 | 18.3 | -0.07 | 2 | 4.466% | -3.68 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.066 | 114 | 45 | 0 | 4 | 110 | 110.8 | 0.8 | -2.94 | 3.773 | 1.259 | 2 | 15.71% | 110.4 | -4.1 | 4.497 | 1.381 | 0.4 | -0.07 | 2 | 33.32% | -30.18 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.066 | 54.5 | 22.5 | 0 | 9.5 | 45 | 45.7 | 0.7 | 0.1 | 0.565 | 0.71 | 0.795 | 8.605% | 45.9 | 0.1 | 0.774 | 0.785 | 0.9 | -0.07 | 0.986 | 7.096% | -5.47 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 54.7 | 22.5 | 0 | 10.3 | 44.4 | 45.8 | 1.4 | 0.37 | 1.063 | 0.713 | 1.492 | 4.318% | 46 | 0.5 | 1.069 | 0.788 | 1.6 | -0.07 | 1.357 | 4.006% | -3.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.066 | 940 | 322 | 0 | 20.3 | 919.7 | 925 | 5.3 | 2.59 | 2.717 | 9.847 | 0.276 | 19.51% | 928.5 | 3.6 | 5.112 | 10.765 | 8.8 | -0.07 | 0.475 | 12.47% | -11.49 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.066 | 940 | 322 | 0 | 20.3 | 919.7 | 925 | 5.3 | 2.59 | 2.717 | 9.847 | 0.276 | 19.51% | 928.5 | 3.6 | 5.112 | 10.765 | 8.8 | -0.07 | 0.475 | 12.47% | -11.49 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.066 | 940 | 322 | 0 | 20.3 | 919.7 | 925 | 5.3 | 2.59 | 2.717 | 9.847 | 0.276 | 19.51% | 928.5 | 3.6 | 5.112 | 10.765 | 8.8 | -0.07 | 0.475 | 12.47% | -11.49 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.066 | 940 | 322 | 0 | 20.3 | 919.7 | 925 | 5.3 | 2.59 | 2.717 | 9.847 | 0.276 | 19.51% | 928.5 | 3.6 | 5.112 | 10.765 | 8.8 | -0.07 | 0.475 | 12.47% | -11.49 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 167 | 55 | 0 | 109 | 58 | 60.5 | 2.5 | -0.12 | 2.582 | 1.394 | 1.852 | 7.371% | 60.3 | -0.2 | 2.386 | 1.606 | 2.3 | -0.07 | 1.486 | 8.496% | -2.75 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.066 | 425 | 295 | 0 | 9 | 416 | 420.8 | 4.8 | -2.73 | 7.473 | 6.255 | 1.195 | 9.745% | 422.8 | -3.8 | 10.578 | 6.839 | 6.8 | -0.07 | 1.547 | 7.296% | -6.73 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 41 | 13 | 0 | 27.9 | 13.1 | 13.6 | 0.5 | -0.24 | 0.733 | 0.372 | 1.97 | 9.133% | 13.5 | -0.3 | 0.728 | 0.429 | 0.4 | -0.07 | 1.7 | 12.1% | -3.46 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.066 | 264 | 100 | 20 | 5.4 | 238.6 | 238.3 | -0.3 | -0.91 | 0.584 | 2.694 | 0.217 | -96.89% | 238.2 | -1.3 | 0.868 | 2.956 | -0.4 | -0.07 | 0.294 | -77.07% | 65.54 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.066 | 230.3 | 130 | 0 | 38 | 192.3 | 195.3 | 3 | 0.23 | 2.741 | 2.543 | 1.078 | 8.454% | 194.7 | 0.3 | 2.127 | 2.79 | 2.4 | -0.07 | 0.762 | 11.21% | -8.8 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.066 | 255 | 165 | 35 | 11.9 | 208.1 | 212.6 | 4.5 | 0.04 | 4.559 | 2.429 | 1.877 | 6.24% | 214 | 0.1 | 5.905 | 2.665 | 5.9 | -0.07 | 2 | 5.047% | -3.88 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.066 | 169 | 27 | 0 | 78.1 | 90.9 | 95.5 | 4.6 | -0.98 | 5.564 | 1.277 | 2 | 4.054% | 95.5 | -1.4 | 5.949 | 1.472 | 4.6 | -0.07 | 2 | 4.299% | -2.16 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 169 | 27 | 0 | 77.5 | 91.5 | 95.1 | 3.6 | -2.14 | 5.681 | 1.196 | 2 | 5.18% | 93 | -3 | 4.426 | 1.378 | 1.5 | -0.07 | 2 | 13.18% | -6.67 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.066 | 238 | 54 | 0 | 5.9 | 232.1 | 237.5 | 5.4 | -1.18 | 6.567 | 1.98 | 2 | 4.859% | 237 | -1.6 | 6.552 | 2.281 | 4.9 | -0.07 | 2 | 5.678% | -5.2 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.066 | 674 | 300 | 40 | 172 | 462 | 477 | 15 | -1.73 | 16.786 | 7.001 | 2 | 4.945% | 475.5 | -2.4 | 15.907 | 7.681 | 13.5 | -0.07 | 2 | 5.827% | -3.76 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 632.7 | 252 | 128 | 121.4 | 383.3 | 422 | 38.7 | 38.18 | 0.529 | 3.828 | 0.138 | 1.663% | 434.8 | 53.1 | -1.561 | 3.468 | 51.5 | -0.059 | 0 | 1.209% | -0.76 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 520 | 275 | 12 | 51.7 | 456.3 | 462 | 5.7 | -0.89 | 6.536 | 3.853 | 1.697 | 9.28% | 465 | -1.2 | 9.911 | 3.491 | 8.7 | -0.059 | 2 | 5.881% | -5.33 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.061 | 591 | 220 | 0 | 23.6 | 567.4 | 573.3 | 5.9 | 0.58 | 5.26 | 6.086 | 0.864 | 10.19% | 574.7 | 0.8 | 6.446 | 5.547 | 7.3 | -0.059 | 1.162 | 7.965% | -7.9 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.061 | 459 | 300 | 0 | 62.3 | 396.7 | 402.9 | 6.2 | 0.89 | 5.312 | 3.481 | 1.526 | 7.531% | 406.4 | 1.2 | 8.415 | 3.154 | 9.7 | -0.059 | 2 | 4.656% | -4.15 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 193.5 | 145.5 | 0 | 42.5 | 151 | 157.2 | 6.2 | 0.21 | 5.93 | 1.468 | 2 | 3.178% | 157.5 | 0.3 | 6.192 | 1.33 | 6.5 | -0.059 | 2 | 2.932% | -2.36 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.061 | 420 | 125 | 0 | 165.7 | 254.3 | 256.7 | 2.4 | 0.25 | 2.203 | 3.159 | 0.697 | 17.8% | 254.2 | 0.3 | -0.371 | 2.88 | -0.1 | -0.059 | 0 | -413.3% | 258.25 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.061 | 417 | 125 | 0 | 259.6 | 157.4 | 162 | 4.6 | -2.55 | 7.129 | 2.96 | 2 | 9.222% | 160.1 | -3.5 | 6.259 | 2.698 | 2.7 | -0.059 | 2 | 15.2% | -5.92 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.061 | 420 | 70 | 0 | 305.5 | 114.5 | 118.1 | 3.6 | 0.15 | 3.517 | 3.11 | 1.131 | 11.87% | 116.8 | 0.2 | 2.152 | 2.834 | 2.3 | -0.059 | 0.759 | 17.97% | -5.05 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.061 | 223 | 168 | 12 | 41.9 | 169.1 | 171.3 | 2.2 | -0.24 | 2.431 | 1.6 | 1.519 | 10.32% | 171.6 | -0.3 | 2.864 | 1.45 | 2.5 | -0.059 | 1.976 | 8.783% | -6.87 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.061 | 746 | 142 | 0 | 603 | 143 | 152.2 | 9.2 | -0.49 | 9.664 | 2.907 | 2 | 8.25% | 152.1 | -0.7 | 9.797 | 2.33 | 9.1 | -0.059 | 2 | 8.067% | -1.59 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.061 | 240 | 167 | 0 | 46.4 | 193.6 | 194.9 | 1.3 | 0.09 | 1.198 | 1.82 | 0.658 | 18.79% | 194.9 | 0.1 | 1.231 | 1.649 | 1.3 | -0.059 | 0.747 | 18.18% | -15.12 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 322 | 246 | 0 | 43.4 | 278.6 | 283.6 | 5 | 0.77 | 4.196 | 2.442 | 1.718 | 6.553% | 284 | 1.1 | 4.349 | 2.212 | 5.4 | -0.059 | 1.966 | 5.869% | -5.24 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.061 | 105 | 12 | 0 | 93 | 12 | 13.2 | 1.2 | -0.07 | 1.21 | 1.072 | 1.128 | 8.919% | 13.3 | -0.1 | 1.321 | 0.977 | 1.3 | -0.059 | 1.352 | 7.964% | -0.92 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.061 | 420 | 52 | 0 | 366.9 | 53.1 | 60.9 | 7.8 | 0.13 | 7.643 | 2.818 | 2 | 5.478% | 60.7 | 0.2 | 7.471 | 2.568 | 7.6 | -0.059 | 2 | 5.438% | -0.71 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.061 | 332 | 143 | 0 | 188.3 | 143.7 | 147.5 | 3.8 | 0.04 | 3.746 | 2.518 | 1.488 | 8.89% | 147.9 | 0.1 | 4.128 | 2.281 | 4.2 | -0.059 | 1.81 | 7.78% | -3.47 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.061 | 579.2 | 149.2 | 0 | 26.7 | 552.5 | 557.4 | 4.9 | -4.35 | 9.292 | 4.228 | 2 | 12.02% | 551.7 | -6.1 | 5.262 | 3.853 | -0.8 | -0.059 | 1.365 | -71.23% | 70.18 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.061 | 579.2 | 149.2 | 0 | 26.7 | 552.5 | 557.4 | 4.9 | -4.35 | 9.292 | 4.228 | 2 | 12.02% | 551.7 | -6.1 | 5.262 | 3.853 | -0.8 | -0.059 | 1.365 | -71.23% | 70.18 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.061 | 894.5 | 461 | 141 | 25.5 | 728 | 742.9 | 14.9 | 0.38 | 14.616 | 5.715 | 2 | 6.105% | 744.4 | 0.5 | 15.92 | 5.177 | 16.4 | -0.059 | 2 | 5.365% | -4.51 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 269 | 175 | 44 | 48.7 | 176.3 | 178.4 | 2.1 | -0.6 | 2.75 | 1.707 | 1.611 | 13.04% | 180.8 | -0.8 | 5.39 | 1.546 | 4.5 | -0.059 | 2 | 5.884% | -3.98 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.061 | 470 | 180 | 0 | 155.7 | 314.3 | 311.9 | -2.4 | -3.71 | 1.369 | 1.544 | 0.886 | -19.93% | 310.8 | -5.2 | 1.714 | 1.238 | -3.5 | -0.059 | 1.385 | -13.22% | 9.11 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.061 | 470 | 180 | 0 | 155.7 | 314.3 | 311.9 | -2.4 | -3.71 | 1.369 | 1.544 | 0.886 | -19.93% | 310.8 | -5.2 | 1.714 | 1.238 | -3.5 | -0.059 | 1.385 | -13.22% | 9.11 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.061 | 470 | 180 | 0 | 155.7 | 314.3 | 311.9 | -2.4 | -3.71 | 1.369 | 1.544 | 0.886 | -19.93% | 310.8 | -5.2 | 1.714 | 1.238 | -3.5 | -0.059 | 1.385 | -13.22% | 9.11 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.061 | 470 | 180 | 0 | 155.7 | 314.3 | 311.9 | -2.4 | -3.71 | 1.369 | 1.544 | 0.886 | -19.93% | 310.8 | -5.2 | 1.714 | 1.238 | -3.5 | -0.059 | 1.385 | -13.22% | 9.11 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.061 | 229 | 150 | 0 | 23.2 | 205.8 | 208.7 | 2.9 | -0.01 | 2.894 | 2.183 | 1.326 | 8.038% | 208.7 | 0 | 2.94 | 1.99 | 2.9 | -0.059 | 1.478 | 7.775% | -7.21 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.061 | 236 | 150 | 0 | 66.8 | 169.2 | 169 | -0.2 | -4.35 | 4.158 | 2.016 | 2 | -120.1% | 167.3 | -6.1 | 4.101 | 1.837 | -1.9 | -0.059 | 2 | -12.23% | 9.04 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.061 | 237 | 150 | 0 | 29.2 | 207.8 | 210.8 | 3 | 0.03 | 2.959 | 2.274 | 1.301 | 8.041% | 210.8 | 0 | 2.997 | 2.073 | 3 | -0.059 | 1.446 | 7.778% | -7.03 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.061 | 228 | 150 | 0 | 28.2 | 199.8 | 202.6 | 2.8 | 0.17 | 2.625 | 2.137 | 1.229 | 8.289% | 203.1 | 0.2 | 3.04 | 1.947 | 3.3 | -0.059 | 1.561 | 6.803% | -6.15 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.061 | 395 | 100 | 0 | 292.5 | 102.5 | 109.7 | 7.2 | -1.04 | 8.246 | 1.23 | 2 | 5.585% | 107.4 | -1.4 | 6.31 | 0.986 | 4.9 | -0.059 | 2 | 7.938% | -2.12 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.061 | 152.7 | 0 | 40 | 29.2 | 83.5 | 86.1 | 2.6 | -0.43 | 3.041 | 0.855 | 2 | 5.982% | 85.4 | -0.6 | 2.494 | 0.774 | 1.9 | -0.059 | 2 | 7.918% | -4.45 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 604 | 305 | 111 | 145 | 348 | 353.2 | 5.2 | -0.95 | 6.104 | 3.739 | 1.633 | 11.81% | 354 | -1.3 | 7.333 | 3.387 | 6 | -0.059 | 2 | 9.904% | -5.89 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 616 | 305 | 111 | 168.9 | 336.1 | 339.3 | 3.2 | 1.69 | 1.498 | 3.83 | 0.391 | 19.58% | 345 | 2.3 | 6.496 | 3.47 | 8.9 | -0.059 | 1.872 | 6.809% | -3.84 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 595 | 460 | 0 | 133.7 | 461.3 | 461.3 | 0 | -0.07 | 0.081 | 4.512 | 0.018 | 0% | 464.2 | -0.1 | 3.033 | 4.088 | 2.9 | -0.059 | 0.742 | 20.19% | -16.16 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.061 | 98 | 64 | 0 | 9.4 | 88.6 | 90.7 | 2.1 | 0.47 | 1.641 | 0.88 | 1.865 | 4.758% | 92.2 | 0.6 | 2.9 | 0.791 | 3.6 | -0.059 | 2 | 2.685% | -2.49 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 525.3 | 309.7 | 38.6 | 22.3 | 464.4 | 469.3 | 4.9 | 0.66 | 4.276 | 3.691 | 1.159 | 10.9% | 468.8 | 0.9 | 3.538 | 3.344 | 4.4 | -0.059 | 1.058 | 11.75% | -10.72 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 526.4 | 310.3 | 37 | 23.9 | 465.5 | 470 | 4.5 | 0.52 | 3.945 | 3.712 | 1.063 | 11.9% | 469.1 | 0.7 | 2.852 | 3.363 | 3.6 | -0.059 | 0.848 | 14.39% | -13.14 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.061 | 568 | 200 | 0 | 328.2 | 239.8 | 245.6 | 5.8 | 1.52 | 4.332 | 2.726 | 1.589 | 9.961% | 253.1 | 2.1 | 11.223 | 2.485 | 13.3 | -0.059 | 2 | 4.202% | -1.83 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.061 | 235 | 150 | 0 | 23 | 212 | 215.2 | 3.2 | 0.12 | 3.008 | 1.975 | 1.523 | 7.475% | 215.4 | 0.2 | 3.193 | 1.8 | 3.4 | -0.059 | 1.774 | 6.805% | -6.33 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.061 | 233 | 150 | 0 | 82.3 | 150.7 | 153.8 | 3.1 | 0.06 | 3.032 | 1.767 | 1.716 | 7.651% | 154.2 | 0.1 | 3.418 | 1.611 | 3.5 | -0.059 | 2 | 6.554% | -4.37 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.061 | 235 | 150 | 0 | 22 | 213 | 214.6 | 1.6 | 0.17 | 1.475 | 1.982 | 0.744 | 14.95% | 214.7 | 0.2 | 1.422 | 1.806 | 1.7 | -0.059 | 0.787 | 13.61% | -12.72 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.061 | 780 | 300 | 0 | 73 | 707 | 720.8 | 13.8 | 3.39 | 10.391 | 8.032 | 1.294 | 5.748% | 723.4 | 4.7 | 11.701 | 7.321 | 16.4 | -0.059 | 1.598 | 4.679% | -4.38 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.061 | 795 | 300 | 0 | 36.8 | 758.2 | 761.2 | 3 | -2.47 | 5.393 | 8.187 | 0.659 | 26.95% | 762.8 | -3.4 | 8.053 | 7.462 | 4.6 | -0.059 | 1.079 | 17% | -16.75 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | WDS | STM | -0.061 | 105 | 70 | 0 | 34.7 | 70.3 | 71.4 | 1.1 | 0.12 | 0.961 | 0.943 | 1.02 | 9.73% | 71.5 | 0.2 | 1.022 | 0.847 | 1.2 | -0.059 | 1.206 | 8.628% | -5.93 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.061 | 497 | 309 | 45.7 | 131.2 | 320.1 | 324.1 | 4 | 1.75 | 2.231 | 3.423 | 0.652 | 12.64% | 325.5 | 2.4 | 2.93 | 3.101 | 5.4 | -0.059 | 0.945 | 9.056% | -6.02 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 492 | 334 | 45.5 | 97.2 | 349.3 | 349.4 | 0.1 | -6.89 | 6.967 | 3.386 | 2 | 500.5% | 356.8 | -9.6 | 17.09 | 3.068 | 7.5 | -0.059 | 2 | 6.454% | -4.73 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.061 | 650 | 189.8 | 0 | 133.4 | 516.6 | 520.7 | 4.1 | -0.23 | 4.391 | 4.358 | 1.008 | 16.12% | 523.5 | -0.3 | 7.246 | 3.972 | 6.9 | -0.059 | 1.824 | 9.267% | -7.61 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.061 | 650 | 189.8 | 0 | 133.4 | 516.6 | 520.7 | 4.1 | -0.23 | 4.391 | 4.358 | 1.008 | 16.12% | 523.5 | -0.3 | 7.246 | 3.972 | 6.9 | -0.059 | 1.824 | 9.267% | -7.61 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.061 | 650 | 189.8 | 0 | 133.4 | 516.6 | 520.7 | 4.1 | -0.23 | 4.391 | 4.358 | 1.008 | 16.12% | 523.5 | -0.3 | 7.246 | 3.972 | 6.9 | -0.059 | 1.824 | 9.267% | -7.61 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.061 | 650 | 189.8 | 0 | 133.4 | 516.6 | 520.7 | 4.1 | -0.23 | 4.391 | 4.358 | 1.008 | 16.12% | 523.5 | -0.3 | 7.246 | 3.972 | 6.9 | -0.059 | 1.824 | 9.267% | -7.61 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.061 | 650 | 189.8 | 0 | 133.4 | 516.6 | 520.7 | 4.1 | -0.23 | 4.391 | 4.358 | 1.008 | 16.12% | 523.5 | -0.3 | 7.246 | 3.972 | 6.9 | -0.059 | 1.824 | 9.267% | -7.61 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.061 | 726.7 | 462.2 | 37.9 | 160.1 | 528.7 | 536.5 | 7.8 | 0.18 | 7.636 | 5.224 | 1.462 | 9.476% | 537.2 | 0.2 | 8.254 | 4.733 | 8.5 | -0.059 | 1.744 | 8.41% | -6.32 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 711.1 | 446.6 | 58.5 | 202.3 | 450.3 | 462 | 11.7 | 0.88 | 10.789 | 4.95 | 2 | 6.181% | 464.9 | 1.2 | 13.383 | 4.484 | 14.6 | -0.059 | 2 | 4.791% | -3.13 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 478.3 | 230 | 20.9 | 193.2 | 264.2 | 273.6 | 9.4 | -3.42 | 12.858 | 3.469 | 2 | 5.176% | 276.7 | -4.8 | 17.276 | 3.143 | 12.5 | -0.059 | 2 | 3.765% | -2.15 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 696 | 420 | 0 | 76.2 | 619.8 | 630.5 | 10.7 | -1.39 | 12.075 | 5.279 | 2 | 6.616% | 632.1 | -1.9 | 14.238 | 4.782 | 12.3 | -0.059 | 2 | 5.567% | -5.12 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 221 | 118 | 0 | 11.1 | 209.9 | 213.4 | 3.5 | -0.1 | 3.597 | 1.677 | 2 | 6.428% | 215.6 | -0.1 | 5.838 | 1.519 | 5.7 | -0.059 | 2 | 3.818% | -3.74 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.061 | 940 | 322 | 0 | 44.5 | 895.5 | 908 | 12.5 | -0.62 | 13.119 | 6.932 | 1.893 | 7.648% | 912.8 | -0.9 | 18.198 | 6.318 | 17.3 | -0.059 | 2 | 5.345% | -5.26 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.061 | 940 | 322 | 0 | 44.5 | 895.5 | 908 | 12.5 | -0.62 | 13.119 | 6.932 | 1.893 | 7.648% | 912.8 | -0.9 | 18.198 | 6.318 | 17.3 | -0.059 | 2 | 5.345% | -5.26 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.061 | 940 | 322 | 0 | 44.5 | 895.5 | 908 | 12.5 | -0.62 | 13.119 | 6.932 | 1.893 | 7.648% | 912.8 | -0.9 | 18.198 | 6.318 | 17.3 | -0.059 | 2 | 5.345% | -5.26 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.061 | 940 | 322 | 0 | 44.5 | 895.5 | 908 | 12.5 | -0.62 | 13.119 | 6.932 | 1.893 | 7.648% | 912.8 | -0.9 | 18.198 | 6.318 | 17.3 | -0.059 | 2 | 5.345% | -5.26 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.061 | 78 | 57 | 0 | 19.5 | 58.5 | 59.8 | 1.3 | 0.23 | 1.05 | 0.701 | 1.499 | 6.122% | 59.6 | 0.3 | 0.832 | 0.629 | 1.1 | -0.059 | 1.322 | 6.998% | -5.38 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 264 | 100 | 20 | 117.8 | 126.2 | 127.8 | 1.6 | 0.18 | 1.44 | 1.851 | 0.778 | 16.79% | 129.3 | 0.3 | 2.792 | 1.677 | 3.1 | -0.059 | 1.665 | 8.383% | -4.13 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 835 | 465 | 122.9 | 60.2 | 651.9 | 660.6 | 8.7 | -4.71 | 13.419 | 5.401 | 2 | 9.761% | 664.9 | -6.5 | 19.61 | 4.893 | 13 | -0.059 | 2 | 6.318% | -5.1 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 259 | 165 | 35 | 57.8 | 166.2 | 172.2 | 6 | 0.11 | 5.846 | 1.699 | 2 | 4.393% | 173.1 | 0.2 | 6.734 | 1.539 | 6.9 | -0.059 | 2 | 3.695% | -2.44 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.061 | 663 | 156 | 0 | 32.7 | 630.3 | 632.1 | 1.8 | -4.56 | 6.34 | 5.229 | 1.212 | 37.46% | 631.5 | -6.3 | 7.488 | 4.766 | 1.2 | -0.059 | 1.571 | 54.35% | -53.38 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.061 | 684 | 300 | 40 | 202.7 | 441.3 | 449.9 | 8.6 | 0.86 | 7.704 | 4.885 | 1.577 | 8.089% | 450.5 | 1.2 | 8.007 | 4.425 | 9.2 | -0.059 | 1.809 | 7.314% | -4.87 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.061 | 1060 | 379 | 175 | 100.6 | 784.4 | 786.2 | 1.8 | -14.19 | 15.971 | 6.712 | 2 | 59.89% | 786 | -19.8 | 21.311 | 6.081 | 1.6 | -0.059 | 2 | 65.16% | -49.82 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 645.5 | 254 | 121 | 15.6 | 508.9 | 505.1 | -3.8 | -6.37 | 2.537 | 7.721 | 0.329 | -20.96% | 509.8 | -8.9 | 9.791 | 7.317 | 0.9 | -0.071 | 1.338 | 84.9% | -69.71 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 228 | 165 | 10 | 45 | 173 | 178.8 | 5.8 | 0.18 | 5.632 | 3.209 | 1.755 | 4.853% | 178.8 | 0.2 | 5.525 | 3.041 | 5.8 | -0.071 | 1.817 | 4.657% | -3.67 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.074 | 412 | 70 | 0 | 178.7 | 233.3 | 248 | 14.7 | -0.95 | 15.639 | 4.548 | 2 | 3.461% | 249.1 | -1.3 | 17.12 | 4.221 | 15.8 | -0.071 | 2 | 3.089% | -1.82 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 560 | 135 | 0 | 120.2 | 439.8 | 453.4 | 13.6 | 0.28 | 13.289 | 9.604 | 1.384 | 5.081% | 453.8 | 0.4 | 13.615 | 9.117 | 14 | -0.071 | 1.493 | 4.735% | -3.87 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 420 | 125 | 0 | 97.3 | 322.7 | 331.8 | 9.1 | 0.44 | 8.693 | 6.22 | 1.398 | 5.695% | 331.9 | 0.6 | 8.612 | 5.904 | 9.2 | -0.071 | 1.459 | 5.405% | -4.32 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 410 | 70 | 0 | 148.6 | 261.4 | 269.9 | 8.5 | 2.34 | 6.143 | 6.952 | 0.884 | 5.952% | 269.3 | 3.3 | 4.655 | 6.599 | 7.9 | -0.071 | 0.705 | 6.145% | -4.08 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 746 | 650 | 0 | 52.8 | 693.2 | 713.2 | 20 | 3.24 | 16.774 | 8.408 | 1.995 | 4.603% | 717.7 | 4.5 | 19.994 | 7.805 | 24.5 | -0.071 | 2 | 3.605% | -3.49 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 749 | 310 | 0 | 136.9 | 612.1 | 615.1 | 3 | -1.25 | 4.225 | 8.703 | 0.485 | 30.81% | 616.4 | -1.7 | 5.996 | 8.078 | 4.3 | -0.071 | 0.742 | 20.63% | -17.54 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 326 | 242 | 0 | 34 | 292 | 301.2 | 9.2 | 0.14 | 9.067 | 4.799 | 1.889 | 4.373% | 302.3 | 0.2 | 10.124 | 4.548 | 10.3 | -0.071 | 2 | 3.748% | -3.49 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.074 | 105 | 12 | 0 | 92.6 | 12.4 | 14.9 | 2.5 | -0.04 | 2.563 | 2.019 | 1.269 | 5.191% | 14.7 | 0 | 2.409 | 1.917 | 2.3 | -0.071 | 1.257 | 5.414% | -0.65 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 420 | 50 | 0 | 287.6 | 132.4 | 149.8 | 17.4 | 2.87 | 14.553 | 5.157 | 2 | 2.979% | 151.5 | 4 | 15.13 | 4.896 | 19.1 | -0.071 | 2 | 2.604% | -0.85 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 60 | 21 | 13 | 9.5 | 37.5 | 38.4 | 0.9 | -1.39 | 2.219 | 0.692 | 2 | 8.254% | 38.1 | -1.9 | 2.531 | 0.656 | 0.6 | -0.071 | 2 | 11.88% | -7.66 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.074 | 470 | 180 | 0 | 11.8 | 458.2 | 459 | 0.8 | -0.05 | 0.821 | 4.975 | 0.165 | 72.53% | 459.5 | -0.1 | 1.426 | 4.618 | 1.3 | -0.071 | 0.309 | 42.83% | -43.43 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 470 | 180 | 0 | 11.8 | 458.2 | 459 | 0.8 | -0.05 | 0.821 | 4.975 | 0.165 | 72.53% | 459.5 | -0.1 | 1.426 | 4.618 | 1.3 | -0.071 | 0.309 | 42.83% | -43.43 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 470 | 180 | 0 | 11.8 | 458.2 | 459 | 0.8 | -0.05 | 0.821 | 4.975 | 0.165 | 72.53% | 459.5 | -0.1 | 1.426 | 4.618 | 1.3 | -0.071 | 0.309 | 42.83% | -43.43 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 470 | 180 | 0 | 11.8 | 458.2 | 459 | 0.8 | -0.05 | 0.821 | 4.975 | 0.165 | 72.53% | 459.5 | -0.1 | 1.426 | 4.618 | 1.3 | -0.071 | 0.309 | 42.83% | -43.43 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.074 | 226 | 150 | 0 | 23.3 | 202.7 | 207.8 | 5.1 | -0.01 | 5.125 | 4.028 | 1.273 | 5.471% | 207.4 | 0 | 4.738 | 3.823 | 4.7 | -0.071 | 1.239 | 5.696% | -5.31 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.074 | 233 | 150 | 0 | 29.1 | 203.9 | 208.8 | 4.9 | -0.09 | 4.908 | 4.167 | 1.178 | 5.87% | 208.7 | -0.1 | 4.926 | 3.956 | 4.8 | -0.071 | 1.245 | 5.75% | -5.23 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.074 | 234 | 150 | 0 | 29 | 205 | 210.2 | 5.2 | -0.03 | 5.21 | 4.198 | 1.241 | 5.555% | 209.6 | 0 | 4.603 | 3.985 | 4.6 | -0.071 | 1.155 | 6.026% | -5.49 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.074 | 225 | 150 | 0 | 24.8 | 200.2 | 204.6 | 4.4 | 0.29 | 4.091 | 3.982 | 1.028 | 6.313% | 205.1 | 0.4 | 4.488 | 3.78 | 4.9 | -0.071 | 1.187 | 5.439% | -5.03 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 516 | 334 | 0 | 23.3 | 492.7 | 503.1 | 10.4 | -0.06 | 10.44 | 7.596 | 1.374 | 6.122% | 501.9 | -0.1 | 9.282 | 7.198 | 9.2 | -0.071 | 1.29 | 6.64% | -6.6 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 518.6 | 309.7 | 8.4 | 16.3 | 493.9 | 506.6 | 12.7 | -1.44 | 14.194 | 7.51 | 1.89 | 5.039% | 509.3 | -2 | 17.398 | 7.117 | 15.4 | -0.071 | 2 | 3.987% | -3.95 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.074 | 51 | 0 | 0 | 13.4 | 37.6 | 39.3 | 1.7 | -0.81 | 2.446 | 0.99 | 2 | 3.717% | 39.4 | -1.1 | 2.88 | 0.94 | 1.8 | -0.071 | 2 | 3.369% | -2.56 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | GT | -0.074 | 229 | 150 | 0 | 21 | 208 | 212 | 4 | 0.12 | 3.956 | 3.591 | 1.102 | 7.068% | 212.4 | 0.2 | 4.279 | 3.409 | 4.4 | -0.071 | 1.255 | 6.165% | -5.82 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.074 | 228 | 150 | 0 | 22.2 | 205.8 | 209.9 | 4.1 | 0.34 | 3.766 | 3.556 | 1.059 | 6.865% | 210.1 | 0.5 | 3.819 | 3.376 | 4.3 | -0.071 | 1.131 | 6.281% | -5.9 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.074 | 226 | 150 | 0 | 23.1 | 202.9 | 206.9 | 4 | 0.17 | 3.845 | 3.504 | 1.097 | 6.975% | 207.4 | 0.2 | 4.249 | 3.326 | 4.5 | -0.071 | 1.278 | 5.949% | -5.55 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.074 | 228 | 150 | 0 | 19.9 | 208.1 | 211.7 | 3.6 | 0.47 | 3.12 | 3.578 | 0.872 | 7.819% | 212.1 | 0.6 | 3.389 | 3.396 | 4 | -0.071 | 0.998 | 6.752% | -6.41 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.074 | 231 | 150 | 0 | 16 | 215 | 220.1 | 5.1 | 0 | 5.052 | 3.555 | 1.421 | 5.592% | 219.7 | 0 | 4.626 | 3.375 | 4.7 | -0.071 | 1.371 | 5.822% | -5.64 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.074 | 240 | 110 | 0 | 22.4 | 217.6 | 222.9 | 5.3 | 0.67 | 4.645 | 3.716 | 1.25 | 5.59% | 222.9 | 0.9 | 4.372 | 3.527 | 5.3 | -0.071 | 1.24 | 5.364% | -5.06 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.074 | 600 | 250 | 54.7 | 73.1 | 472.2 | 490.1 | 17.9 | -0.25 | 18.18 | 8.028 | 2 | 4.136% | 509.5 | -0.4 | 37.674 | 7.607 | 37.3 | -0.071 | 2 | 1.904% | -1.56 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 716.5 | 454.4 | 26.1 | 102 | 588.4 | 607.6 | 19.2 | -0.06 | 19.209 | 10.163 | 1.89 | 4.604% | 607.7 | -0.1 | 19.382 | 9.631 | 19.3 | -0.071 | 2 | 4.395% | -3.76 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 329.1 | 205.8 | 11.6 | 46 | 271.5 | 281.2 | 9.7 | 0.47 | 9.224 | 4.674 | 1.973 | 4.187% | 287.1 | 0.7 | 14.957 | 4.429 | 15.6 | -0.071 | 2 | 2.498% | -2.14 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 716.3 | 446.2 | 30.1 | 126.1 | 560.1 | 577.4 | 17.3 | 1 | 16.295 | 10.101 | 1.613 | 5.108% | 584 | 1.4 | 22.49 | 9.572 | 23.9 | -0.071 | 2 | 3.548% | -2.89 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.074 | 49.9 | 24 | 0 | 9.6 | 40.3 | 41.9 | 1.6 | 0.1 | 1.443 | 0.866 | 1.665 | 3.864% | 43.9 | 0.1 | 3.435 | 0.817 | 3.6 | -0.071 | 2 | 1.648% | -1.37 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 49.9 | 24 | 0 | 9.5 | 40.4 | 42 | 1.6 | 0.9 | 0.658 | 0.866 | 0.76 | 3.864% | 43.8 | 1.3 | 2.132 | 0.816 | 3.4 | -0.071 | 2 | 1.745% | -1.46 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 474.4 | 230 | 0 | 31.3 | 443.1 | 450.6 | 7.5 | -0.3 | 7.737 | 6.983 | 1.108 | 7.805% | 452.2 | -0.4 | 9.496 | 6.618 | 9.1 | -0.071 | 1.435 | 6.172% | -6 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 115 | 45 | 0 | 67.2 | 47.8 | 55 | 7.2 | 0.14 | 7.011 | 1.693 | 2 | 1.974% | 56.8 | 0.2 | 8.761 | 1.604 | 9 | -0.071 | 2 | 1.515% | -0.65 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.074 | 55.8 | 22.5 | 0 | 10.3 | 45.5 | 47.9 | 2.4 | 0.28 | 2.138 | 0.969 | 2 | 2.879% | 49.7 | 0.4 | 3.798 | 0.914 | 4.2 | -0.071 | 2 | 1.579% | -1.33 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 55.8 | 22.5 | 0 | 9.8 | 46 | 47.4 | 1.4 | 0.38 | 1.048 | 0.969 | 1.081 | 4.936% | 49.8 | 0.5 | 3.331 | 0.914 | 3.8 | -0.071 | 2 | 1.745% | -1.49 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 940.5 | 322 | 0 | 203.2 | 737.3 | 755.7 | 18.4 | -0.27 | 18.713 | 13.695 | 1.366 | 6.306% | 760.4 | -0.4 | 23.51 | 13.001 | 23.1 | -0.071 | 1.808 | 4.819% | -3.94 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 940.5 | 322 | 0 | 203.2 | 737.3 | 755.7 | 18.4 | -0.27 | 18.713 | 13.695 | 1.366 | 6.306% | 760.4 | -0.4 | 23.51 | 13.001 | 23.1 | -0.071 | 1.808 | 4.819% | -3.94 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 940.5 | 322 | 0 | 203.2 | 737.3 | 755.7 | 18.4 | -0.27 | 18.713 | 13.695 | 1.366 | 6.306% | 760.4 | -0.4 | 23.51 | 13.001 | 23.1 | -0.071 | 1.808 | 4.819% | -3.94 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 940.5 | 322 | 0 | 203.2 | 737.3 | 755.7 | 18.4 | -0.27 | 18.713 | 13.695 | 1.366 | 6.306% | 760.4 | -0.4 | 23.51 | 13.001 | 23.1 | -0.071 | 1.808 | 4.819% | -3.94 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 41 | 13 | 0 | 27.4 | 13.6 | 14 | 0.4 | 0.06 | 0.347 | 0.566 | 0.614 | 12.78% | 13.6 | 0.1 | -0.082 | 0.525 | 0 | -0.071 | 0 | 0% |  | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 233.9 | 130 | 0 | 42.5 | 191.4 | 195.9 | 4.5 | 0.5 | 3.997 | 3.443 | 1.161 | 6.417% | 195.6 | 0.7 | 3.443 | 3.263 | 4.2 | -0.071 | 1.055 | 6.597% | -5.61 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 263 | 165 | 35 | 13.4 | 214.6 | 221.2 | 6.6 | -0.06 | 6.647 | 3.356 | 1.98 | 4.919% | 223.5 | -0.1 | 8.997 | 3.181 | 8.9 | -0.071 | 2 | 3.5% | -2.97 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.074 | 238 | 102 | 0 | 112.3 | 125.7 | 135 | 9.3 | 1.32 | 8 | 3.13 | 2 | 3.162% | 134.6 | 1.8 | 7.062 | 2.905 | 8.9 | -0.071 | 2 | 3.171% | -1.74 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.074 | 537 | 260 | 0 | 83.4 | 453.6 | 461.3 | 7.7 | 3.19 | 4.473 | 6.943 | 0.644 | 8.609% | 468.2 | 4.4 | 10.095 | 6.444 | 14.6 | -0.071 | 1.566 | 4.356% | -3.83 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 674 | 300 | 40 | 160.2 | 473.8 | 493.1 | 19.3 | 2.59 | 16.755 | 9.333 | 1.795 | 4.309% | 488.6 | 3.6 | 11.253 | 8.845 | 14.8 | -0.071 | 1.272 | 5.391% | -3.95 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.076 | 560 | 200 | 0 | 334.1 | 225.9 | 231.6 | 5.7 | 0.31 | 5.36 | 8.677 | 0.618 | 12.45% | 231.5 | 0.4 | 5.12 | 8.448 | 5.6 | -0.075 | 0.606 | 12.51% | -5.1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 420 | 125 | 0 | 278.8 | 141.2 | 143 | 1.8 | -1.83 | 3.65 | 6.042 | 0.604 | 29.57% | 142.9 | -2.5 | 4.183 | 5.883 | 1.7 | -0.075 | 0.711 | 30.9% | -10.5 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 417 | 125 | 0 | 279.5 | 137.5 | 145.5 | 8 | 0.44 | 7.554 | 5.991 | 1.261 | 6.606% | 152.7 | 0.6 | 14.591 | 5.833 | 15.2 | -0.075 | 2 | 3.431% | -1.14 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 226.4 | 168 | 12 | 45.2 | 169.2 | 175.3 | 6.1 | 0 | 6.056 | 3.363 | 1.801 | 4.706% | 176.5 | 0 | 7.3 | 3.272 | 7.3 | -0.075 | 2 | 3.881% | -2.93 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 236.4 | 165 | 18 | 29.5 | 188.9 | 194.8 | 5.9 | 0.89 | 5.05 | 3.426 | 1.474 | 5.08% | 193.9 | 1.2 | 3.797 | 3.333 | 5 | -0.075 | 1.139 | 5.916% | -4.78 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.076 | 746 | 142 | 0 | 602.4 | 143.6 | 163.2 | 19.6 | -1.21 | 20.831 | 9.444 | 2 | 4.824% | 164 | -1.7 | 22.051 | 9.1 | 20.4 | -0.075 | 2 | 4.574% | -0.89 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 245 | 159 | 0 | 85.3 | 159.7 | 164.1 | 4.4 | 0.11 | 4.279 | 3.843 | 1.113 | 7.059% | 165 | 0.2 | 5.128 | 3.739 | 5.3 | -0.075 | 1.372 | 5.784% | -3.81 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 62 | 10 | 25 | 5.7 | 31.3 | 37 | 5.7 | 0.89 | 4.83 | 0.58 | 2 | 1.383% | 36.8 | 1.2 | 4.24 | 0.565 | 5.5 | -0.075 | 2 | 1.414% | -0.72 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.076 | 645 | 300 | 0 | 127.9 | 517.1 | 537.8 | 20.7 | -0.53 | 21.21 | 11.506 | 1.843 | 3.948% | 535.8 | -0.7 | 19.425 | 11.202 | 18.7 | -0.075 | 1.734 | 4.313% | -3.5 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 324 | 255 | 0 | 37.9 | 286.1 | 296.8 | 10.7 | 2.19 | 8.505 | 5.083 | 1.673 | 3.838% | 298.1 | 3 | 9.007 | 4.945 | 12 | -0.075 | 1.822 | 3.377% | -3.02 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.076 | 105 | 12 | 0 | 92 | 13 | 14.8 | 1.8 | 0.15 | 1.625 | 2.148 | 0.757 | 7.405% | 14.4 | 0.2 | 1.157 | 2.091 | 1.4 | -0.075 | 0.553 | 9.395% | -1.16 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 56 | 6 | 0 | 39.8 | 16.2 | 20.6 | 4.4 | -0.79 | 5.218 | 0.878 | 2 | 1.619% | 25.9 | -1.1 | 10.799 | 0.855 | 9.7 | -0.075 | 2 | 0.7246% | -0.21 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 325 | 141 | 0 | 33 | 292 | 301.8 | 9.8 | 1.79 | 7.988 | 5.098 | 1.567 | 4.204% | 301.9 | 2.5 | 7.311 | 4.96 | 9.9 | -0.075 | 1.474 | 4.106% | -3.73 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.076 | 583.2 | 149.7 | 0 | 29.5 | 553.7 | 567.8 | 14.1 | -0.11 | 14.225 | 8.48 | 1.678 | 5.241% | 566.3 | -0.1 | 12.748 | 8.256 | 12.6 | -0.075 | 1.544 | 5.788% | -5.56 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 583.2 | 149.7 | 0 | 29.5 | 553.7 | 567.8 | 14.1 | -0.11 | 14.225 | 8.48 | 1.678 | 5.241% | 566.3 | -0.1 | 12.748 | 8.256 | 12.6 | -0.075 | 1.544 | 5.788% | -5.56 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 390 | 215 | 83.9 | 89.1 | 217 | 222.8 | 5.8 | 0 | 5.797 | 4.802 | 1.207 | 8.522% | 223.4 | 0 | 6.367 | 4.671 | 6.4 | -0.075 | 1.363 | 7.622% | -4.29 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.076 | 470 | 180 | 0 | 240.9 | 229.1 | 231.5 | 2.4 | -1.94 | 4.427 | 4.7 | 0.942 | 24.83% | 229.6 | -2.7 | 3.251 | 4.529 | 0.5 | -0.075 | 0.718 | 117.6% | -57.93 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 470 | 180 | 0 | 240.9 | 229.1 | 231.5 | 2.4 | -1.94 | 4.427 | 4.7 | 0.942 | 24.83% | 229.6 | -2.7 | 3.251 | 4.529 | 0.5 | -0.075 | 0.718 | 117.6% | -57.93 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 470 | 180 | 0 | 240.9 | 229.1 | 231.5 | 2.4 | -1.94 | 4.427 | 4.7 | 0.942 | 24.83% | 229.6 | -2.7 | 3.251 | 4.529 | 0.5 | -0.075 | 0.718 | 117.6% | -57.93 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 470 | 180 | 0 | 240.9 | 229.1 | 231.5 | 2.4 | -1.94 | 4.427 | 4.7 | 0.942 | 24.83% | 229.6 | -2.7 | 3.251 | 4.529 | 0.5 | -0.075 | 0.718 | 117.6% | -57.93 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.076 | 235 | 150 | 0 | 82.7 | 152.3 | 158 | 5.7 | -0.72 | 6.395 | 3.961 | 1.615 | 5.227% | 157.7 | -1 | 6.438 | 3.856 | 5.4 | -0.075 | 1.67 | 5.445% | -3.57 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.076 | 234 | 150 | 0 | 62.3 | 171.7 | 171.3 | -0.4 | -5.34 | 4.893 | 4.042 | 1.211 | -74.17% | 169.3 | -7.4 | 5.039 | 3.935 | -2.4 | -0.075 | 1.28 | -12.2% | 9.05 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 177.3 | 0 | 40 | 23.3 | 114 | 122.5 | 8.5 | 2.28 | 6.244 | 2.154 | 2 | 2.645% | 119.1 | 3.2 | 1.904 | 2.095 | 5.1 | -0.075 | 0.909 | 4.351% | -2.83 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 284 | 165 | 40 | 54.2 | 189.8 | 185.8 | -4 | -6.02 | 2.019 | 3.828 | 0.528 | -9% | 185.5 | -8.4 | 4.101 | 3.724 | -4.3 | -0.075 | 1.101 | -8.262% | 5.58 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 620 | 305 | 111 | 176.3 | 332.7 | 336.7 | 4 | -4.35 | 8.285 | 7.985 | 1.038 | 19.64% | 341.7 | -6.1 | 15.062 | 7.768 | 9 | -0.075 | 1.939 | 8.614% | -4.68 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 521.2 | 309.7 | 34.8 | 16.1 | 470.3 | 481.9 | 11.6 | 0.19 | 11.402 | 7.631 | 1.494 | 5.694% | 480.1 | 0.3 | 9.543 | 7.424 | 9.8 | -0.075 | 1.285 | 6.651% | -6.08 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.076 | 239 | 150 | 0 | 26.5 | 212.5 | 216.8 | 4.3 | -0.62 | 4.899 | 4.031 | 1.215 | 7.047% | 216.9 | -0.9 | 5.236 | 3.925 | 4.4 | -0.075 | 1.334 | 6.796% | -6.11 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.076 | 241 | 150 | 0 | 27.6 | 213.4 | 218 | 4.6 | -0.47 | 5.055 | 4.073 | 1.241 | 6.642% | 217.9 | -0.6 | 5.173 | 3.965 | 4.5 | -0.075 | 1.305 | 6.701% | -6 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.076 | 243 | 150 | 0 | 20.1 | 222.9 | 228 | 5.1 | -0.57 | 5.638 | 4.052 | 1.391 | 6.041% | 227.6 | -0.8 | 5.445 | 3.945 | 4.7 | -0.075 | 1.38 | 6.469% | -6 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.076 | 450 | 220 | 0 | 177.3 | 272.7 | 284 | 11.3 | -1.83 | 13.195 | 9.296 | 1.419 | 5.047% | 282.4 | -2.5 | 12.247 | 9.051 | 9.7 | -0.075 | 1.353 | 5.802% | -3.56 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.076 | 450 | 220 | 0 | 175.8 | 274.2 | 286.6 | 12.4 | 0.62 | 11.857 | 9.296 | 1.275 | 4.599% | 286 | 0.9 | 10.964 | 9.051 | 11.8 | -0.075 | 1.211 | 4.769% | -2.94 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.076 | 810 | 300 | 0 | 493.1 | 316.9 | 332.2 | 15.3 | 1.71 | 13.585 | 16.734 | 0.812 | 6.708% | 333 | 2.4 | 13.644 | 16.292 | 16.1 | -0.075 | 0.837 | 6.291% | -2.49 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.076 | 530 | 210 | 0 | 209.3 | 320.7 | 327 | 6.3 | -1.94 | 8.232 | 10.949 | 0.752 | 10.66% | 330 | -2.7 | 11.984 | 10.66 | 9.3 | -0.075 | 1.124 | 7.127% | -4.36 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.076 | 540 | 210 | 0 | 240.1 | 299.9 | 306.5 | 6.6 | -2.24 | 8.839 | 11.156 | 0.792 | 10.37% | 310.1 | -3.1 | 13.288 | 10.861 | 10.2 | -0.075 | 1.223 | 6.62% | -3.72 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.076 | 765 | 300 | 0 | 282.8 | 482.2 | 498.1 | 15.9 | 5.46 | 10.418 | 15.804 | 0.659 | 6.096% | 500.9 | 7.6 | 11.121 | 15.387 | 18.7 | -0.075 | 0.723 | 5.115% | -3.26 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 650 | 189.8 | 0 | 323.1 | 326.9 | 340 | 13.1 | 1.9 | 11.187 | 7.884 | 1.419 | 6.287% | 344.1 | 2.6 | 14.476 | 7.676 | 17.2 | -0.075 | 1.886 | 4.725% | -2.41 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 650 | 189.8 | 0 | 323.1 | 326.9 | 340 | 13.1 | 1.9 | 11.187 | 7.884 | 1.419 | 6.287% | 344.1 | 2.6 | 14.476 | 7.676 | 17.2 | -0.075 | 1.886 | 4.725% | -2.41 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 650 | 189.8 | 0 | 323.1 | 326.9 | 340 | 13.1 | 1.9 | 11.187 | 7.884 | 1.419 | 6.287% | 344.1 | 2.6 | 14.476 | 7.676 | 17.2 | -0.075 | 1.886 | 4.725% | -2.41 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 650 | 189.8 | 0 | 323.1 | 326.9 | 340 | 13.1 | 1.9 | 11.187 | 7.884 | 1.419 | 6.287% | 344.1 | 2.6 | 14.476 | 7.676 | 17.2 | -0.075 | 1.886 | 4.725% | -2.41 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 650 | 189.8 | 0 | 323.1 | 326.9 | 340 | 13.1 | 1.9 | 11.187 | 7.884 | 1.419 | 6.287% | 344.1 | 2.6 | 14.476 | 7.676 | 17.2 | -0.075 | 1.886 | 4.725% | -2.41 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 489.7 | 230 | 21.7 | 193.1 | 274.9 | 290.4 | 15.5 | 2.71 | 12.739 | 7.342 | 1.735 | 4.004% | 306.3 | 3.8 | 27.595 | 7.142 | 31.4 | -0.075 | 2 | 1.95% | -1.11 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 687 | 420 | 0 | 98.8 | 588.2 | 610.9 | 22.7 | -1.44 | 24.153 | 10.777 | 2 | 3.835% | 611.2 | -2 | 24.967 | 10.484 | 23 | -0.075 | 2 | 3.735% | -3.24 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 273.1 | 118 | 60 | 54.5 | 158.6 | 164.6 | 6 | 0.99 | 5.017 | 3.342 | 1.501 | 5.77% | 167.8 | 1.4 | 7.834 | 3.252 | 9.2 | -0.075 | 2 | 3.714% | -2.18 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.076 | 78 | 57 | 0 | 20.5 | 57.5 | 59.5 | 2 | -0.29 | 2.272 | 1.442 | 1.575 | 4.954% | 59.2 | -0.4 | 2.088 | 1.4 | 1.7 | -0.075 | 1.492 | 5.752% | -4.27 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 827 | 465 | 129.2 | 146.3 | 551.5 | 556.6 | 5.1 | -9.26 | 14.391 | 10.946 | 1.315 | 20.55% | 555 | -12.9 | 16.45 | 10.648 | 3.5 | -0.075 | 1.545 | 29.54% | -19.95 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 263 | 165 | 35 | 61.4 | 166.6 | 174.7 | 8.1 | 0.15 | 7.899 | 3.577 | 2 | 4.116% | 177.6 | 0.2 | 10.763 | 3.48 | 11 | -0.075 | 2 | 2.991% | -1.92 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.076 | 663 | 156 | 0 | 46.4 | 616.6 | 635.6 | 19 | 5.07 | 13.978 | 10.472 | 1.335 | 4.421% | 637.7 | 7 | 14.062 | 10.196 | 21.1 | -0.075 | 1.379 | 3.929% | -3.7 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 681 | 300 | 40 | 198.2 | 442.8 | 463 | 20.2 | -0.86 | 21.063 | 10.056 | 2 | 4.272% | 457.9 | -1.2 | 16.274 | 9.783 | 15.1 | -0.075 | 1.663 | 5.639% | -3.71 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 1068 | 433 | 98 | 26.9 | 943.1 | 947.5 | 4.4 | 0.21 | 4.155 | 15.217 | 0.273 | 30.75% | 948.4 | 0.3 | 4.972 | 14.803 | 5.3 | -0.075 | 0.336 | 25.19% | -22.53 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.099 | 135.8 | 0 | 0 | 12.7 | 123.1 | 133.4 | 10.3 | 0.95 | 9.285 | 4.047 | 2 | 2.178% | 136.1 | 1.3 | 11.679 | 4.144 | 13 | -0.101 | 2 | 1.761% | -1.56 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | FOSS | -0.099 | 230 | 60 | 0 | 167.3 | 62.7 | 69.2 | 6.5 | -0.51 | 7.04 | 5.316 | 1.324 | 5.847% | 73 | -0.7 | 11.031 | 5.474 | 10.3 | -0.101 | 2 | 3.764% | -1 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 412 | 70 | 0 | 172.9 | 239.1 | 247.2 | 8.1 | -2.22 | 10.328 | 8.013 | 1.289 | 8.4% | 251.1 | -3.1 | 15.102 | 8.25 | 12 | -0.101 | 1.831 | 5.784% | -3.28 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 420 | 70 | 0 | 206.4 | 213.6 | 223.3 | 9.7 | -0.05 | 9.819 | 9.043 | 1.086 | 7.147% | 223.2 | -0.1 | 9.74 | 9.259 | 9.6 | -0.101 | 1.052 | 7.368% | -3.67 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 410 | 70 | 0 | 175.1 | 234.9 | 242.7 | 7.8 | 0.13 | 7.666 | 9.917 | 0.773 | 8.677% | 241.1 | 0.2 | 6.052 | 10.155 | 6.2 | -0.101 | 0.596 | 11.14% | -6.25 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 749 | 95 | 0 | 45.4 | 703.6 | 718.7 | 15.1 | -0.86 | 15.971 | 14.796 | 1.079 | 8.188% | 724.4 | -1.2 | 21.993 | 15.234 | 20.8 | -0.101 | 1.444 | 6.064% | -5.58 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 616 | 442 | 20 | 15.7 | 580.3 | 593.5 | 13.2 | 0.75 | 12.454 | 13.607 | 0.915 | 7.702% | 595.9 | 1 | 14.499 | 13.94 | 15.6 | -0.101 | 1.04 | 6.649% | -6.14 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.099 | 105 | 12 | 0 | 92.3 | 12.7 | 16.2 | 3.5 | 0.4 | 3.126 | 3.094 | 1.01 | 4.958% | 16.3 | 0.6 | 3 | 3.169 | 3.6 | -0.101 | 0.947 | 4.918% | -0.57 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 315 | 50 | 0 | 89.8 | 225.2 | 247.5 | 22.3 | -0.23 | 22.516 | 6.728 | 2 | 2.332% | 249.5 | -0.3 | 24.583 | 6.888 | 24.3 | -0.101 | 2 | 2.183% | -1.53 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 420 | 50 | 0 | 212.6 | 207.4 | 227.6 | 20.2 | -0.55 | 20.715 | 9.129 | 2 | 3.432% | 230 | -0.8 | 23.371 | 9.348 | 22.6 | -0.101 | 2 | 3.13% | -1.51 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.099 | 152 | 80 | 0 | 13.4 | 138.6 | 146 | 7.4 | -0.32 | 7.713 | 4.084 | 1.888 | 3.393% | 146.6 | -0.4 | 8.459 | 4.193 | 8 | -0.101 | 2 | 3.202% | -2.86 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.099 | 322 | 135 | 0 | 12.2 | 309.8 | 318.2 | 8.4 | 0.12 | 8.314 | 7.352 | 1.131 | 6.328% | 326 | 0.2 | 16.06 | 7.531 | 16.2 | -0.101 | 2 | 3.348% | -3.15 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.099 | 584.1 | 148.6 | 0 | 15.3 | 568.8 | 580.6 | 11.8 | -0.07 | 11.846 | 12.188 | 0.972 | 8.17% | 576.2 | -0.1 | 7.433 | 12.479 | 7.4 | -0.101 | 0.596 | 13.29% | -12.68 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 584.1 | 148.6 | 0 | 15.3 | 568.8 | 580.6 | 11.8 | -0.07 | 11.846 | 12.188 | 0.972 | 8.17% | 576.2 | -0.1 | 7.433 | 12.479 | 7.4 | -0.101 | 0.596 | 13.29% | -12.68 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | STM | -0.099 | 295.4 | 54.4 | 0 | 25.9 | 269.5 | 280.2 | 10.7 | -0.04 | 10.679 | 8.408 | 1.27 | 4.558% | 280.2 | -0.1 | 10.679 | 8.609 | 10.7 | -0.101 | 1.24 | 4.65% | -4.15 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | COGN | -0.099 | 225 | 150 | 5 | 19.7 | 200.3 | 206.6 | 6.3 | 0.22 | 6.071 | 5.974 | 1.016 | 5.897% | 206.6 | 0.3 | 6.026 | 6.116 | 6.3 | -0.101 | 0.985 | 6.016% | -5.24 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.099 | 230 | 150 | 12 | 18.7 | 199.3 | 205.3 | 6 | 0.03 | 5.984 | 5.902 | 1.014 | 6.33% | 205.7 | 0 | 6.287 | 6.044 | 6.4 | -0.101 | 1.04 | 6.054% | -5.13 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.099 | 231 | 150 | 12 | 18.7 | 200.3 | 206.5 | 6.2 | -0.07 | 6.248 | 5.946 | 1.051 | 6.152% | 206.7 | -0.1 | 6.471 | 6.088 | 6.4 | -0.101 | 1.063 | 6.08% | -5.16 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.099 | 224 | 150 | 5 | 19.6 | 199.4 | 205 | 5.6 | 0.01 | 5.587 | 5.93 | 0.942 | 6.605% | 205.9 | 0 | 6.545 | 6.072 | 6.5 | -0.101 | 1.078 | 5.805% | -5.06 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.099 | 375 | 100 | 0 | 25.9 | 349.1 | 374.7 | 25.6 | 0.13 | 25.488 | 7.194 | 2 | 2.419% | 381 | 0.2 | 31.688 | 7.407 | 31.9 | -0.101 | 2 | 1.981% | -1.8 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 425 | 120 | 0 | 85.3 | 339.7 | 355.4 | 15.7 | -0.44 | 16.157 | 9.662 | 1.672 | 4.468% | 355.3 | -0.6 | 16.219 | 9.893 | 15.6 | -0.101 | 1.639 | 4.588% | -3.59 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 162.1 | 0 | 13.3 | 25.8 | 123 | 131.7 | 8.7 | -0.43 | 9.168 | 3.397 | 2 | 3.078% | 126.2 | -0.6 | 3.775 | 3.48 | 3.2 | -0.101 | 1.085 | 8.536% | -6.33 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.099 | 616 | 305 | 111 | 22.2 | 482.8 | 496.2 | 13.4 | -0.55 | 14.038 | 11.53 | 1.218 | 7.587% | 500.7 | -0.8 | 18.712 | 11.811 | 17.9 | -0.101 | 1.584 | 5.795% | -4.45 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.099 | 88 | 35 | 0 | 28.8 | 59.2 | 64.3 | 5.1 | 0.11 | 5.036 | 2.365 | 2 | 2.853% | 65.3 | 0.1 | 5.988 | 2.427 | 6.1 | -0.101 | 2 | 2.433% | -1.6 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.099 | 791 | 258 | 0 | 80.5 | 710.5 | 728.4 | 17.9 | -0.99 | 18.899 | 17.337 | 1.09 | 7.293% | 729.3 | -1.4 | 20.167 | 17.752 | 18.8 | -0.101 | 1.136 | 7.084% | -6.23 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 523 | 45 | 0 | 166.1 | 356.9 | 365.6 | 8.7 | -0.04 | 8.724 | 12.412 | 0.703 | 9.922% | 372.8 | -0.1 | 15.973 | 12.709 | 15.9 | -0.101 | 1.257 | 5.539% | -3.7 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 530 | 320 | 0 | 166.1 | 363.9 | 370.6 | 6.7 | 1.52 | 5.167 | 10.645 | 0.485 | 13.06% | 374.2 | 2.1 | 8.216 | 10.9 | 10.3 | -0.101 | 0.754 | 8.665% | -5.83 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.099 | 230 | 150 | 12 | 14.2 | 203.8 | 208.1 | 4.3 | 0.21 | 4.073 | 5.15 | 0.791 | 8.832% | 208.4 | 0.3 | 4.376 | 5.273 | 4.6 | -0.101 | 0.83 | 8.423% | -7.3 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.099 | 229 | 150 | 12 | 14.4 | 202.6 | 207.7 | 5.1 | 0.42 | 4.744 | 5.11 | 0.928 | 7.414% | 208.1 | 0.6 | 4.941 | 5.232 | 5.5 | -0.101 | 0.944 | 7.014% | -6.07 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.099 | 225 | 150 | 12 | 13.6 | 199.4 | 204.3 | 4.9 | 0.15 | 4.768 | 4.981 | 0.957 | 7.582% | 204.9 | 0.2 | 5.355 | 5.101 | 5.5 | -0.101 | 1.05 | 6.892% | -5.98 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.099 | 231 | 150 | 12 | 14.5 | 204.5 | 208.8 | 4.3 | 0.25 | 4.066 | 5.181 | 0.785 | 8.871% | 209.4 | 0.4 | 4.543 | 5.305 | 4.9 | -0.101 | 0.856 | 7.941% | -6.88 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.099 | 230 | 150 | 12 | 7.6 | 210.4 | 215.4 | 5 | 0.11 | 4.952 | 5.047 | 0.981 | 7.596% | 215.8 | 0.2 | 5.247 | 5.168 | 5.4 | -0.101 | 1.015 | 7.175% | -6.42 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.099 | 239 | 110 | 12 | 14.6 | 212.4 | 218.1 | 5.7 | 0.34 | 5.351 | 5.28 | 1.013 | 6.923% | 218.3 | 0.5 | 5.372 | 5.407 | 5.9 | -0.101 | 0.994 | 6.824% | -5.94 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.099 | 204 | 40 | 0 | 163.9 | 40.1 | 50.9 | 10.8 | 0.26 | 10.492 | 5.872 | 1.787 | 3.119% | 52.4 | 0.4 | 11.889 | 6.012 | 12.3 | -0.101 | 1.977 | 2.794% | -0.54 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | LIG | FOSS | -0.099 | 685 | 300 | 0 | 26.9 | 658.1 | 672.4 | 14.3 | 4.27 | 9.985 | 20.409 | 0.489 | 7.906% | 677.2 | 5.9 | 13.121 | 20.897 | 19.1 | -0.101 | 0.628 | 6.039% | -5.68 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 702.1 | 441.1 | 50.4 | 72.7 | 579 | 602.2 | 23.2 | -0.35 | 23.499 | 14.879 | 1.579 | 4.995% | 614.3 | -0.5 | 35.75 | 15.242 | 35.3 | -0.101 | 2 | 3.349% | -2.71 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.099 | 49.8 | 24 | 0 | 11.3 | 38.5 | 40.6 | 2.1 | 0.03 | 2.063 | 1.338 | 1.541 | 3.926% | 45.9 | 0 | 7.405 | 1.374 | 7.4 | -0.101 | 2 | 1.137% | -0.85 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 49.7 | 24 | 0 | 11.4 | 38.3 | 40.1 | 1.8 | 0.14 | 1.676 | 1.336 | 1.255 | 4.572% | 44.7 | 0.2 | 6.218 | 1.371 | 6.4 | -0.101 | 2 | 1.312% | -0.98 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 461.1 | 230 | 10.2 | 53.5 | 397.4 | 411.3 | 13.9 | 0.71 | 13.153 | 10.295 | 1.278 | 5.476% | 415.7 | 1 | 17.301 | 10.546 | 18.3 | -0.101 | 1.64 | 4.243% | -3.58 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.099 | 114 | 45 | 0 | 15.2 | 98.8 | 103.5 | 4.7 | 0.09 | 4.563 | 2.603 | 1.753 | 4.008% | 103.9 | 0.1 | 4.945 | 2.666 | 5.1 | -0.101 | 1.855 | 3.768% | -3.19 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.099 | 55.6 | 22.5 | 0 | 10.2 | 45.4 | 47.6 | 2.2 | -0.17 | 2.285 | 1.494 | 1.53 | 4.183% | 48.2 | -0.2 | 2.952 | 1.533 | 2.8 | -0.101 | 1.925 | 3.353% | -2.67 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 55.8 | 22.5 | 0 | 10.1 | 45.7 | 47.7 | 2 | -0.16 | 2.147 | 1.5 | 1.431 | 4.618% | 47.9 | -0.2 | 2.464 | 1.54 | 2.2 | -0.101 | 1.6 | 4.282% | -3.41 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 219.1 | 118 | 0 | 6.4 | 212.7 | 217 | 4.3 | 0.21 | 4.06 | 5.003 | 0.811 | 8.414% | 216.2 | 0.3 | 3.181 | 5.126 | 3.5 | -0.101 | 0.621 | 10.55% | -10.02 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.099 | 41 | 13 | 0 | 27 | 14 | 14.3 | 0.3 | 0 | 0.288 | 0.994 | 0.289 | 22.74% | 13.6 | 0 | -0.4 | 1.023 | -0.4 | -0.101 | 0 | -17.4% | 5.63 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 264 | 100 | 20 | 39 | 205 | 211.1 | 6.1 | -0.18 | 6.33 | 5.571 | 1.136 | 7.146% | 212.8 | -0.3 | 8.123 | 5.707 | 7.8 | -0.101 | 1.423 | 5.701% | -4.33 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.099 | 537 | 93 | 0 | 440.4 | 96.6 | 102.9 | 6.3 | -0.06 | 6.278 | 8.339 | 0.753 | 14.07% | 117 | -0.1 | 20.422 | 8.586 | 20.4 | -0.101 | 2 | 4.434% | -0.78 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 696 | 273 | 0 | 150.1 | 545.9 | 565.2 | 19.3 | 0.37 | 18.925 | 15.891 | 1.191 | 5.952% | 572.8 | 0.5 | 26.408 | 16.279 | 26.9 | -0.101 | 1.622 | 4.356% | -3.35 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.111 | 190 | 85 | 0 | 37.1 | 152.9 | 161.1 | 8.2 | 1.18 | 7.016 | 4.45 | 1.577 | 4.29% | 162 | 1.6 | 7.429 | 3.771 | 9.1 | -0.1 | 1.97 | 3.483% | -3.11 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.111 | 510.1 | 275 | 12 | 118.7 | 379.4 | 388.8 | 9.4 | -2.71 | 12.082 | 9.907 | 1.219 | 10.04% | 398 | -3.8 | 22.383 | 8.516 | 18.6 | -0.1 | 2 | 4.572% | -3.77 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.111 | 230 | 60 | 0 | 72.3 | 157.7 | 166.2 | 8.5 | 3.17 | 5.323 | 4.182 | 1.273 | 5.013% | 168 | 4.4 | 5.833 | 3.448 | 10.3 | -0.1 | 1.692 | 3.727% | -2.83 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.111 | 412 | 115 | 0 | 93.4 | 318.6 | 326.4 | 7.8 | 0.82 | 6.998 | 6.73 | 1.04 | 9.779% | 326.2 | 1.1 | 6.489 | 5.547 | 7.6 | -0.1 | 1.17 | 9.043% | -7.75 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.111 | 560 | 135 | 0 | 57.4 | 502.6 | 516.2 | 13.6 | -2.09 | 15.662 | 14.4 | 1.088 | 7.62% | 518.3 | -2.9 | 18.583 | 12.424 | 15.7 | -0.1 | 1.496 | 5.947% | -5.92 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.111 | 420 | 125 | 0 | 17.1 | 402.9 | 411.1 | 8.2 | 0.12 | 8.096 | 8.686 | 0.932 | 9.479% | 411.5 | 0.2 | 8.481 | 7.494 | 8.6 | -0.1 | 1.132 | 8.143% | -8.66 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.111 | 417 | 125 | 0 | 41.4 | 375.6 | 384.8 | 9.2 | 0.36 | 8.862 | 8.529 | 1.039 | 8.388% | 383.8 | 0.5 | 7.674 | 7.359 | 8.2 | -0.1 | 1.043 | 8.479% | -8.47 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.111 | 420 | 70 | 0 | 113.4 | 306.6 | 312.9 | 6.3 | -2.62 | 8.995 | 9.736 | 0.924 | 12.34% | 314.3 | -3.6 | 11.373 | 8.4 | 7.7 | -0.1 | 1.354 | 9.095% | -7.36 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.111 | 452 | 331 | 40 | 17.2 | 394.8 | 404.3 | 9.5 | -0.53 | 10.081 | 8.195 | 1.23 | 8.805% | 406.8 | -0.7 | 12.763 | 7.044 | 12 | -0.1 | 1.812 | 6.28% | -6.08 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.111 | 316 | 50 | 0 | 33.4 | 282.6 | 304.4 | 21.8 | 2.38 | 19.427 | 6.685 | 2 | 2.683% | 300.8 | 3.3 | 14.873 | 5.768 | 18.2 | -0.1 | 2 | 2.895% | -2.87 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | STM | -0.111 | 119 | 25 | 0 | 29.1 | 89.9 | 94.8 | 4.9 | -0.16 | 5.07 | 3.055 | 1.659 | 4.499% | 95.2 | -0.2 | 5.511 | 2.636 | 5.3 | -0.1 | 2 | 3.747% | -3.13 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.111 | 301.7 | 54.7 | 0 | 34.1 | 267.6 | 277.7 | 10.1 | -0.06 | 10.156 | 7.504 | 1.353 | 5.529% | 277.4 | -0.1 | 9.837 | 6.474 | 9.8 | -0.1 | 1.519 | 5.134% | -5.05 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | COGN | -0.111 | 234 | 150 | 21 | 10.1 | 202.9 | 208.7 | 5.8 | 0.04 | 5.778 | 5.091 | 1.135 | 7.469% | 208.9 | 0.1 | 5.981 | 4.392 | 6 | -0.1 | 1.362 | 6.505% | -6.25 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.111 | 235 | 150 | 21 | 10.5 | 203.5 | 209.5 | 6 | -0.13 | 6.113 | 5.125 | 1.193 | 7.251% | 209.9 | -0.2 | 6.535 | 4.421 | 6.4 | -0.1 | 1.478 | 6.124% | -5.88 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.111 | 228 | 150 | 21 | 6.8 | 200.2 | 205.9 | 5.7 | -0.12 | 5.794 | 4.91 | 1.18 | 7.405% | 206.6 | -0.2 | 6.497 | 4.236 | 6.4 | -0.1 | 1.534 | 5.942% | -5.78 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.111 | 168 | 0 | 0 | 55 | 113 | 126.9 | 13.9 | 0.26 | 13.653 | 3.342 | 2 | 2.238% | 124.1 | 0.4 | 10.757 | 2.872 | 11.1 | -0.1 | 2 | 2.525% | -1.88 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.111 | 600 | 260 | 0 | 13.9 | 586.1 | 586.5 | 0.4 | 0.03 | 0.361 | 11.934 | 0.03 | 277.6% | 587.1 | 0 | 0.943 | 10.258 | 1 | -0.1 | 0.092 | 100% | -108.4 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.111 | 824 | 258 | 0 | 54.2 | 769.8 | 794.9 | 25.1 | -0.52 | 25.568 | 14.122 | 1.81 | 6.074% | 794.4 | -0.7 | 25.311 | 12.184 | 24.6 | -0.1 | 2 | 5.584% | -5.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.111 | 95 | 60 | 0 | 20.5 | 74.5 | 80.9 | 6.4 | 0 | 6.475 | 2.225 | 2 | 2.751% | 81.2 | 0 | 6.698 | 1.886 | 6.7 | -0.1 | 2 | 2.367% | -2.05 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | GT | -0.111 | 238 | 150 | 17 | 10.7 | 210.3 | 213.5 | 3.2 | 0.05 | 3.157 | 4.619 | 0.683 | 13.77% | 213.9 | 0.1 | 3.52 | 3.985 | 3.6 | -0.1 | 0.883 | 11.03% | -10.8 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.111 | 236 | 150 | 17 | 10.9 | 208.1 | 211.7 | 3.6 | -0.16 | 3.806 | 4.551 | 0.836 | 12.14% | 212 | -0.2 | 4.172 | 3.926 | 3.9 | -0.1 | 1.063 | 10.09% | -9.86 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.111 | 233 | 150 | 17 | 10.8 | 205.2 | 210.7 | 5.5 | -0.33 | 5.861 | 4.45 | 1.317 | 7.842% | 210.8 | -0.5 | 6.14 | 3.84 | 5.6 | -0.1 | 1.599 | 6.94% | -6.77 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.111 | 238 | 150 | 17 | 10.8 | 210.2 | 212.8 | 2.6 | -0.11 | 2.729 | 4.62 | 0.591 | 16.95% | 213 | -0.2 | 2.935 | 3.986 | 2.8 | -0.1 | 0.736 | 14.18% | -13.88 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.111 | 248 | 110 | 17 | 11.1 | 219.9 | 223.7 | 3.8 | 0 | 3.786 | 4.769 | 0.794 | 12.08% | 224.1 | 0 | 4.155 | 4.115 | 4.2 | -0.1 | 1.01 | 9.848% | -9.68 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.111 | 332 | 205 | 4.9 | 25.1 | 302 | 311.6 | 9.6 | 0.41 | 9.139 | 6.506 | 1.405 | 6.401% | 317.5 | 0.6 | 14.89 | 5.592 | 15.5 | -0.1 | 2 | 3.572% | -3.6 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.111 | 709.6 | 444.8 | 14.4 | 44 | 651.2 | 675.9 | 24.7 | 6.08 | 18.693 | 13.828 | 1.352 | 5.316% | 676.4 | 8.5 | 16.779 | 11.885 | 25.2 | -0.1 | 1.412 | 4.694% | -4.78 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.111 | 49.8 | 24 | 0 | 17.3 | 32.5 | 35.6 | 3.1 | -0.45 | 3.588 | 1.165 | 2 | 2.981% | 41.8 | -0.6 | 9.947 | 0.988 | 9.3 | -0.1 | 2 | 0.8955% | -0.64 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.111 | 49.8 | 24 | 0 | 17.5 | 32.3 | 34.9 | 2.6 | -1.06 | 3.693 | 1.166 | 2 | 3.554% | 41.1 | -1.5 | 10.357 | 0.989 | 8.8 | -0.1 | 2 | 0.9464% | -0.68 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.111 | 461.8 | 230 | 6.1 | 146.9 | 308.8 | 313.6 | 4.8 | -9.97 | 14.714 | 9.064 | 1.623 | 17.8% | 325.7 | -13.9 | 30.746 | 7.791 | 16.9 | -0.1 | 2 | 4.556% | -3.38 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.111 | 232.4 | 130 | 0 | 44.7 | 187.7 | 195.7 | 8 | -0.17 | 8.079 | 4.622 | 1.748 | 5.378% | 194.1 | -0.2 | 6.595 | 3.973 | 6.4 | -0.1 | 1.66 | 6.057% | -5.42 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.111 | 163 | 120 | 0 | 39.2 | 123.8 | 127.8 | 4 | -0.07 | 4.103 | 3.144 | 1.305 | 7.553% | 134.4 | -0.1 | 10.695 | 2.592 | 10.6 | -0.1 | 2 | 2.568% | -2.16 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.111 | 676 | 300 | 40 | 147.4 | 488.6 | 512.2 | 23.6 | -0.86 | 24.399 | 12.651 | 1.929 | 5.3% | 509.2 | -1.2 | 21.716 | 10.874 | 20.6 | -0.1 | 1.997 | 5.471% | -4.39 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.111 | 44 | 13 | 0 | 25.6 | 18.4 | 20.2 | 1.8 | 0 | 1.802 | 1.03 | 1.749 | 4.538% | 20.1 | 0 | 1.743 | 0.873 | 1.7 | -0.1 | 1.996 | 4.33% | -1.99 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.111 | 44 | 13 | 0 | 25.6 | 18.4 | 20.7 | 2.3 | 0 | 2.25 | 1.03 | 2 | 3.551% | 20.6 | 0 | 2.2 | 0.873 | 2.2 | -0.1 | 2 | 3.346% | -1.53 | 0.017 | 0.05 | 6.335% | 5.367%
Hydro | NA | HYDR | -0.099 | 30 | 0 | 0 | 19.8 | 10.2 | 29.9 | 19.7 | -2.34 | 22.05 | 0.91 | 2 | 0.2527% | 30 | -3.3 | 23.031 | 0.955 | 19.8 | -0.103 | 2 | 0.2615% | -0.08 | 0.017 | 0.05 | 0.2285% | 0.2528%
Thermal | NG | FOSS | -0.099 | 217 | 62 | 0 | 73.2 | 143.8 | 157.8 | 14 | -0.13 | 14.142 | 5.38 | 2 | 2.562% | 158.9 | -0.2 | 15.239 | 5.707 | 15.1 | -0.103 | 2 | 2.471% | -1.57 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 230 | 60 | 0 | 166.2 | 63.8 | 78.1 | 14.3 | 1.09 | 13.172 | 5.405 | 2 | 2.658% | 81.5 | 1.5 | 16.228 | 5.734 | 17.7 | -0.103 | 2 | 2.234% | -0.59 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 412 | 115 | 0 | 180.1 | 231.9 | 254.8 | 22.9 | 0.56 | 22.322 | 8.131 | 2 | 2.971% | 253 | 0.8 | 20.332 | 8.625 | 21.1 | -0.103 | 2 | 3.355% | -1.81 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 420 | 70 | 0 | 222.7 | 197.3 | 217.2 | 19.9 | 3.08 | 16.828 | 8.833 | 1.905 | 3.484% | 222.4 | 4.3 | 20.873 | 9.269 | 25.1 | -0.103 | 2 | 2.874% | -1.3 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 410 | 70 | 0 | 159.2 | 250.8 | 269.4 | 18.6 | -0.05 | 18.586 | 10.546 | 1.762 | 3.639% | 270.8 | -0.1 | 20.083 | 11.067 | 20 | -0.103 | 1.815 | 3.521% | -2.07 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 746 | 310 | 0 | 55 | 691 | 716.6 | 25.6 | -4.47 | 30.113 | 15.086 | 1.996 | 4.81% | 724 | -6.2 | 39.239 | 16.003 | 33 | -0.103 | 2 | 3.882% | -3.45 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 105 | 12 | 0 | 91.9 | 13.1 | 15.9 | 2.8 | 0.11 | 2.731 | 3.153 | 0.866 | 6.198% | 15.9 | 0.1 | 2.702 | 3.308 | 2.8 | -0.103 | 0.817 | 6.448% | -0.76 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 315 | 50 | 0 | 97.4 | 217.6 | 247.2 | 29.6 | -1.23 | 30.83 | 6.681 | 2 | 1.757% | 249 | -1.7 | 33.09 | 7.011 | 31.4 | -0.103 | 2 | 1.723% | -1.14 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 420 | 50 | 0 | 185 | 235 | 259.7 | 24.7 | -1.39 | 26.17 | 9.716 | 2 | 2.807% | 264 | -1.9 | 30.933 | 10.196 | 29 | -0.103 | 2 | 2.487% | -1.34 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 329 | 139 | 11 | 39.8 | 278.2 | 289.2 | 11 | -0.96 | 12.053 | 7.398 | 1.629 | 4.938% | 293.8 | -1.3 | 16.984 | 7.771 | 15.6 | -0.103 | 2 | 3.622% | -2.94 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.099 | 470 | 180 | 0 | 20.3 | 449.7 | 454.2 | 4.5 | -0.27 | 4.803 | 8.883 | 0.541 | 17.25% | 454.3 | -0.4 | 4.971 | 9.423 | 4.6 | -0.103 | 0.528 | 17.55% | -16.12 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 470 | 180 | 0 | 20.3 | 449.7 | 454.2 | 4.5 | -0.27 | 4.803 | 8.883 | 0.541 | 17.25% | 454.3 | -0.4 | 4.971 | 9.423 | 4.6 | -0.103 | 0.528 | 17.55% | -16.12 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 470 | 180 | 0 | 20.3 | 449.7 | 454.2 | 4.5 | -0.27 | 4.803 | 8.883 | 0.541 | 17.25% | 454.3 | -0.4 | 4.971 | 9.423 | 4.6 | -0.103 | 0.528 | 17.55% | -16.12 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 470 | 180 | 0 | 20.3 | 449.7 | 454.2 | 4.5 | -0.27 | 4.803 | 8.883 | 0.541 | 17.25% | 454.3 | -0.4 | 4.971 | 9.423 | 4.6 | -0.103 | 0.528 | 17.55% | -16.12 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.099 | 234 | 150 | 21 | 7.7 | 205.3 | 210.8 | 5.5 | -0.3 | 5.765 | 5.977 | 0.965 | 7.025% | 210.6 | -0.4 | 5.697 | 6.272 | 5.3 | -0.103 | 0.908 | 7.585% | -6.39 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.099 | 234 | 150 | 21 | 8.3 | 204.7 | 210 | 5.3 | -0.46 | 5.716 | 5.966 | 0.958 | 7.29% | 209.6 | -0.6 | 5.493 | 6.26 | 4.9 | -0.103 | 0.877 | 8.204% | -6.89 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.099 | 231 | 150 | 21 | 9.1 | 200.9 | 206.2 | 5.3 | -0.8 | 6.088 | 5.818 | 1.046 | 7.197% | 206.7 | -1.1 | 6.914 | 6.105 | 5.8 | -0.103 | 1.132 | 6.842% | -5.71 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.099 | 375 | 100 | 0 | 213.9 | 161.1 | 216 | 54.9 | -1.17 | 56.132 | 6.423 | 2 | 1.128% | 192.2 | -1.6 | 32.77 | 6.814 | 31.1 | -0.103 | 2 | 2.072% | -0.85 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 221 | 42.4 | 40 | 60.9 | 120.1 | 128.1 | 8 | 0 | 8.056 | 4.211 | 1.913 | 4.562% | 123.6 | 0 | 3.549 | 4.423 | 3.5 | -0.103 | 0.802 | 10.85% | -5.65 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.099 | 824 | 259 | 0 | 67 | 757 | 781.1 | 24.1 | 0.08 | 24.057 | 16.611 | 1.448 | 5.643% | 781 | 0.1 | 23.908 | 17.431 | 24 | -0.103 | 1.372 | 5.895% | -5.2 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.099 | 96 | 52 | 0 | 25.1 | 70.9 | 77.2 | 6.3 | 0 | 6.28 | 2.629 | 2 | 2.519% | 77.6 | 0 | 6.698 | 2.772 | 6.7 | -0.103 | 2 | 2.464% | -1.74 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | GT | -0.099 | 242 | 150 | 21 | 37.6 | 183.4 | 188.7 | 5.3 | -0.87 | 6.144 | 5.056 | 1.215 | 7.539% | 189 | -1.2 | 6.79 | 5.305 | 5.6 | -0.103 | 1.28 | 7.424% | -5.4 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.099 | 240 | 150 | 21 | 33.2 | 185.8 | 191.6 | 5.8 | -0.62 | 6.446 | 5.033 | 1.281 | 6.832% | 191.7 | -0.9 | 6.789 | 5.282 | 5.9 | -0.103 | 1.285 | 6.988% | -5.19 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.099 | 237 | 150 | 21 | 36.4 | 179.6 | 185.2 | 5.6 | -0.39 | 6.04 | 4.896 | 1.234 | 6.988% | 185.1 | -0.5 | 6.036 | 5.137 | 5.5 | -0.103 | 1.175 | 7.402% | -5.38 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.099 | 242 | 150 | 21 | 9.1 | 211.9 | 215 | 3.1 | -0.41 | 3.464 | 5.391 | 0.643 | 12.89% | 215.4 | -0.6 | 4.038 | 5.657 | 3.5 | -0.103 | 0.714 | 11.88% | -9.98 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.099 | 253 | 110 | 21 | 9.1 | 222.9 | 227.1 | 4.2 | -0.58 | 4.757 | 5.605 | 0.849 | 9.946% | 227.7 | -0.8 | 5.613 | 5.882 | 4.8 | -0.103 | 0.954 | 9.054% | -7.66 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.099 | 205 | 40 | 0 | 140.6 | 64.4 | 77.3 | 12.9 | 0.8 | 12.107 | 5.901 | 2 | 2.624% | 78.1 | 1.1 | 12.527 | 6.192 | 13.7 | -0.103 | 2 | 2.571% | -0.77 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | WDS | STM | -0.099 | 105 | 70 | 0 | 34.3 | 70.7 | 74.3 | 3.6 | -0.18 | 3.804 | 2.875 | 1.323 | 4.82% | 74.2 | -0.2 | 3.761 | 3.032 | 3.5 | -0.103 | 1.24 | 5.158% | -3.32 | 0.017 | 0.05 | 5.146% | 4.85%
Hydro | NA | HYDR | -0.099 | 34 | 0 | 0 | 23.9 | 10.1 | 33.3 | 23.2 | -2.75 | 25.992 | 1.032 | 2 | 0.243% | 33.3 | -3.8 | 27.069 | 1.083 | 23.2 | -0.103 | 2 | 0.2528% | -0.07 | 0.017 | 0.05 | 0.2285% | 0.2528%
Thermal | SUB | FOSS | -0.099 | 650 | 187.7 | 0 | 36.7 | 613.3 | 623.1 | 9.8 | -1.93 | 11.725 | 13.094 | 0.895 | 10.95% | 625.5 | -2.7 | 14.931 | 13.74 | 12.2 | -0.103 | 1.087 | 9.148% | -8.29 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 650 | 187.7 | 0 | 36.7 | 613.3 | 623.1 | 9.8 | -1.93 | 11.725 | 13.094 | 0.895 | 10.95% | 625.5 | -2.7 | 14.931 | 13.74 | 12.2 | -0.103 | 1.087 | 9.148% | -8.29 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 650 | 187.7 | 0 | 36.7 | 613.3 | 623.1 | 9.8 | -1.93 | 11.725 | 13.094 | 0.895 | 10.95% | 625.5 | -2.7 | 14.931 | 13.74 | 12.2 | -0.103 | 1.087 | 9.148% | -8.29 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 650 | 187.7 | 0 | 36.7 | 613.3 | 623.1 | 9.8 | -1.93 | 11.725 | 13.094 | 0.895 | 10.95% | 625.5 | -2.7 | 14.931 | 13.74 | 12.2 | -0.103 | 1.087 | 9.148% | -8.29 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 650 | 187.7 | 0 | 36.7 | 613.3 | 623.1 | 9.8 | -1.93 | 11.725 | 13.094 | 0.895 | 10.95% | 625.5 | -2.7 | 14.931 | 13.74 | 12.2 | -0.103 | 1.087 | 9.148% | -8.29 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 714.7 | 453.4 | 13.1 | 35.3 | 666.3 | 689.4 | 23.1 | 1.77 | 21.369 | 16.323 | 1.309 | 5.106% | 690.5 | 2.5 | 21.751 | 17.145 | 24.2 | -0.103 | 1.269 | 5.071% | -4.54 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.099 | 327.5 | 204.6 | 12.6 | 55.6 | 259.3 | 271.6 | 12.3 | -3.36 | 15.665 | 7.326 | 2 | 4.396% | 279 | -4.7 | 24.394 | 7.695 | 19.7 | -0.103 | 2 | 2.855% | -2.17 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.099 | 702.6 | 444 | 19.4 | 70.7 | 612.5 | 638.2 | 25.7 | -2.6 | 28.309 | 15.895 | 1.781 | 4.512% | 648.9 | -3.6 | 40.012 | 16.695 | 36.4 | -0.103 | 2 | 3.314% | -2.78 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.099 | 41.5 | 20 | 0 | 10.9 | 30.6 | 36.3 | 5.7 | 0.31 | 5.383 | 1.135 | 2 | 1.206% | 41.7 | 0.4 | 10.706 | 1.198 | 11.1 | -0.103 | 2 | 0.6444% | -0.45 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 49.8 | 24 | 0 | 17.5 | 32.3 | 38.3 | 6 | 0.14 | 5.942 | 1.363 | 2 | 1.374% | 44.5 | 0.2 | 12.071 | 1.437 | 12.2 | -0.103 | 2 | 0.7031% | -0.43 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 461.8 | 230 | 0 | 24.7 | 437.1 | 444.3 | 7.2 | -0.12 | 7.313 | 10.744 | 0.681 | 10.59% | 446.5 | -0.2 | 9.521 | 11.285 | 9.4 | -0.103 | 0.844 | 8.437% | -7.67 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.099 | 55.8 | 22.5 | 0 | 16.3 | 39.5 | 44.3 | 4.8 | -0.01 | 4.852 | 1.528 | 2 | 1.924% | 50.1 | 0 | 10.6 | 1.612 | 10.6 | -0.103 | 2 | 0.9064% | -0.61 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 55.8 | 22.5 | 0 | 15.7 | 40.1 | 43.2 | 3.1 | 0.62 | 2.485 | 1.529 | 1.625 | 2.979% | 43.9 | 0.9 | 2.896 | 1.613 | 3.8 | -0.103 | 1.796 | 2.528% | -1.73 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 205 | 100 | 0 | 40.8 | 164.2 | 171.4 | 7.2 | -0.18 | 7.383 | 4.769 | 1.548 | 4.702% | 175 | -0.3 | 11.003 | 5.01 | 10.8 | -0.103 | 2 | 3.261% | -2.51 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.099 | 232.4 | 130 | 0 | 42.8 | 189.6 | 197.3 | 7.7 | -0.67 | 8.287 | 5.407 | 1.533 | 4.984% | 195.6 | -0.9 | 6.945 | 5.679 | 6 | -0.103 | 1.223 | 6.654% | -5.21 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.099 | 164 | 27 | 0 | 133.9 | 30.1 | 39.8 | 9.7 | 0.42 | 9.338 | 1.953 | 2 | 2.796% | 40.8 | 0.6 | 10.141 | 2.071 | 10.7 | -0.103 | 2 | 2.636% | -0.46 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 673 | 300 | 40 | 133.7 | 499.3 | 536.1 | 36.8 | 3.46 | 33.303 | 14.728 | 2 | 3.018% | 535.5 | 4.8 | 31.4 | 15.47 | 36.2 | -0.103 | 2 | 3.192% | -2.28 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.045 | 56 | 30 | 0 | 13.3 | 42.7 | 44.6 | 1.9 | 0.15 | 1.836 | 0.713 | 2 | 2.225% | 44.6 | 0.2 | 1.732 | 0.546 | 1.9 | -0.036 | 2 | 1.783% | -1.67 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.045 | 520.3 | 275 | 12 | 48.3 | 460 | 466.1 | 6.1 | 1.83 | 4.316 | 5.479 | 0.788 | 6.402% | 471.9 | 2.5 | 9.348 | 4.292 | 11.9 | -0.036 | 2 | 2.626% | -2.9 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.045 | 521 | 327 | 63.6 | 54.5 | 402.9 | 409.5 | 6.6 | -0.12 | 6.679 | 4.931 | 1.355 | 5.925% | 409.9 | -0.2 | 7.15 | 3.862 | 7 | -0.036 | 1.851 | 4.47% | -4.31 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.045 | 217 | 62 | 0 | 145.7 | 71.3 | 73.7 | 2.4 | -0.31 | 2.697 | 1.895 | 1.423 | 6.805% | 74.6 | -0.4 | 3.749 | 1.244 | 3.3 | -0.036 | 2 | 3.963% | -1.6 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.045 | 230 | 60 | 0 | 161.4 | 68.6 | 76.2 | 7.6 | -0.21 | 7.802 | 1.907 | 2 | 2.277% | 79.5 | -0.3 | 11.253 | 1.251 | 10.9 | -0.036 | 2 | 1.271% | -0.47 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.045 | 412 | 115 | 0 | 288.7 | 123.3 | 133.7 | 10.4 | -1.18 | 11.624 | 2.885 | 2 | 2.977% | 127.1 | -1.6 | 5.479 | 1.893 | 3.8 | -0.036 | 2 | 6.52% | -2.42 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.045 | 560 | 135 | 0 | 37.9 | 522.1 | 527.8 | 5.7 | 0.84 | 4.907 | 8.055 | 0.609 | 7.373% | 528.6 | 1.2 | 5.405 | 6.383 | 6.5 | -0.036 | 0.847 | 5.174% | -6.02 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.045 | 410 | 70 | 0 | 330 | 80 | 92 | 12 | 0.42 | 11.585 | 4.372 | 2 | 2.565% | 91.3 | 0.6 | 10.766 | 3.464 | 11.3 | -0.036 | 2 | 2.179% | -0.53 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.045 | 634 | 445 | 5 | 22.3 | 606.7 | 616.9 | 10.2 | -0.38 | 10.551 | 6.78 | 1.556 | 4.665% | 617.3 | -0.5 | 11.056 | 5.311 | 10.6 | -0.036 | 2 | 3.591% | -4.29 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.045 | 105 | 12 | 0 | 92.9 | 12.1 | 14.8 | 2.7 | -0.36 | 3.139 | 1.495 | 2 | 2.927% | 14.6 | -0.5 | 3.101 | 1.185 | 2.5 | -0.036 | 2 | 2.531% | -0.35 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.045 | 316 | 50 | 0 | 88.6 | 227.4 | 236.5 | 9.1 | 0.23 | 8.857 | 3.308 | 2 | 2.608% | 237.6 | 0.3 | 9.827 | 2.622 | 10.2 | -0.036 | 2 | 1.862% | -1.67 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | STM | -0.045 | 302.1 | 55 | 0 | 56.1 | 246 | 252.3 | 6.3 | 0.02 | 6.366 | 4.17 | 1.526 | 3.601% | 251.1 | 0 | 5.132 | 3.305 | 5.1 | -0.036 | 1.553 | 3.56% | -3.61 | 0.017 | 0.05 | 5.146% | 4.85%
Wind | WND | WIND | -0.045 | 47 | 0 | 0 | 4.7 | 42.3 | 41.4 | -0.9 | -1.01 | 0.042 | 0.676 | 0.062 | -3.948% | 43.3 | -1.4 | 2.416 | 0.536 | 1 | -0.036 | 2 | 2.848% | -3.14 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | COGN | -0.045 | 230 | 150 | 21 | 23.6 | 185.4 | 189.8 | 4.4 | -0.07 | 4.404 | 2.622 | 1.68 | 3.927% | 189.8 | -0.1 | 4.471 | 2.078 | 4.4 | -0.036 | 2 | 3.143% | -3.15 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.045 | 236 | 150 | 21 | 39.1 | 175.9 | 180.4 | 4.5 | -0.33 | 4.83 | 2.619 | 1.844 | 3.94% | 180 | -0.5 | 4.589 | 2.076 | 4.1 | -0.036 | 2 | 3.461% | -3.21 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.045 | 236 | 150 | 21 | 10.6 | 204.4 | 208.8 | 4.4 | 0.09 | 4.315 | 2.851 | 1.513 | 4.029% | 208.1 | 0.1 | 3.611 | 2.259 | 3.7 | -0.036 | 1.598 | 3.835% | -4.14 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.045 | 233 | 150 | 21 | 12 | 200 | 203.8 | 3.8 | -0.01 | 3.798 | 2.776 | 1.368 | 4.606% | 204.4 | 0 | 4.422 | 2.2 | 4.4 | -0.036 | 2 | 3.184% | -3.4 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | GT | -0.045 | 91 | 35 | 0 | 18.2 | 72.8 | 78.1 | 5.3 | 0.27 | 5.032 | 1.158 | 2 | 1.293% | 80.3 | 0.4 | 7.121 | 0.887 | 7.5 | -0.036 | 2 | 0.7318% | -0.72 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.045 | 88 | 35 | 0 | 16.2 | 71.8 | 76.9 | 5.1 | 0.31 | 4.859 | 1.12 | 2 | 1.3% | 78.8 | 0.4 | 6.579 | 0.857 | 7 | -0.036 | 2 | 0.7583% | -0.77 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.045 | 824 | 259 | 0 | 70.8 | 753.2 | 764.1 | 10.9 | 0 | 10.91 | 7.959 | 1.371 | 5.672% | 764.4 | 0 | 11.136 | 6.307 | 11.2 | -0.036 | 1.766 | 4.417% | -5.04 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.045 | 836 | 258 | 0 | 53.4 | 782.6 | 792.3 | 9.7 | 0.62 | 9.098 | 8.567 | 1.062 | 6.467% | 790.2 | 0.9 | 6.746 | 6.789 | 7.6 | -0.036 | 0.994 | 6.604% | -7.72 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.045 | 46 | 20 | 0 | 6 | 40 | 41.3 | 1.3 | -0.1 | 1.453 | 0.586 | 2 | 2.676% | 41.3 | -0.1 | 1.429 | 0.448 | 1.3 | -0.036 | 2 | 2.145% | -2.29 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.045 | 239 | 150 | 21 | 38.9 | 179.1 | 182.3 | 3.2 | 0.57 | 2.669 | 2.344 | 1.139 | 5.61% | 182.4 | 0.8 | 2.584 | 1.857 | 3.3 | -0.036 | 1.391 | 4.354% | -4.06 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.045 | 237 | 150 | 21 | 38.6 | 177.4 | 180.9 | 3.5 | 0.67 | 2.751 | 2.312 | 1.19 | 5.087% | 181 | 0.9 | 2.608 | 1.832 | 3.6 | -0.036 | 1.424 | 3.958% | -3.69 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.045 | 236 | 150 | 21 | 37.8 | 177.2 | 180.6 | 3.4 | 0.61 | 2.822 | 2.3 | 1.227 | 5.214% | 180.8 | 0.8 | 2.724 | 1.822 | 3.6 | -0.036 | 1.495 | 3.941% | -3.68 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.045 | 239 | 150 | 21 | 38.8 | 179.2 | 182.6 | 3.4 | 0.73 | 2.669 | 2.344 | 1.139 | 5.28% | 182.5 | 1 | 2.28 | 1.857 | 3.3 | -0.036 | 1.228 | 4.354% | -4.06 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.045 | 241 | 150 | 21 | 40.3 | 179.7 | 183.7 | 4 | 0.76 | 3.256 | 2.263 | 1.439 | 4.526% | 183.6 | 1.1 | 2.853 | 1.793 | 3.9 | -0.036 | 1.591 | 3.715% | -3.45 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.045 | 250 | 110 | 21 | 40.3 | 188.7 | 192.8 | 4.1 | 0.71 | 3.355 | 2.414 | 1.39 | 4.58% | 192 | 1 | 2.305 | 1.913 | 3.3 | -0.036 | 1.205 | 4.554% | -4.28 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.045 | 205 | 40 | 0 | 141.7 | 63.3 | 71 | 7.7 | 0 | 7.646 | 2.809 | 2 | 2% | 72.8 | 0 | 9.449 | 2.226 | 9.5 | -0.036 | 2 | 1.298% | -0.5 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.045 | 718.5 | 448.5 | 19.2 | 86.6 | 612.7 | 630.3 | 17.6 | 0.47 | 17.123 | 7.538 | 2 | 3.063% | 634.2 | 0.7 | 20.8 | 5.905 | 21.5 | -0.036 | 2 | 2.006% | -2.14 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.045 | 722.3 | 448.2 | 29.1 | 125.6 | 567.6 | 583.9 | 16.3 | 0.47 | 15.859 | 7.472 | 2 | 3.325% | 588.5 | 0.7 | 20.243 | 5.854 | 20.9 | -0.036 | 2 | 2.075% | -2.04 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.045 | 49.8 | 24 | 0 | 19.6 | 30.2 | 35.3 | 5.1 | -0.08 | 5.229 | 0.634 | 2 | 0.7379% | 42.3 | -0.1 | 12.199 | 0.485 | 12.1 | -0.036 | 2 | 0.2493% | -0.18 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.045 | 49.6 | 24 | 0 | 14.1 | 35.5 | 37.7 | 2.2 | -0.41 | 2.587 | 0.631 | 2 | 1.704% | 40.7 | -0.6 | 5.805 | 0.483 | 5.2 | -0.036 | 2 | 0.5778% | -0.51 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.045 | 49.8 | 24 | 0 | 14.3 | 35.5 | 38.3 | 2.8 | 0.38 | 2.357 | 0.634 | 2 | 1.344% | 39.4 | 0.5 | 3.38 | 0.485 | 3.9 | -0.036 | 2 | 0.7734% | -0.68 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.045 | 114 | 50 | 0 | 52.4 | 61.6 | 67.6 | 6 | -0.1 | 6.127 | 1.229 | 2 | 1.43% | 68.3 | -0.1 | 6.89 | 0.963 | 6.7 | -0.036 | 2 | 1.025% | -0.69 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.045 | 391 | 220 | 0 | 8.2 | 382.8 | 383 | 0.2 | 0 | 0.213 | 5.525 | 0.038 | 146.8% | 383 | 0 | 0.2 | 4.378 | 0.2 | -0.036 | 0.046 | 117.4% | -143.41 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.045 | 934.4 | 322 | 0 | 23.1 | 911.3 | 928.4 | 17.1 | -0.2 | 17.36 | 9.551 | 1.818 | 4.1% | 931.8 | -0.3 | 20.844 | 7.568 | 20.5 | -0.036 | 2 | 2.736% | -3.33 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.045 | 934.4 | 322 | 0 | 23.1 | 911.3 | 928.4 | 17.1 | -0.2 | 17.36 | 9.551 | 1.818 | 4.1% | 931.8 | -0.3 | 20.844 | 7.568 | 20.5 | -0.036 | 2 | 2.736% | -3.33 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.045 | 934.4 | 322 | 0 | 23.1 | 911.3 | 928.4 | 17.1 | -0.2 | 17.36 | 9.551 | 1.818 | 4.1% | 931.8 | -0.3 | 20.844 | 7.568 | 20.5 | -0.036 | 2 | 2.736% | -3.33 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.045 | 934.4 | 322 | 0 | 23.1 | 911.3 | 928.4 | 17.1 | -0.2 | 17.36 | 9.551 | 1.818 | 4.1% | 931.8 | -0.3 | 20.844 | 7.568 | 20.5 | -0.036 | 2 | 2.736% | -3.33 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.045 | 205 | 100 | 0 | 41.6 | 163.4 | 167 | 3.6 | 0 | 3.575 | 2.21 | 1.618 | 4.279% | 167.3 | 0 | 3.825 | 1.731 | 3.9 | -0.036 | 2 | 3.161% | -3.14 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.045 | 256 | 234 | 0 | 5.9 | 250.1 | 250.2 | 0.1 | -0.04 | 0.112 | 2.76 | 0.041 | 192.3% | 250.1 | 0 | 0.085 | 2.162 | 0 | -0.036 | 0.039 | 0% |  | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.045 | 233.2 | 130 | 0 | 41.5 | 191.7 | 194.9 | 3.2 | 0.75 | 2.49 | 2.514 | 0.99 | 5.474% | 194.5 | 1 | 1.77 | 1.969 | 2.8 | -0.036 | 0.899 | 5.007% | -5.12 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.045 | 164 | 120 | 0 | 41.5 | 122.5 | 125.3 | 2.8 | -0.39 | 3.112 | 1.353 | 2 | 4.413% | 130.2 | -0.5 | 8.221 | 0.888 | 7.7 | -0.036 | 2 | 1.285% | -1.19 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.045 | 238 | 195 | 0 | 9 | 229 | 233.5 | 4.5 | -0.95 | 5.406 | 1.909 | 2 | 3.979% | 231.3 | -1.3 | 3.596 | 1.253 | 2.3 | -0.036 | 2 | 6.233% | -7.44 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.045 | 683 | 300 | 40 | 204.2 | 438.8 | 455.6 | 16.8 | -2.59 | 19.352 | 6.932 | 2 | 3.051% | 465.2 | -3.6 | 29.982 | 5.43 | 26.4 | -0.036 | 2 | 1.553% | -1.25 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 523.6 | 275 | 12 | 61 | 450.6 | 469.6 | 19 | 1 | 17.931 | 10.063 | 1.782 | 3.86% | 480.8 | 1.4 | 28.766 | 9.417 | 30.2 | -0.079 | 2 | 2.284% | -2.09 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 459 | 300 | 0 | 39.8 | 419.2 | 432.8 | 13.6 | 0.07 | 13.573 | 9.028 | 1.503 | 4.727% | 430.4 | 0.1 | 11.149 | 8.449 | 11.2 | -0.079 | 1.32 | 5.399% | -5.24 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.084 | 560 | 135 | 0 | 39.4 | 520.6 | 533.4 | 12.8 | 0.03 | 12.779 | 14.42 | 0.886 | 6.127% | 534.2 | 0 | 13.63 | 13.517 | 13.6 | -0.079 | 1.008 | 5.424% | -5.36 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.084 | 417 | 125 | 0 | 81.6 | 335.4 | 346.1 | 10.7 | -0.04 | 10.746 | 8.242 | 1.304 | 5.459% | 342.7 | -0.1 | 7.36 | 7.726 | 7.3 | -0.079 | 0.953 | 7.525% | -6.43 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 217.8 | 167 | 12 | 38.7 | 167.1 | 174.8 | 7.7 | 0.18 | 7.48 | 4.047 | 1.848 | 3.964% | 172.8 | 0.2 | 5.411 | 3.787 | 5.7 | -0.079 | 1.429 | 5.036% | -4.1 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 230.5 | 163 | 18 | 47.1 | 165.4 | 172.4 | 7 | 0.47 | 6.566 | 4.181 | 1.57 | 4.614% | 170.6 | 0.7 | 4.543 | 3.912 | 5.2 | -0.079 | 1.161 | 5.842% | -4.45 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.084 | 746 | 93 | 0 | 652.5 | 93.5 | 108.5 | 15 | 0.36 | 14.615 | 10.923 | 1.338 | 6.966% | 109.4 | 0.5 | 15.34 | 10.044 | 15.9 | -0.079 | 1.527 | 6.181% | -0.82 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 644 | 93 | 0 | 549.5 | 94.5 | 109.1 | 14.6 | 0.08 | 14.562 | 9.459 | 1.54 | 6.179% | 114.4 | 0.1 | 19.868 | 8.698 | 19.9 | -0.079 | 2 | 4.264% | -0.66 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 637 | 460 | 6 | 46.2 | 584.8 | 606.3 | 21.5 | 1.63 | 19.951 | 12.411 | 1.608 | 4.149% | 607.8 | 2.3 | 20.726 | 11.615 | 23 | -0.079 | 1.784 | 3.648% | -3.56 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.084 | 105 | 12 | 0 | 92.9 | 12.1 | 15.3 | 3.2 | 0.06 | 3.095 | 2.676 | 1.157 | 4.603% | 14.9 | 0.1 | 2.67 | 2.509 | 2.8 | -0.079 | 1.064 | 4.948% | -0.59 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 335 | 140 | 11 | 7.9 | 316.1 | 323.1 | 7 | -4.53 | 11.567 | 6.373 | 1.815 | 6.704% | 319.3 | -6.3 | 9.537 | 5.964 | 3.2 | -0.079 | 1.599 | 13.79% | -13.82 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 521.8 | 347.3 | 0 | 31.4 | 490.4 | 510 | 19.6 | 0.52 | 19.085 | 10.264 | 1.859 | 3.729% | 510.9 | 0.7 | 19.841 | 9.605 | 20.5 | -0.079 | 2 | 3.353% | -3.35 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 886.3 | 461 | 13.5 | 26.3 | 846.5 | 871.4 | 24.9 | -5.1 | 30.016 | 17.167 | 1.748 | 4.984% | 874.7 | -7.1 | 35.339 | 16.066 | 28.2 | -0.079 | 2 | 4.139% | -4.2 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 531.1 | 310 | 128.9 | 90.7 | 311.5 | 315.8 | 4.3 | 1.2 | 3.11 | 7.91 | 0.393 | 17.3% | 319.6 | 1.7 | 6.44 | 7.403 | 8.1 | -0.079 | 0.87 | 8.637% | -5.38 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.084 | 470 | 180 | 0 | 31.5 | 438.5 | 439 | 0.5 | -0.93 | 1.442 | 7.207 | 0.2 | 131.7% | 438.3 | -1.3 | 1.037 | 6.627 | -0.2 | -0.079 | 0.156 | -309.7% | 306.67 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.084 | 470 | 180 | 0 | 31.5 | 438.5 | 439 | 0.5 | -0.93 | 1.442 | 7.207 | 0.2 | 131.7% | 438.3 | -1.3 | 1.037 | 6.627 | -0.2 | -0.079 | 0.156 | -309.7% | 306.67 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.084 | 470 | 180 | 0 | 31.5 | 438.5 | 439 | 0.5 | -0.93 | 1.442 | 7.207 | 0.2 | 131.7% | 438.3 | -1.3 | 1.037 | 6.627 | -0.2 | -0.079 | 0.156 | -309.7% | 306.67 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.084 | 470 | 180 | 0 | 31.5 | 438.5 | 439 | 0.5 | -0.93 | 1.442 | 7.207 | 0.2 | 131.7% | 438.3 | -1.3 | 1.037 | 6.627 | -0.2 | -0.079 | 0.156 | -309.7% | 306.67 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.084 | 236 | 150 | 21 | 50.2 | 164.8 | 172.7 | 7.9 | -0.04 | 8.001 | 4.527 | 1.767 | 4.186% | 172.2 | -0.1 | 7.467 | 4.244 | 7.4 | -0.079 | 1.76 | 4.203% | -3.11 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.084 | 242 | 150 | 21 | 50.2 | 170.8 | 178.5 | 7.7 | -0.17 | 7.891 | 4.745 | 1.663 | 4.404% | 178.4 | -0.2 | 7.767 | 4.447 | 7.6 | -0.079 | 1.746 | 4.196% | -3.14 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.084 | 243 | 150 | 21 | 51.8 | 170.2 | 177.8 | 7.6 | -0.05 | 7.695 | 4.757 | 1.618 | 4.48% | 178.3 | -0.1 | 8.201 | 4.459 | 8.1 | -0.079 | 1.839 | 3.953% | -2.94 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.084 | 240 | 150 | 21 | 54.7 | 164.3 | 172.1 | 7.8 | 0 | 7.722 | 4.605 | 1.677 | 4.311% | 172.8 | 0 | 8.441 | 4.317 | 8.5 | -0.079 | 1.955 | 3.721% | -2.7 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 604 | 305 | 111 | 111.4 | 381.6 | 393.4 | 11.8 | -0.67 | 12.431 | 9.697 | 1.282 | 7.169% | 395.2 | -0.9 | 14.581 | 9.075 | 13.6 | -0.079 | 1.607 | 5.85% | -3.93 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 590 | 260 | 0 | 132 | 458 | 466.8 | 8.8 | -0.27 | 9.004 | 11.605 | 0.776 | 9.39% | 473.4 | -0.4 | 15.716 | 10.86 | 15.4 | -0.079 | 1.447 | 5.046% | -4.16 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 601.4 | 260 | 0 | 141 | 460.4 | 467.3 | 6.9 | -0.23 | 7.121 | 11.828 | 0.602 | 12.21% | 473.9 | -0.3 | 13.804 | 11.069 | 13.5 | -0.079 | 1.247 | 5.868% | -4.77 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.084 | 94 | 35 | 0 | 56 | 38 | 43.8 | 5.8 | 0.15 | 5.619 | 2.177 | 2 | 2.274% | 43 | 0.2 | 4.764 | 2.025 | 5 | -0.079 | 2 | 2.481% | -1.06 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.084 | 501.8 | 400 | 0.9 | 25 | 475.9 | 485.2 | 9.3 | -0.24 | 9.51 | 9.851 | 0.965 | 7.557% | 487.5 | -0.3 | 11.9 | 9.219 | 11.6 | -0.079 | 1.291 | 5.698% | -5.74 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 526.8 | 314.3 | 8.9 | 33 | 484.9 | 499.9 | 15 | 0.05 | 14.926 | 10.185 | 1.465 | 4.919% | 495.1 | 0.1 | 10.163 | 9.532 | 10.2 | -0.079 | 1.066 | 6.803% | -6.65 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.084 | 245 | 150 | 21 | 41.5 | 182.5 | 189 | 6.5 | 0.29 | 6.172 | 4.336 | 1.424 | 5.281% | 189.5 | 0.4 | 6.622 | 4.064 | 7 | -0.079 | 1.629 | 4.612% | -3.65 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.084 | 243 | 150 | 21 | 41.1 | 180.9 | 188 | 7.1 | 0.38 | 6.77 | 4.278 | 1.582 | 4.796% | 188.1 | 0.5 | 6.665 | 4.01 | 7.2 | -0.079 | 1.662 | 4.448% | -3.51 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.084 | 239 | 150 | 21 | 46.9 | 171.1 | 171.6 | 0.5 | -4.24 | 4.691 | 4.113 | 1.14 | 66.98% | 169.8 | -5.9 | 4.622 | 3.855 | -1.3 | -0.079 | 1.199 | -24.23% | 18.4 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.084 | 245 | 150 | 21 | 41.6 | 182.4 | 190.3 | 7.9 | 0.08 | 7.86 | 4.329 | 1.816 | 4.345% | 190 | 0.1 | 7.499 | 4.058 | 7.6 | -0.079 | 1.848 | 4.248% | -3.36 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.084 | 255 | 110 | 21 | 10.3 | 223.7 | 226.5 | 2.8 | 0.13 | 2.72 | 4.811 | 0.565 | 12.76% | 227.5 | 0.2 | 3.589 | 4.51 | 3.8 | -0.079 | 0.796 | 8.843% | -8.23 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.084 | 641 | 250 | 128.5 | 46.2 | 466.3 | 489.7 | 23.4 | 0.15 | 23.265 | 10.081 | 2 | 3.836% | 492.8 | 0.2 | 26.312 | 9.434 | 26.5 | -0.079 | 2 | 3.186% | -2.46 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.084 | 650 | 189.6 | 0 | 90.8 | 559.2 | 581.7 | 22.5 | -1.85 | 24.327 | 10.886 | 2 | 4.046% | 584.8 | -2.6 | 28.196 | 10.204 | 25.6 | -0.079 | 2 | 3.344% | -3.06 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.084 | 650 | 189.6 | 0 | 90.8 | 559.2 | 581.7 | 22.5 | -1.85 | 24.327 | 10.886 | 2 | 4.046% | 584.8 | -2.6 | 28.196 | 10.204 | 25.6 | -0.079 | 2 | 3.344% | -3.06 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.084 | 650 | 189.6 | 0 | 90.8 | 559.2 | 581.7 | 22.5 | -1.85 | 24.327 | 10.886 | 2 | 4.046% | 584.8 | -2.6 | 28.196 | 10.204 | 25.6 | -0.079 | 2 | 3.344% | -3.06 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.084 | 650 | 189.6 | 0 | 90.8 | 559.2 | 581.7 | 22.5 | -1.85 | 24.327 | 10.886 | 2 | 4.046% | 584.8 | -2.6 | 28.196 | 10.204 | 25.6 | -0.079 | 2 | 3.344% | -3.06 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.084 | 650 | 189.6 | 0 | 90.8 | 559.2 | 581.7 | 22.5 | -1.85 | 24.327 | 10.886 | 2 | 4.046% | 584.8 | -2.6 | 28.196 | 10.204 | 25.6 | -0.079 | 2 | 3.344% | -3.06 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 729.1 | 463.3 | 25.3 | 112.7 | 591.1 | 614.8 | 23.7 | -2.07 | 25.788 | 13.843 | 1.863 | 4.308% | 613.2 | -2.9 | 24.959 | 12.955 | 22.1 | -0.079 | 1.927 | 4.345% | -3.74 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 732.7 | 455.3 | 55.4 | 220.4 | 456.9 | 482.5 | 25.6 | 0.18 | 25.421 | 13.322 | 1.908 | 4.008% | 489.1 | 0.2 | 31.939 | 12.467 | 32.2 | -0.079 | 2 | 2.997% | -1.99 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 375 | 190 | 0 | 77.3 | 297.7 | 318.5 | 20.8 | 0.41 | 20.437 | 7.376 | 2 | 2.525% | 323.1 | 0.6 | 24.825 | 6.903 | 25.4 | -0.079 | 2 | 1.945% | -1.64 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.084 | 55.8 | 22.5 | 0 | 29.1 | 26.7 | 29.9 | 3.2 | -0.04 | 3.28 | 1.294 | 2 | 2.45% | 34.2 | -0.1 | 7.643 | 1.203 | 7.5 | -0.079 | 2 | 0.9834% | -0.49 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 699 | 420 | 0 | 85.2 | 613.8 | 646.1 | 32.3 | 0.62 | 31.757 | 13.748 | 2 | 3.031% | 645.3 | 0.9 | 30.681 | 12.867 | 31.5 | -0.079 | 2 | 2.923% | -2.73 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.084 | 78 | 58 | 0 | 19.5 | 58.5 | 61.2 | 2.7 | 0.25 | 2.423 | 1.807 | 1.341 | 4.055% | 60.4 | 0.4 | 1.556 | 1.681 | 1.9 | -0.079 | 0.926 | 5.42% | -4.3 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 835 | 465 | 121.2 | 16.5 | 697.3 | 709.3 | 12 | -2.18 | 14.249 | 14.039 | 1.015 | 9.744% | 705.3 | -3 | 11.101 | 13.139 | 8 | -0.079 | 0.845 | 13.75% | -12.2 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 80 | 65 | 3 | 9.5 | 67.5 | 69.6 | 2.1 | -0.06 | 2.174 | 1.514 | 1.436 | 5.347% | 69.7 | -0.1 | 2.254 | 1.417 | 2.2 | -0.079 | 1.59 | 4.801% | -4.28 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.084 | 464 | 156 | 0 | 226.8 | 237.2 | 237.3 | 0.1 | 0 | 0.017 | 10.887 | 0.002 | 649.9% | 237.6 | 0 | 0.375 | 10.205 | 0.4 | -0.079 | 0.037 | 152.8% | -82.95 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.084 | 373 | 159 | 0 | 13.2 | 359.8 | 368.6 | 8.8 | 0.39 | 8.417 | 8.096 | 1.04 | 5.937% | 370.8 | 0.5 | 10.512 | 7.589 | 11 | -0.079 | 1.385 | 4.467% | -4.58 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 691 | 300 | 40 | 209.5 | 441.5 | 474 | 32.5 | -0.86 | 33.308 | 12.805 | 2 | 2.977% | 468.1 | -1.2 | 27.786 | 11.984 | 26.6 | -0.079 | 2 | 3.421% | -2.32 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.11 | 516 | 275 | 12 | 210.5 | 293.5 | 301.5 | 8 | -10.86 | 18.853 | 10.124 | 1.862 | 11.83% | 309.3 | -15.1 | 30.913 | 9.145 | 15.8 | -0.102 | 2 | 5.554% | -3.4 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.11 | 48 | 20 | 0 | 16.9 | 31.1 | 31.1 | 0 | -0.03 | 0.043 | 1.135 | 0.037 | 0% | 30.6 | 0 | -0.435 | 1.016 | -0.5 | -0.102 | 0 | -16.38% | 11.35 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.11 | 420 | 125 | 0 | 30.2 | 389.8 | 402.2 | 12.4 | -0.76 | 13.226 | 8.719 | 1.517 | 6.212% | 397.6 | -1.1 | 8.909 | 7.896 | 7.8 | -0.102 | 1.128 | 9.157% | -9.16 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.11 | 417 | 125 | 0 | 42 | 375 | 386.2 | 11.2 | -0.08 | 11.207 | 8.599 | 1.303 | 6.828% | 384.6 | -0.1 | 9.639 | 7.787 | 9.6 | -0.102 | 1.238 | 7.387% | -7.16 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.11 | 631 | 448 | 7 | 21.3 | 602.7 | 615.5 | 12.8 | 0.85 | 12.013 | 12.534 | 0.958 | 9.04% | 620.3 | 1.2 | 16.406 | 11.323 | 17.6 | -0.102 | 1.449 | 6.096% | -6.28 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.11 | 105 | 12 | 0 | 93 | 12 | 15.4 | 3.4 | -0.01 | 3.403 | 2.731 | 1.246 | 5.67% | 14.8 | 0 | 2.778 | 2.474 | 2.8 | -0.102 | 1.123 | 6.385% | -0.78 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.11 | 320 | 50 | 0 | 144.5 | 175.5 | 193.4 | 17.9 | -3.17 | 21.063 | 5.51 | 2 | 3.279% | 194.1 | -4.4 | 23 | 4.989 | 18.6 | -0.102 | 2 | 2.926% | -1.73 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.11 | 420 | 50 | 0 | 177.5 | 242.5 | 264 | 21.5 | -2.6 | 24.155 | 8.527 | 2 | 3.583% | 262.1 | -3.6 | 23.257 | 7.722 | 19.6 | -0.102 | 2 | 3.644% | -2.27 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.11 | 148 | 80 | 0 | 67 | 81 | 88.4 | 7.4 | -0.06 | 7.542 | 3.5 | 2 | 3.67% | 87.7 | -0.1 | 6.795 | 3.133 | 6.7 | -0.102 | 2 | 3.759% | -2.21 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | SUB | FOSS | -0.11 | 590.7 | 148.8 | 0 | 20.5 | 570.2 | 586.9 | 16.7 | -2.76 | 19.498 | 10.823 | 1.801 | 6.486% | 581.8 | -3.8 | 15.411 | 9.801 | 11.6 | -0.102 | 1.572 | 8.659% | -9.01 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.11 | 590.7 | 148.8 | 0 | 20.5 | 570.2 | 586.9 | 16.7 | -2.76 | 19.498 | 10.823 | 1.801 | 6.486% | 581.8 | -3.8 | 15.411 | 9.801 | 11.6 | -0.102 | 1.572 | 8.659% | -9.01 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.11 | 233 | 150 | 21 | 11.3 | 200.7 | 206.9 | 6.2 | 0.38 | 5.798 | 5.084 | 1.141 | 6.894% | 207.4 | 0.5 | 6.166 | 4.604 | 6.7 | -0.102 | 1.339 | 5.916% | -5.49 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.11 | 355.7 | 193.8 | 0 | 40.4 | 315.3 | 319 | 3.7 | -0.27 | 4.018 | 7.145 | 0.562 | 17.63% | 317.7 | -0.4 | 2.847 | 6.454 | 2.4 | -0.102 | 0.441 | 25.21% | -24.07 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.11 | 824 | 259 | 0 | 21.7 | 802.3 | 818.2 | 15.9 | -2.44 | 18.351 | 14.042 | 1.307 | 9.503% | 818.6 | -3.4 | 19.762 | 12.715 | 16.3 | -0.102 | 1.554 | 8.596% | -9.02 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.11 | 98 | 52 | 0 | 21 | 77 | 84.1 | 7.1 | 0 | 7.012 | 2.318 | 2 | 2.535% | 83.9 | 0 | 6.863 | 2.075 | 6.9 | -0.102 | 2 | 2.419% | -2.04 | 0.017 | 0.05 | 5.933% | 5.163%
Solar | SUN | PVGR | -0.11 | 100 | 0 | 0 | 67.5 | 32.5 | 30.1 | -2.4 | -3.24 | 0.85 | 2.628 | 0.323 | -7.651% | 30.4 | -4.5 | 2.394 | 2.38 | -2.1 | -0.102 | 1.006 | -8.109% | 2.82 | 0.017 | 0.05 | 6.014% | 6.718%
CombinedCycle | CC | COGN | -0.11 | 496 | 353 | 0 | 34.5 | 461.5 | 479.8 | 18.3 | 0.12 | 18.2 | 9.963 | 1.827 | 4.971% | 480.6 | 0.2 | 18.907 | 9 | 19.1 | -0.102 | 2 | 4.416% | -4.43 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.11 | 526.4 | 314.3 | 6.6 | 35.6 | 484.2 | 494.5 | 10.3 | -4.96 | 15.236 | 10.44 | 1.459 | 9.372% | 490.5 | -6.9 | 13.194 | 9.431 | 6.3 | -0.102 | 1.399 | 14.21% | -14.09 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.11 | 122 | 15 | 0 | 106 | 16 | 24.1 | 8.1 | 0.11 | 8.02 | 2.622 | 2 | 2.765% | 22.8 | 0.2 | 6.679 | 2.374 | 6.8 | -0.102 | 2 | 3.054% | -0.43 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.11 | 118 | 15 | 0 | 53.1 | 64.9 | 72 | 7.1 | 0.11 | 6.958 | 2.295 | 2 | 3.055% | 72.1 | 0.2 | 7.048 | 2.018 | 7.2 | -0.102 | 2 | 2.794% | -1.64 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.11 | 525 | 210 | 0 | 87.3 | 437.7 | 449.5 | 11.8 | 1.17 | 10.659 | 13.799 | 0.772 | 8.159% | 454.7 | 1.6 | 15.412 | 12.496 | 17 | -0.102 | 1.233 | 5.252% | -4.72 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.11 | 525 | 210 | 0 | 81.2 | 443.8 | 454.6 | 10.8 | 0.14 | 10.66 | 13.799 | 0.772 | 8.915% | 458.6 | 0.2 | 14.606 | 12.496 | 14.8 | -0.102 | 1.169 | 6.032% | -5.5 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.11 | 795 | 300 | 0 | 99.6 | 695.4 | 707.4 | 12 | 0.33 | 11.682 | 20.896 | 0.559 | 12.15% | 712.3 | 0.5 | 16.465 | 18.923 | 16.9 | -0.102 | 0.87 | 7.999% | -7.54 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.11 | 654.1 | 250 | 93.4 | 21.7 | 539 | 557.1 | 18.1 | 0.1 | 17.979 | 11.261 | 1.597 | 6.627% | 559.9 | 0.1 | 20.697 | 10.173 | 20.9 | -0.102 | 2 | 5.322% | -4.73 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.11 | 712.1 | 452.1 | 26.6 | 98.2 | 587.3 | 608.2 | 20.9 | -0.06 | 21.018 | 13.769 | 1.526 | 6.248% | 606.8 | -0.1 | 19.625 | 12.439 | 19.5 | -0.102 | 1.578 | 6.21% | -5.52 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.11 | 714.7 | 444.8 | 28.2 | 124.9 | 561.6 | 585.2 | 23.6 | 1.06 | 22.6 | 13.79 | 1.639 | 5.553% | 590.1 | 1.5 | 27.044 | 12.457 | 28.5 | -0.102 | 2 | 4.264% | -3.61 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.11 | 713.9 | 444.3 | 34.2 | 141.8 | 537.9 | 560.1 | 22.2 | 1.06 | 21.14 | 13.653 | 1.548 | 5.897% | 565.8 | 1.5 | 26.386 | 12.333 | 27.9 | -0.102 | 2 | 4.351% | -3.53 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.11 | 64 | 41 | 0 | 22.4 | 41.6 | 45.3 | 3.7 | 0.03 | 3.695 | 1.514 | 2 | 3.179% | 44.9 | 0 | 3.261 | 1.355 | 3.3 | -0.102 | 2 | 3.306% | -2.3 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.11 | 65 | 41 | 0 | 23.9 | 41.1 | 44.9 | 3.8 | -0.03 | 3.845 | 1.537 | 2 | 3.143% | 44.7 | 0 | 3.644 | 1.376 | 3.6 | -0.102 | 2 | 3.077% | -2.09 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.11 | 338 | 190 | 0 | 91.9 | 246.1 | 260.8 | 14.7 | -0.59 | 15.294 | 6.789 | 2 | 4.217% | 268.6 | -0.8 | 23.278 | 6.133 | 22.5 | -0.102 | 2 | 2.555% | -2 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.11 | 114 | 45 | 0 | 68.6 | 45.4 | 54.7 | 9.3 | -0.11 | 9.45 | 2.29 | 2 | 2.25% | 57.2 | -0.1 | 11.929 | 2.069 | 11.8 | -0.102 | 2 | 1.645% | -0.7 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.11 | 205 | 100 | 0 | 87.6 | 117.4 | 123.8 | 6.4 | -1 | 7.423 | 4.118 | 1.803 | 5.877% | 127.7 | -1.4 | 11.7 | 3.72 | 10.3 | -0.102 | 2 | 3.386% | -2.09 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.11 | 250 | 234 | 0 | 5.8 | 244.2 | 246.2 | 2 | 0.64 | 1.348 | 5.022 | 0.268 | 22.93% | 246.4 | 0.9 | 1.327 | 4.536 | 2.2 | -0.102 | 0.293 | 19.33% | -20.34 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.11 | 250 | 234 | 0 | 5.7 | 244.3 | 249.4 | 5.1 | 0.71 | 4.385 | 5.022 | 0.873 | 8.992% | 249.8 | 1 | 4.525 | 4.536 | 5.5 | -0.102 | 0.998 | 7.732% | -8.14 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.11 | 155 | 80 | 0 | 6.8 | 148.2 | 152.4 | 4.2 | 0.07 | 4.159 | 3.669 | 1.134 | 6.773% | 153.1 | 0.1 | 4.798 | 3.323 | 4.9 | -0.102 | 1.444 | 5.383% | -5.54 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.11 | 527 | 262 | 0 | 16.5 | 510.5 | 517.7 | 7.2 | -0.11 | 7.336 | 10.136 | 0.724 | 13.43% | 523.5 | -0.2 | 13.139 | 8.914 | 13 | -0.102 | 1.474 | 6.896% | -7.2 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.11 | 713 | 271 | 70 | 16.4 | 626.6 | 644.8 | 18.2 | 0.66 | 17.554 | 12.916 | 1.359 | 7.184% | 650 | 0.9 | 22.548 | 11.667 | 23.4 | -0.102 | 1.933 | 5.181% | -4.91 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.11 | 679 | 300 | 40 | 149.9 | 489.1 | 522.5 | 33.4 | 0.86 | 32.6 | 12.836 | 2 | 3.728% | 517.9 | 1.2 | 27.682 | 11.596 | 28.8 | -0.102 | 2 | 4.009% | -3.11 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.098 | 587 | 220 | 0 | 30.8 | 556.2 | 562.6 | 6.4 | 0.33 | 6.17 | 14.47 | 0.426 | 14.99% | 559.2 | 0.5 | 2.551 | 13.578 | 3 | -0.093 | 0.188 | 30.34% | -30.27 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.098 | 412 | 115 | 0 | 281.6 | 130.4 | 139.9 | 9.5 | 0.86 | 8.578 | 6.301 | 1.361 | 7.089% | 139.9 | 1.2 | 8.24 | 5.796 | 9.5 | -0.093 | 1.422 | 6.728% | -2.24 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.098 | 194 | 150 | 0 | 38.2 | 155.8 | 167.1 | 11.3 | -0.49 | 11.778 | 3.649 | 2 | 2.807% | 167.1 | -0.7 | 12.039 | 3.418 | 11.3 | -0.093 | 2 | 2.664% | -2.25 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.098 | 560 | 135 | 0 | 127.9 | 432.1 | 452.2 | 20.1 | 3.96 | 16.173 | 12.011 | 1.346 | 4.552% | 456.2 | 5.5 | 18.633 | 11.271 | 24.1 | -0.093 | 1.653 | 3.603% | -2.93 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.098 | 420 | 125 | 0 | 178.9 | 241.1 | 257.3 | 16.2 | 1.16 | 15.005 | 7.429 | 2 | 4.236% | 287.7 | 1.6 | 45.032 | 6.971 | 46.6 | -0.093 | 2 | 1.398% | -0.84 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.098 | 417 | 125 | 0 | 254.5 | 162.5 | 175.9 | 13.4 | -0.4 | 13.796 | 7.031 | 1.962 | 5.085% | 173.3 | -0.6 | 11.352 | 6.598 | 10.8 | -0.093 | 1.721 | 5.987% | -2.45 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.098 | 410 | 70 | 0 | 327.4 | 82.6 | 91.1 | 8.5 | -1.3 | 9.764 | 7.494 | 1.303 | 7.882% | 88.8 | -1.8 | 7.973 | 7.032 | 6.2 | -0.093 | 1.134 | 10.25% | -2.17 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.098 | 645 | 300 | 0 | 132 | 513 | 537.9 | 24.9 | 1.06 | 23.846 | 13.728 | 1.737 | 4.232% | 535.8 | 1.5 | 21.336 | 12.882 | 22.8 | -0.093 | 1.656 | 4.386% | -3.67 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.098 | 590.3 | 148.3 | 0 | 14.5 | 575.8 | 588.4 | 12.6 | -2.23 | 14.807 | 10.132 | 1.461 | 7.654% | 584.6 | -3.1 | 11.911 | 9.508 | 8.8 | -0.093 | 1.253 | 10.4% | -10.68 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.098 | 590.3 | 148.3 | 0 | 14.5 | 575.8 | 588.4 | 12.6 | -2.23 | 14.807 | 10.132 | 1.461 | 7.654% | 584.6 | -3.1 | 11.911 | 9.508 | 8.8 | -0.093 | 1.253 | 10.4% | -10.68 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.098 | 886.9 | 461 | 141 | 121 | 624.9 | 651.5 | 26.6 | -1.86 | 28.41 | 14.029 | 2 | 5.447% | 663.3 | -2.6 | 40.96 | 13.143 | 38.4 | -0.093 | 2 | 3.581% | -2.66 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 899.1 | 461 | 141 | 124.8 | 633.3 | 661.1 | 27.8 | 0.24 | 27.658 | 14.258 | 1.94 | 5.284% | 668.8 | 0.3 | 35.22 | 13.358 | 35.5 | -0.093 | 2 | 3.926% | -2.91 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.098 | 237 | 150 | 21 | 50.3 | 165.7 | 172.5 | 6.8 | 0.07 | 6.73 | 4.367 | 1.541 | 5.697% | 173.9 | 0.1 | 8.078 | 4.098 | 8.2 | -0.093 | 1.971 | 4.483% | -3.3 | 0.017 | 0.05 | 5.933% | 5.163%
Wind | WND | WIND | -0.098 | 40.8 | 0 | 0 | 4.7 | 36.1 | 36.8 | 0.7 | -0.4 | 1.077 | 1.006 | 1.07 | 9.56% | 37.7 | -0.6 | 2.154 | 0.944 | 1.6 | -0.093 | 2 | 3.97% | -3.67 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.098 | 608 | 305 | 111 | 169.2 | 327.8 | 337.6 | 9.8 | -0.9 | 10.725 | 9.348 | 1.147 | 10.14% | 339.5 | -1.3 | 12.913 | 8.757 | 11.7 | -0.093 | 1.475 | 8.057% | -4.57 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 621 | 305 | 111 | 202.4 | 307.6 | 321.9 | 14.3 | 0.09 | 14.241 | 9.592 | 1.485 | 7.095% | 324.9 | 0.1 | 17.231 | 8.986 | 17.3 | -0.093 | 1.918 | 5.566% | -2.9 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 600.6 | 260 | 0 | 286.1 | 314.5 | 317.1 | 2.6 | 1 | 1.552 | 11.296 | 0.137 | 37.74% | 323.6 | 1.4 | 7.682 | 10.583 | 9.1 | -0.093 | 0.726 | 10.23% | -5.64 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.098 | 78 | 51 | 0 | 18.1 | 59.9 | 65.4 | 5.5 | 0 | 5.542 | 1.728 | 2 | 2.322% | 65.4 | 0 | 5.518 | 1.609 | 5.5 | -0.093 | 2 | 2.203% | -1.77 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 499 | 349 | 0 | 51.7 | 447.3 | 464.6 | 17.3 | 0.06 | 17.284 | 9.386 | 1.842 | 4.713% | 467.9 | 0.1 | 20.561 | 8.792 | 20.6 | -0.093 | 2 | 3.756% | -3.55 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 518.6 | 411 | 42.8 | 27.6 | 448.2 | 454.8 | 6.6 | 0.47 | 6.192 | 8.948 | 0.692 | 12.84% | 455 | 0.7 | 6.217 | 8.382 | 6.8 | -0.093 | 0.742 | 11.83% | -10.76 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 527.9 | 314.3 | 36.8 | 43.4 | 447.7 | 461 | 13.3 | 0.21 | 13.108 | 9.237 | 1.419 | 6.485% | 459.2 | 0.3 | 11.23 | 8.654 | 11.5 | -0.093 | 1.298 | 7.118% | -6.36 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.098 | 244 | 150 | 21 | 70.4 | 152.6 | 158.8 | 6.2 | 0.7 | 5.486 | 3.816 | 1.438 | 6.433% | 160.2 | 1 | 6.577 | 3.581 | 7.6 | -0.093 | 1.837 | 4.98% | -3.28 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.098 | 815 | 300 | 0 | 280.1 | 534.9 | 543.3 | 8.4 | -4.67 | 13.064 | 20.09 | 0.65 | 15.85% | 541.5 | -6.5 | 13.083 | 18.851 | 6.6 | -0.093 | 0.694 | 19.14% | -13.23 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.098 | 825 | 300 | 0 | 499 | 326 | 332.6 | 6.6 | -4.82 | 11.423 | 20.336 | 0.562 | 20.42% | 329.9 | -6.7 | 10.535 | 19.083 | 3.9 | -0.093 | 0.552 | 32.8% | -13.65 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.098 | 810 | 300 | 0 | 356.5 | 453.5 | 469.1 | 15.6 | 2.48 | 13.124 | 19.967 | 0.657 | 8.483% | 469.7 | 3.5 | 12.722 | 18.736 | 16.2 | -0.093 | 0.679 | 7.752% | -4.57 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.098 | 510 | 210 | 0 | 274.3 | 235.7 | 239.6 | 3.9 | -2.36 | 6.189 | 12.572 | 0.492 | 21.37% | 238.2 | -3.3 | 5.777 | 11.797 | 2.5 | -0.093 | 0.49 | 31.63% | -15.39 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.098 | 775 | 300 | 0 | 289.5 | 485.5 | 506.1 | 20.6 | 0.4 | 20.191 | 19.104 | 1.057 | 6.146% | 512.8 | 0.6 | 26.744 | 17.926 | 27.3 | -0.093 | 1.492 | 4.401% | -2.9 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | WDS | STM | -0.098 | 105 | 70 | 0 | 34.7 | 70.3 | 73.4 | 3.1 | 0.06 | 3.011 | 2.326 | 1.294 | 5.541% | 73.3 | 0.1 | 2.875 | 2.166 | 3 | -0.093 | 1.327 | 5.434% | -3.82 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.098 | 628.6 | 250 | 152.1 | 50.6 | 425.9 | 453.2 | 27.3 | 5.81 | 21.473 | 8.963 | 2 | 3.762% | 464 | 8.1 | 30.002 | 8.397 | 38.1 | -0.093 | 2 | 2.558% | -1.83 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 618 | 453 | 22.9 | 141.5 | 453.6 | 475.9 | 22.3 | -0.12 | 22.372 | 11.193 | 1.999 | 4.528% | 482.4 | -0.2 | 28.95 | 10.486 | 28.8 | -0.093 | 2 | 3.327% | -2.57 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 104.5 | 80 | 15.8 | 6.8 | 81.9 | 83.4 | 1.5 | 0.18 | 1.261 | 1.668 | 0.756 | 11.4% | 84.1 | 0.2 | 1.911 | 1.563 | 2.2 | -0.093 | 1.223 | 7.375% | -6.07 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.098 | 56 | 22.5 | 0 | 33.3 | 22.7 | 26.1 | 3.4 | -0.02 | 3.4 | 1.24 | 2 | 2.699% | 32.7 | 0 | 10.099 | 1.155 | 10 | -0.093 | 2 | 0.8708% | -0.37 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.098 | 705 | 420 | 0 | 112.5 | 592.5 | 617.6 | 25.1 | 1.76 | 23.27 | 13.26 | 1.755 | 4.589% | 618.1 | 2.4 | 23.132 | 12.422 | 25.6 | -0.093 | 1.862 | 4.27% | -3.78 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 279.9 | 118 | 65 | 35.4 | 179.5 | 186.8 | 7.3 | -0.29 | 7.589 | 4.043 | 1.877 | 6.266% | 191.8 | -0.4 | 12.695 | 3.787 | 12.3 | -0.093 | 2 | 3.529% | -2.38 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.098 | 932.6 | 322 | 0 | 52.6 | 880 | 905.8 | 25.8 | -3.41 | 29.168 | 16.409 | 1.778 | 5.905% | 910 | -4.7 | 34.726 | 15.397 | 30 | -0.093 | 2 | 4.819% | -4.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.098 | 932.6 | 322 | 0 | 52.6 | 880 | 905.8 | 25.8 | -3.41 | 29.168 | 16.409 | 1.778 | 5.905% | 910 | -4.7 | 34.726 | 15.397 | 30 | -0.093 | 2 | 4.819% | -4.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.098 | 932.6 | 322 | 0 | 52.6 | 880 | 905.8 | 25.8 | -3.41 | 29.168 | 16.409 | 1.778 | 5.905% | 910 | -4.7 | 34.726 | 15.397 | 30 | -0.093 | 2 | 4.819% | -4.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.098 | 932.6 | 322 | 0 | 52.6 | 880 | 905.8 | 25.8 | -3.41 | 29.168 | 16.409 | 1.778 | 5.905% | 910 | -4.7 | 34.726 | 15.397 | 30 | -0.093 | 2 | 4.819% | -4.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.098 | 78 | 56 | 0 | 20.8 | 57.2 | 59.2 | 2 | 0.15 | 1.823 | 1.728 | 1.055 | 6.384% | 59.2 | 0.2 | 1.778 | 1.609 | 2 | -0.093 | 1.105 | 6.059% | -4.66 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 845 | 465 | 122.4 | 147.6 | 575 | 599.2 | 24.2 | -1.48 | 25.665 | 13.591 | 1.888 | 5.704% | 601.1 | -2.1 | 28.18 | 12.732 | 26.1 | -0.093 | 2 | 5.019% | -3.6 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.098 | 169 | 27 | 0 | 139.8 | 29.2 | 37.9 | 8.7 | 1.06 | 7.652 | 1.759 | 2 | 3.179% | 36.2 | 1.5 | 5.518 | 1.618 | 7 | -0.093 | 2 | 3.75% | -0.67 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.098 | 684 | 300 | 40 | 203.7 | 440.3 | 467.6 | 27.3 | 1.73 | 25.56 | 12.114 | 2 | 4.093% | 466.7 | 2.4 | 23.968 | 11.348 | 26.4 | -0.093 | 2 | 4.017% | -2.72 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 615.4 | 252 | 146.5 | 216.6 | 252.3 | 272.9 | 20.6 | 1.52 | 19.063 | 6.894 | 2 | 3.088% | 277.2 | 2.1 | 22.773 | 6.541 | 24.9 | -0.059 | 2 | 2.431% | -1.05 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.062 | 581 | 220 | 0 | 357.7 | 223.3 | 233.1 | 9.8 | 0.14 | 9.588 | 11.272 | 0.851 | 6.129% | 231.5 | 0.2 | 7.936 | 10.712 | 8.2 | -0.059 | 0.741 | 6.971% | -2.81 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.062 | 577 | 220 | 0 | 351.6 | 225.4 | 237.1 | 11.7 | 1.19 | 10.53 | 11.195 | 0.941 | 5.098% | 236.7 | 1.7 | 9.726 | 10.638 | 11.3 | -0.059 | 0.914 | 5.024% | -2.06 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.062 | 237 | 160 | 10 | 63.2 | 163.8 | 165.3 | 1.5 | -0.18 | 1.647 | 3.338 | 0.493 | 16.35% | 164.8 | -0.2 | 1.232 | 3.167 | 1 | -0.059 | 0.389 | 23.33% | -16.9 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 459 | 300 | 0 | 150.7 | 308.3 | 316.3 | 8 | 0.52 | 7.444 | 6.749 | 1.103 | 5.932% | 314.7 | 0.7 | 5.634 | 6.403 | 6.4 | -0.059 | 0.88 | 7.057% | -4.97 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 346 | 94 | 0 | 252 | 94 | 105.4 | 11.4 | 0.35 | 10.987 | 5.088 | 2 | 3.139% | 109.2 | 0.5 | 14.686 | 4.827 | 15.2 | -0.059 | 2 | 2.24% | -0.64 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 564 | 313 | 72 | 72.7 | 419.3 | 423.3 | 4 | -0.89 | 4.838 | 7.234 | 0.669 | 14.58% | 422 | -1.2 | 3.931 | 6.863 | 2.7 | -0.059 | 0.573 | 20.55% | -16.04 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 204.5 | 155.5 | 0 | 48.3 | 156.2 | 162.6 | 6.4 | 0.37 | 6.054 | 3.007 | 2 | 3.306% | 163.2 | 0.5 | 6.506 | 2.853 | 7 | -0.059 | 2 | 2.877% | -2.3 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 186 | 101 | 6 | 78.8 | 101.2 | 103.9 | 2.7 | 0.35 | 2.373 | 2.647 | 0.897 | 7.129% | 104.1 | 0.5 | 2.45 | 2.511 | 2.9 | -0.059 | 0.976 | 6.317% | -3.6 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.062 | 560 | 135 | 0 | 423.7 | 136.3 | 147.4 | 11.1 | -0.1 | 11.129 | 8.149 | 1.366 | 5.216% | 147.5 | -0.1 | 11.327 | 7.744 | 11.2 | -0.059 | 1.463 | 4.919% | -1.26 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.062 | 417 | 125 | 0 | 292 | 125 | 134.8 | 9.8 | -0.07 | 9.827 | 5.659 | 1.737 | 4.4% | 133.1 | -0.1 | 8.183 | 5.378 | 8.1 | -0.059 | 1.522 | 5.066% | -1.59 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.062 | 1091 | 430 | 170 | 223.8 | 697.2 | 707.5 | 10.3 | 0.58 | 9.769 | 13.542 | 0.721 | 10.95% | 703.8 | 0.8 | 5.844 | 12.848 | 6.6 | -0.059 | 0.455 | 16.26% | -10.91 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.062 | 749 | 93 | 0 | 654.8 | 94.2 | 107.5 | 13.3 | -0.41 | 13.647 | 7.515 | 1.816 | 5.824% | 109.2 | -0.6 | 15.509 | 6.986 | 15 | -0.059 | 2 | 4.914% | -0.65 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.062 | 380 | 270 | 75 | 34.3 | 270.7 | 273.4 | 2.7 | 0.41 | 2.291 | 4.485 | 0.511 | 14.55% | 274 | 0.6 | 2.711 | 4.255 | 3.3 | -0.059 | 0.637 | 11.33% | -8.47 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.062 | 645 | 300 | 0 | 341.5 | 303.5 | 320.3 | 16.8 | -1.12 | 17.87 | 10.935 | 1.634 | 3.969% | 318.9 | -1.6 | 16.953 | 10.392 | 15.4 | -0.059 | 1.631 | 4.12% | -2.03 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.062 | 540 | 319 | 72 | 148.8 | 319.2 | 329.2 | 10 | -0.06 | 10.03 | 6.881 | 1.458 | 5.583% | 329.6 | -0.1 | 10.454 | 6.529 | 10.4 | -0.059 | 1.601 | 5.108% | -3.17 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 347 | 149 | 11 | 185.4 | 150.6 | 158.4 | 7.8 | 0.04 | 7.746 | 4.941 | 1.568 | 4.601% | 160.1 | 0.1 | 9.481 | 4.687 | 9.5 | -0.059 | 2 | 3.595% | -1.64 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 527 | 337.4 | 0 | 172.2 | 354.8 | 369.7 | 14.9 | -0.17 | 15.026 | 7.749 | 1.939 | 3.657% | 379.6 | -0.2 | 24.968 | 7.351 | 24.8 | -0.059 | 2 | 2.091% | -1.48 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.062 | 586.2 | 152.7 | 0 | 410.9 | 175.3 | 193 | 17.7 | 0.21 | 17.473 | 7.928 | 2 | 3.424% | 193.2 | 0.3 | 17.587 | 7.534 | 17.9 | -0.059 | 2 | 3.222% | -1.01 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.062 | 586.2 | 152.7 | 0 | 410.9 | 175.3 | 193 | 17.7 | 0.21 | 17.473 | 7.928 | 2 | 3.424% | 193.2 | 0.3 | 17.587 | 7.534 | 17.9 | -0.059 | 2 | 3.222% | -1.01 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.062 | 594.1 | 152.1 | 0 | 375.5 | 218.6 | 233 | 14.4 | 0.53 | 13.928 | 8.099 | 1.72 | 4.265% | 232.2 | 0.7 | 12.877 | 7.696 | 13.6 | -0.059 | 1.673 | 4.298% | -1.66 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.062 | 594.1 | 152.1 | 0 | 375.5 | 218.6 | 233 | 14.4 | 0.53 | 13.928 | 8.099 | 1.72 | 4.265% | 232.2 | 0.7 | 12.877 | 7.696 | 13.6 | -0.059 | 1.673 | 4.298% | -1.66 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.062 | 424.1 | 180.3 | 0 | 217.9 | 206.2 | 216.1 | 9.9 | -0.16 | 10.014 | 7.097 | 1.411 | 4.429% | 215.9 | -0.2 | 9.92 | 6.744 | 9.7 | -0.059 | 1.471 | 4.302% | -2.19 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.062 | 488 | 291 | 11 | 181.6 | 295.4 | 299.3 | 3.9 | -0.06 | 3.912 | 7.014 | 0.558 | 12.94% | 297.2 | -0.1 | 1.882 | 6.654 | 1.8 | -0.059 | 0.283 | 26.67% | -16.94 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.062 | 96.6 | 0 | 0 | 73 | 23.6 | 24.4 | 0.8 | -0.27 | 1.146 | 1.874 | 0.612 | 12.51% | 24.2 | -0.4 | 1.046 | 1.781 | 0.6 | -0.059 | 0.587 | 15.88% | -4.02 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.062 | 96.6 | 0 | 0 | 77.4 | 19.2 | 20.2 | 1 | -0.29 | 1.271 | 1.874 | 0.678 | 10.01% | 20.1 | -0.4 | 1.29 | 1.781 | 0.9 | -0.059 | 0.725 | 10.59% | -2.17 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.062 | 241 | 164 | 32 | 43.2 | 165.8 | 172.3 | 6.5 | -0.47 | 6.985 | 3.073 | 2 | 3.836% | 172.4 | -0.7 | 7.232 | 2.916 | 6.6 | -0.059 | 2 | 3.595% | -2.59 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 241 | 168 | 31 | 40.9 | 169.1 | 174.9 | 5.8 | 0.47 | 5.275 | 3.088 | 1.708 | 4.299% | 175 | 0.7 | 5.224 | 2.929 | 5.9 | -0.059 | 1.783 | 4.021% | -2.96 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.062 | 243 | 150 | 21 | 68.9 | 153.1 | 157.2 | 4.1 | -0.05 | 4.112 | 3.514 | 1.17 | 6.131% | 157.2 | -0.1 | 4.193 | 3.339 | 4.1 | -0.059 | 1.256 | 5.835% | -3.85 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 618.3 | 260 | 0 | 347.6 | 270.7 | 272.1 | 1.4 | 0.07 | 1.382 | 9.092 | 0.152 | 45.66% | 276.7 | 0.1 | 5.965 | 8.625 | 6 | -0.059 | 0.692 | 10.14% | -4.66 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 621.8 | 260 | 0 | 351.4 | 270.4 | 271.8 | 1.4 | -0.07 | 1.383 | 9.143 | 0.151 | 45.91% | 276.4 | -0.1 | 6.094 | 8.674 | 6 | -0.059 | 0.703 | 10.2% | -4.65 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.062 | 824 | 259 | 0 | 556.3 | 267.7 | 291.6 | 23.9 | 0.61 | 23.242 | 10.268 | 2 | 3.564% | 292 | 0.8 | 23.416 | 9.757 | 24.3 | -0.059 | 2 | 3.336% | -1.14 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.062 | 836 | 258 | 0 | 573.2 | 262.8 | 287.2 | 24.4 | 0.94 | 23.458 | 10.61 | 2 | 3.542% | 288.3 | 1.3 | 24.172 | 10.082 | 25.5 | -0.059 | 2 | 3.225% | -1.06 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.062 | 69 | 57 | 0 | 9.5 | 59.5 | 64 | 4.5 | 0 | 4.539 | 1.196 | 2 | 1.591% | 64.2 | 0 | 4.723 | 1.13 | 4.7 | -0.059 | 2 | 1.45% | -1.3 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 527.6 | 411 | 55.4 | 60.9 | 411.3 | 416.2 | 4.9 | -0.4 | 5.337 | 6.944 | 0.769 | 11.13% | 415.9 | -0.6 | 5.127 | 6.588 | 4.6 | -0.059 | 0.778 | 11.28% | -9.23 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 506.6 | 314.3 | 65.9 | 116.8 | 323.9 | 333.3 | 9.4 | 2.19 | 7.186 | 6.48 | 1.109 | 5.572% | 331.9 | 3.1 | 4.994 | 6.148 | 8 | -0.059 | 0.812 | 6.231% | -4.18 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.062 | 258 | 150 | 21 | 83 | 154 | 159 | 5 | -0.17 | 5.148 | 3.193 | 1.612 | 5.338% | 159.4 | -0.2 | 5.579 | 3.035 | 5.4 | -0.059 | 1.838 | 4.703% | -2.94 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.062 | 805 | 300 | 0 | 504.4 | 300.6 | 314.3 | 13.7 | 0.12 | 13.628 | 15.618 | 0.873 | 6.074% | 313.7 | 0.2 | 12.919 | 14.842 | 13.1 | -0.059 | 0.87 | 6.045% | -2.37 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.062 | 450 | 220 | 0 | 215.5 | 234.5 | 246.4 | 11.9 | 0.38 | 11.499 | 8.731 | 1.317 | 3.91% | 245.9 | 0.5 | 10.92 | 8.297 | 11.4 | -0.059 | 1.316 | 3.884% | -2.12 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.062 | 810 | 300 | 0 | 508.1 | 301.9 | 315.1 | 13.2 | -0.29 | 13.488 | 15.715 | 0.858 | 6.343% | 314.7 | -0.4 | 13.169 | 14.934 | 12.8 | -0.059 | 0.882 | 6.225% | -2.43 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.062 | 510 | 210 | 0 | 294.7 | 215.3 | 217.4 | 2.1 | -0.12 | 2.25 | 9.895 | 0.227 | 25.11% | 215.5 | -0.2 | 0.4 | 9.403 | 0.2 | -0.059 | 0.043 | 250.9% | -111.1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | WDS | STM | -0.062 | 105 | 70 | 0 | 34.4 | 70.6 | 72.9 | 2.3 | 0 | 2.341 | 1.82 | 1.286 | 4.73% | 72.7 | 0 | 2.129 | 1.719 | 2.1 | -0.059 | 1.238 | 4.93% | -3.46 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.062 | 315 | 210 | 8 | 95.4 | 211.6 | 216.4 | 4.8 | 0.65 | 4.129 | 4.514 | 0.915 | 6.787% | 218.7 | 0.9 | 6.197 | 4.283 | 7.1 | -0.059 | 1.447 | 4.367% | -3.08 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 517 | 314.7 | 45 | 154.8 | 317.2 | 321.7 | 4.5 | 0.51 | 3.961 | 6.94 | 0.571 | 11.88% | 330.7 | 0.7 | 12.713 | 6.584 | 13.5 | -0.059 | 1.931 | 3.768% | -2.43 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 514 | 344.1 | 45 | 123.3 | 345.7 | 350.8 | 5.1 | -1.1 | 6.23 | 6.896 | 0.903 | 10.42% | 360.1 | -1.5 | 15.982 | 6.542 | 14.4 | -0.059 | 2 | 3.512% | -2.48 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 755.7 | 470.4 | 58 | 225.6 | 472.1 | 492.7 | 20.6 | 0.65 | 19.969 | 10.259 | 1.947 | 3.792% | 503.3 | 0.9 | 30.268 | 9.733 | 31.2 | -0.059 | 2 | 2.383% | -1.56 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 244 | 168 | 0 | 73 | 171 | 174.6 | 3.6 | 0.35 | 3.168 | 3.588 | 0.883 | 7.012% | 175.5 | 0.5 | 3.957 | 3.404 | 4.5 | -0.059 | 1.163 | 5.338% | -3.92 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 690 | 420 | 0 | 252.6 | 437.4 | 455.7 | 18.3 | 4.43 | 13.912 | 10.146 | 1.371 | 3.898% | 455.4 | 6.2 | 11.889 | 9.625 | 18 | -0.059 | 1.235 | 3.771% | -2.51 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 284.4 | 118 | 65 | 57.1 | 162.3 | 166.4 | 4.1 | 1.18 | 2.91 | 3.227 | 0.902 | 7.175% | 170.4 | 1.6 | 6.453 | 3.061 | 8.1 | -0.059 | 2 | 3.456% | -2.07 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.062 | 932.9 | 322 | 0 | 608.7 | 324.2 | 341.4 | 17.2 | -0.33 | 17.544 | 7.221 | 2 | 5.606% | 343.8 | -0.5 | 20.036 | 6.862 | 19.6 | -0.059 | 2 | 4.682% | -1.71 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.062 | 932.9 | 322 | 0 | 608.7 | 324.2 | 341.4 | 17.2 | -0.33 | 17.544 | 7.221 | 2 | 5.606% | 343.8 | -0.5 | 20.036 | 6.862 | 19.6 | -0.059 | 2 | 4.682% | -1.71 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.062 | 932.9 | 322 | 0 | 608.7 | 324.2 | 341.4 | 17.2 | -0.33 | 17.544 | 7.221 | 2 | 5.606% | 343.8 | -0.5 | 20.036 | 6.862 | 19.6 | -0.059 | 2 | 4.682% | -1.71 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.062 | 932.9 | 322 | 0 | 608.7 | 324.2 | 341.4 | 17.2 | -0.33 | 17.544 | 7.221 | 2 | 5.606% | 343.8 | -0.5 | 20.036 | 6.862 | 19.6 | -0.059 | 2 | 4.682% | -1.71 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.062 | 575 | 295 | 0 | 268.8 | 306.2 | 308.2 | 2 | -0.31 | 2.332 | 11.156 | 0.209 | 29.72% | 308.5 | -0.4 | 2.786 | 10.601 | 2.3 | -0.059 | 0.263 | 24.6% | -13.74 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.062 | 155 | 80 | 0 | 36.1 | 118.9 | 123.7 | 4.8 | -0.25 | 5.04 | 2.765 | 1.823 | 3.343% | 125.5 | -0.4 | 6.888 | 2.627 | 6.6 | -0.059 | 2 | 2.314% | -1.86 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.062 | 155 | 80 | 0 | 25.5 | 129.5 | 134.5 | 5 | -0.66 | 5.686 | 2.743 | 2 | 3.209% | 135.9 | -0.9 | 7.409 | 2.607 | 6.4 | -0.059 | 2 | 2.386% | -2.09 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.062 | 81 | 71 | 4 | 5.7 | 71.3 | 73.1 | 1.8 | -0.06 | 1.841 | 1.132 | 1.626 | 4.666% | 74.1 | -0.1 | 2.839 | 1.074 | 2.8 | -0.059 | 2 | 2.855% | -2.62 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.062 | 664 | 155 | 0 | 354.2 | 309.8 | 324.2 | 14.4 | -0.08 | 14.489 | 11.32 | 1.28 | 4.767% | 323.3 | -0.1 | 13.617 | 10.757 | 13.5 | -0.059 | 1.266 | 4.839% | -2.37 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.062 | 555 | 156 | 0 | 246.7 | 308.3 | 321.3 | 13 | -0.4 | 13.437 | 9.486 | 1.416 | 4.414% | 321.2 | -0.6 | 13.497 | 9.015 | 12.9 | -0.059 | 1.497 | 4.233% | -2.47 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.062 | 577 | 159 | 0 | 284.7 | 292.3 | 303 | 10.7 | -0.07 | 10.708 | 9.725 | 1.101 | 5.575% | 303.2 | -0.1 | 10.922 | 9.242 | 10.9 | -0.059 | 1.182 | 5.208% | -2.77 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.062 | 528 | 307 | 0 | 149.6 | 378.4 | 387.1 | 8.7 | -0.78 | 9.522 | 8.554 | 1.113 | 6.275% | 386.7 | -1.1 | 9.437 | 8.129 | 8.3 | -0.059 | 1.161 | 6.259% | -4.71 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.062 | 356 | 185 | 35 | 134.2 | 186.8 | 195.1 | 8.3 | -0.09 | 8.421 | 4.72 | 1.784 | 4.436% | 196.9 | -0.1 | 10.265 | 4.478 | 10.1 | -0.059 | 2 | 3.469% | -1.91 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.062 | 719 | 300 | 40 | 374.1 | 304.9 | 320.9 | 16 | 0.86 | 15.148 | 9.985 | 1.517 | 4.645% | 327.5 | 1.2 | 21.403 | 9.473 | 22.6 | -0.059 | 2 | 3.13% | -1.39 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.077 | 621 | 357 | 62 | 178.3 | 380.7 | 394.3 | 13.6 | 0.41 | 13.165 | 6.091 | 2 | 5.862% | 396.6 | 0.6 | 15.297 | 6.008 | 15.9 | -0.077 | 2 | 5.014% | -3.07 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.077 | 262.5 | 164.5 | 0 | 97.9 | 164.6 | 169.2 | 4.6 | 2.64 | 1.933 | 2.86 | 0.676 | 7.33% | 169.8 | 3.7 | 1.592 | 2.821 | 5.2 | -0.077 | 0.564 | 6.484% | -4.06 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.077 | 193 | 111 | 0 | 62.8 | 130.2 | 131.9 | 1.7 | 0.06 | 1.684 | 2.103 | 0.801 | 14.59% | 133.1 | 0.1 | 2.861 | 2.074 | 2.9 | -0.077 | 1.379 | 8.551% | -5.75 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.077 | 420 | 125 | 0 | 246.1 | 173.9 | 177.8 | 3.9 | 1.03 | 2.852 | 4.164 | 0.685 | 13.83% | 175 | 1.4 | -0.282 | 4.109 | 1.1 | -0.077 | 0 | 49.03% | -20.26 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.077 | 417 | 125 | 0 | 267.5 | 149.5 | 151.1 | 1.6 | 0.62 | 0.952 | 4.194 | 0.227 | 33.46% | 151.3 | 0.9 | 0.893 | 4.14 | 1.8 | -0.077 | 0.216 | 29.75% | -10.64 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.077 | 431 | 300 | 68 | 51 | 312 | 316.9 | 4.9 | -0.41 | 5.284 | 3.955 | 1.336 | 11.29% | 318.1 | -0.6 | 6.689 | 3.902 | 6.1 | -0.077 | 1.714 | 9.072% | -6.56 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.077 | 645 | 300 | 0 | 71.2 | 573.8 | 589.5 | 15.7 | -0.59 | 16.339 | 7.975 | 2 | 5.274% | 591.2 | -0.8 | 18.264 | 7.871 | 17.4 | -0.077 | 2 | 4.759% | -4.23 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.077 | 447 | 343 | 48 | 29.8 | 369.2 | 378.2 | 9 | -0.21 | 9.268 | 4.348 | 2 | 6.377% | 378.7 | -0.3 | 9.802 | 4.289 | 9.5 | -0.077 | 2 | 6.041% | -4.98 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.077 | 477 | 310 | 0 | 15.2 | 461.8 | 465.5 | 3.7 | -0.53 | 4.202 | 5.198 | 0.808 | 16.55% | 462.9 | -0.7 | 1.853 | 5.127 | 1.1 | -0.077 | 0.361 | 55.68% | -53.85 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.077 | 585.7 | 152.4 | 0 | 43.2 | 542.5 | 553.7 | 11.2 | -0.32 | 11.563 | 6.02 | 1.921 | 6.714% | 553.3 | -0.4 | 11.207 | 5.941 | 10.8 | -0.077 | 1.886 | 6.962% | -6.44 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.077 | 585.7 | 152.4 | 0 | 43.2 | 542.5 | 553.7 | 11.2 | -0.32 | 11.563 | 6.02 | 1.921 | 6.714% | 553.3 | -0.4 | 11.207 | 5.941 | 10.8 | -0.077 | 1.886 | 6.962% | -6.44 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.077 | 593.7 | 152.3 | 0 | 36.6 | 557.1 | 567.8 | 10.7 | 0.21 | 10.527 | 6.068 | 1.735 | 7.123% | 567.4 | 0.3 | 9.977 | 5.989 | 10.3 | -0.077 | 1.666 | 7.4% | -6.94 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.077 | 593.7 | 152.3 | 0 | 36.6 | 557.1 | 567.8 | 10.7 | 0.21 | 10.527 | 6.068 | 1.735 | 7.123% | 567.4 | 0.3 | 9.977 | 5.989 | 10.3 | -0.077 | 1.666 | 7.4% | -6.94 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.077 | 939.3 | 461 | 141 | 23.4 | 774.9 | 791.6 | 16.7 | 1.18 | 15.551 | 8.699 | 1.788 | 7.22% | 797.4 | 1.6 | 20.929 | 8.581 | 22.5 | -0.077 | 2 | 5.359% | -4.42 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.077 | 961 | 461 | 141 | 35.9 | 784.1 | 801.2 | 17.1 | 0.54 | 16.613 | 8.935 | 1.859 | 7.214% | 806.7 | 0.8 | 21.907 | 8.813 | 22.6 | -0.077 | 2 | 5.458% | -4.45 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.077 | 608 | 305 | 111 | 119.1 | 377.9 | 385 | 7.1 | 0.22 | 6.848 | 5.415 | 1.265 | 10.99% | 386.3 | 0.3 | 8.119 | 5.342 | 8.4 | -0.077 | 1.52 | 9.292% | -5.77 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.077 | 824 | 260 | 0 | 512.7 | 311.3 | 327.8 | 16.5 | 1.64 | 14.95 | 7.908 | 1.891 | 6.411% | 329.8 | 2.3 | 16.269 | 7.805 | 18.5 | -0.077 | 2 | 5.718% | -2.16 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.077 | 836 | 258 | 0 | 476.5 | 359.5 | 369 | 9.5 | 5.68 | 3.82 | 8.505 | 0.449 | 11.3% | 371.2 | 7.9 | 3.781 | 8.394 | 11.7 | -0.077 | 0.45 | 9.172% | -3.94 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.077 | 119 | 57 | 0 | 21.7 | 97.3 | 100.1 | 2.8 | -0.23 | 2.99 | 1.531 | 1.953 | 5.464% | 100.5 | -0.3 | 3.472 | 1.508 | 3.2 | -0.077 | 2 | 4.781% | -3.89 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.077 | 514 | 352 | 0 | 94.3 | 419.7 | 425.4 | 5.7 | -1.77 | 7.416 | 5.601 | 1.324 | 11.58% | 430.2 | -2.5 | 12.934 | 5.525 | 10.5 | -0.077 | 2 | 6.285% | -5.13 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.077 | 550 | 294.7 | 19.9 | 67.8 | 462.3 | 469.8 | 7.5 | 0.57 | 6.885 | 5.776 | 1.192 | 9.415% | 469.2 | 0.8 | 6.023 | 5.698 | 6.9 | -0.077 | 1.057 | 10.23% | -8.59 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.077 | 815 | 300 | 0 | 460.9 | 354.1 | 372.5 | 18.4 | 5.8 | 12.581 | 11.824 | 1.064 | 5.686% | 379.6 | 8.1 | 17.481 | 11.67 | 25.5 | -0.077 | 1.498 | 4.103% | -1.78 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.077 | 820 | 300 | 0 | 515.3 | 304.7 | 309.6 | 4.9 | -0.1 | 5.016 | 11.896 | 0.422 | 21.48% | 308.4 | -0.1 | 3.875 | 11.741 | 3.7 | -0.077 | 0.33 | 28.45% | -10.56 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.077 | 775 | 300 | 0 | 186.6 | 588.4 | 609.3 | 20.9 | 4.14 | 16.836 | 11.243 | 1.497 | 4.76% | 611.1 | 5.8 | 16.978 | 11.097 | 22.7 | -0.077 | 1.53 | 4.383% | -3.33 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.077 | 515 | 210 | 0 | 295.1 | 219.9 | 221.3 | 1.4 | 0.37 | 1.073 | 7.471 | 0.144 | 47.23% | 219.7 | 0.5 | -0.717 | 7.374 | -0.2 | -0.077 | 0 | -330.6% | 140.96 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.077 | 750 | 300 | 0 | 275.4 | 474.6 | 485.5 | 10.9 | -0.61 | 11.5 | 10.881 | 1.057 | 8.833% | 489.2 | -0.8 | 15.456 | 10.739 | 14.6 | -0.077 | 1.439 | 6.594% | -4.17 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.077 | 740.3 | 502.3 | 44.5 | 168.1 | 527.7 | 540 | 12.3 | -1.59 | 13.897 | 7.582 | 1.833 | 7.726% | 550.1 | -2.2 | 24.645 | 7.479 | 22.4 | -0.077 | 2 | 4.243% | -3.02 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.077 | 499 | 360 | 10 | 33.1 | 455.9 | 459.5 | 3.6 | -1.24 | 4.818 | 5.328 | 0.904 | 17.8% | 462.1 | -1.7 | 7.91 | 5.256 | 6.2 | -0.077 | 1.505 | 10.33% | -9.43 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.077 | 392 | 223 | 0 | 18.5 | 373.5 | 378.1 | 4.6 | -0.24 | 4.872 | 5.504 | 0.885 | 10.94% | 378.6 | -0.3 | 5.414 | 5.432 | 5.1 | -0.077 | 0.997 | 9.87% | -9.39 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.077 | 84 | 57 | 0 | 25.6 | 58.4 | 60.1 | 1.7 | 0.26 | 1.409 | 1.081 | 1.304 | 6.358% | 60.3 | 0.4 | 1.528 | 1.065 | 1.9 | -0.077 | 1.435 | 5.689% | -3.93 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.077 | 155 | 80 | 0 | 20.3 | 134.7 | 136.8 | 2.1 | -0.04 | 2.071 | 2.048 | 1.011 | 9.486% | 138.1 | -0.1 | 3.385 | 2.021 | 3.4 | -0.077 | 1.674 | 5.859% | -5.08 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.077 | 153 | 80 | 0 | 18.5 | 134.5 | 136.7 | 2.2 | 0.06 | 2.093 | 2.022 | 1.035 | 8.938% | 137.4 | 0.1 | 2.762 | 1.995 | 2.9 | -0.077 | 1.384 | 6.78% | -5.94 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.077 | 664 | 156 | 0 | 499.6 | 164.4 | 176 | 11.6 | 0.35 | 11.256 | 8.999 | 1.251 | 7.348% | 175.4 | 0.5 | 10.561 | 8.881 | 11 | -0.077 | 1.189 | 7.749% | -1.92 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.077 | 555 | 156 | 0 | 395.1 | 159.9 | 169.7 | 9.8 | 0.4 | 9.428 | 7.546 | 1.249 | 7.271% | 170.5 | 0.6 | 10.099 | 7.447 | 10.6 | -0.077 | 1.356 | 6.722% | -1.93 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.077 | 577 | 156 | 0 | 415.6 | 161.4 | 174.5 | 13.1 | -0.48 | 13.603 | 7.738 | 1.758 | 5.655% | 173.2 | -0.7 | 12.497 | 7.637 | 11.8 | -0.077 | 1.636 | 6.278% | -1.75 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.077 | 572 | 159 | 0 | 16.9 | 555.1 | 557.8 | 2.7 | -0.33 | 3.022 | 6.325 | 0.478 | 27.2% | 558.9 | -0.5 | 4.211 | 6.243 | 3.8 | -0.077 | 0.674 | 19.32% | -18.74 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.077 | 376 | 125 | 20 | 188.4 | 167.6 | 172.4 | 4.8 | 0 | 4.88 | 3.879 | 1.258 | 10.06% | 172.2 | 0 | 4.605 | 3.827 | 4.6 | -0.077 | 1.203 | 10.5% | -4.67 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.077 | 1138 | 379 | 152 | 551.9 | 434.1 | 452.9 | 18.8 | -0.98 | 19.819 | 10.744 | 1.845 | 7.77% | 457 | -1.4 | 24.268 | 10.598 | 22.9 | -0.077 | 2 | 6.379% | -2.43 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.082 | 56 | 30 | 0 | 26 | 30 | 31.8 | 1.8 | -0.29 | 2.084 | 0.974 | 2 | 4.268% | 34.4 | -0.4 | 4.815 | 0.954 | 4.4 | -0.081 | 2 | 1.725% | -0.93 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.082 | 597 | 220 | 0 | 48.6 | 548.4 | 552.1 | 3.7 | 3.15 | 0.571 | 11.62 | 0.049 | 22.06% | 550.7 | 4.4 | -2.098 | 11.408 | 2.3 | -0.081 | 0 | 35.05% | -32.57 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 478 | 300 | 0 | 85.3 | 392.7 | 403.8 | 11.1 | -0.42 | 11.561 | 7.052 | 1.639 | 5.888% | 402.9 | -0.6 | 10.749 | 6.919 | 10.2 | -0.081 | 1.554 | 6.329% | -5.26 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.082 | 417 | 125 | 0 | 223 | 194 | 194.8 | 0.8 | -4.89 | 5.693 | 5.649 | 1.008 | 71.27% | 192.5 | -6.8 | 5.332 | 5.546 | -1.5 | -0.081 | 0.961 | -37.55% | 17.66 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 414 | 325 | 76 | 7 | 331 | 334.3 | 3.3 | -1.12 | 4.36 | 4.987 | 0.874 | 17.15% | 334.9 | -1.6 | 5.446 | 4.893 | 3.9 | -0.081 | 1.113 | 14.34% | -11.59 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.082 | 645 | 300 | 0 | 62.4 | 582.6 | 600.7 | 18.1 | -2.12 | 20.203 | 10.67 | 1.893 | 4.872% | 601.3 | -3 | 21.613 | 10.475 | 18.7 | -0.081 | 2 | 4.658% | -4.26 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 350 | 246 | 0 | 95.6 | 254.4 | 262.2 | 7.8 | 0.63 | 7.122 | 5.164 | 1.379 | 6.136% | 263.6 | 0.9 | 8.309 | 5.066 | 9.2 | -0.081 | 1.64 | 5.139% | -3.78 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 479 | 271 | 0 | 13.2 | 465.8 | 469.6 | 3.8 | 0.12 | 3.734 | 7.067 | 0.528 | 17.23% | 467.4 | 0.2 | 1.479 | 6.933 | 1.6 | -0.081 | 0.213 | 40.43% | -39.77 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.082 | 585.7 | 152.4 | 0 | 38.9 | 546.8 | 561.9 | 15.1 | 0.85 | 14.317 | 8.04 | 1.781 | 5.303% | 560.9 | 1.2 | 12.976 | 7.893 | 14.1 | -0.081 | 1.644 | 5.61% | -5.3 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 585.7 | 152.4 | 0 | 38.9 | 546.8 | 561.9 | 15.1 | 0.85 | 14.317 | 8.04 | 1.781 | 5.303% | 560.9 | 1.2 | 12.976 | 7.893 | 14.1 | -0.081 | 1.644 | 5.61% | -5.3 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 593.7 | 152.3 | 0 | 25.9 | 567.8 | 581.3 | 13.5 | 1.81 | 11.741 | 8.088 | 1.452 | 6.012% | 577.6 | 2.5 | 7.33 | 7.94 | 9.8 | -0.081 | 0.923 | 8.181% | -7.92 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 593.7 | 152.3 | 0 | 25.9 | 567.8 | 581.3 | 13.5 | 1.81 | 11.741 | 8.088 | 1.452 | 6.012% | 577.6 | 2.5 | 7.33 | 7.94 | 9.8 | -0.081 | 0.923 | 8.181% | -7.92 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 930.6 | 461 | 141 | 37.6 | 752 | 773.1 | 21.1 | 1.98 | 19.108 | 11.65 | 1.64 | 6.029% | 780.1 | 2.8 | 25.393 | 11.43 | 28.1 | -0.081 | 2 | 4.472% | -3.66 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.082 | 243 | 150 | 21 | 63.3 | 158.7 | 163.6 | 4.9 | -0.7 | 5.64 | 3.525 | 1.6 | 6.783% | 164.4 | -1 | 6.645 | 3.461 | 5.7 | -0.081 | 1.92 | 5.76% | -3.8 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 284 | 165 | 40 | 51.7 | 192.3 | 199.4 | 7.1 | -0.25 | 7.309 | 3.6 | 2 | 5.471% | 199.7 | -0.3 | 7.742 | 3.532 | 7.4 | -0.081 | 2 | 5.185% | -3.55 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.082 | 824 | 260 | 0 | 400.5 | 423.5 | 440.6 | 17.1 | -4.85 | 22.009 | 11.209 | 1.963 | 6.587% | 442 | -6.7 | 25.243 | 11.004 | 18.5 | -0.081 | 2 | 6.015% | -3.13 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.082 | 836 | 258 | 0 | 196.6 | 639.4 | 653.6 | 14.2 | -0.49 | 14.691 | 12.249 | 1.199 | 8.048% | 653.8 | -0.7 | 15.111 | 12.025 | 14.4 | -0.081 | 1.257 | 7.839% | -6.07 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.082 | 113 | 59 | 0 | 21.7 | 91.3 | 95.7 | 4.4 | 0 | 4.422 | 1.965 | 2 | 3.516% | 95.7 | 0 | 4.471 | 1.925 | 4.4 | -0.081 | 2 | 3.473% | -2.83 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 507 | 346 | 0 | 84.6 | 422.4 | 435.5 | 13.1 | -0.3 | 13.395 | 7.48 | 1.791 | 5.291% | 436.4 | -0.4 | 14.439 | 7.339 | 14 | -0.081 | 1.968 | 4.891% | -4.12 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 547.3 | 294.7 | 15.9 | 35.8 | 495.6 | 504.9 | 9.3 | -2.38 | 11.707 | 7.84 | 1.493 | 8.046% | 503.6 | -3.3 | 11.365 | 7.692 | 8 | -0.081 | 1.478 | 9.239% | -8.46 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.082 | 750 | 300 | 0 | 19 | 731 | 744.8 | 13.8 | 0.15 | 13.676 | 14.598 | 0.937 | 7.43% | 743.4 | 0.2 | 12.228 | 14.332 | 12.4 | -0.081 | 0.853 | 8.168% | -8.05 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.082 | 820 | 300 | 0 | 319.8 | 500.2 | 502.9 | 2.7 | -3.47 | 6.14 | 15.961 | 0.385 | 41.52% | 502.5 | -4.8 | 7.062 | 15.669 | 2.3 | -0.081 | 0.451 | 48.14% | -29.71 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.082 | 775 | 300 | 0 | 42.2 | 732.8 | 750.5 | 17.7 | 2.48 | 15.15 | 15.085 | 1.004 | 5.986% | 750 | 3.5 | 13.755 | 14.809 | 17.2 | -0.081 | 0.929 | 6.084% | -5.82 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.082 | 525 | 210 | 0 | 171.4 | 353.6 | 355.4 | 1.8 | -0.93 | 2.734 | 10.219 | 0.267 | 39.88% | 356.7 | -1.3 | 4.358 | 10.032 | 3.1 | -0.081 | 0.434 | 22.87% | -15.58 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.082 | 515 | 210 | 0 | 98.2 | 416.8 | 429.5 | 12.7 | 5.6 | 7.1 | 10.024 | 0.708 | 5.544% | 434.4 | 7.8 | 9.841 | 9.841 | 17.6 | -0.081 | 1 | 3.952% | -3.23 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.082 | 750 | 300 | 0 | 62.8 | 687.2 | 695.3 | 8.1 | -0.56 | 8.651 | 14.598 | 0.593 | 12.66% | 702.9 | -0.8 | 16.509 | 14.332 | 15.7 | -0.081 | 1.152 | 6.451% | -5.98 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 650.9 | 250 | 151.2 | 44.4 | 455.3 | 469.6 | 14.3 | -6.3 | 20.619 | 7.371 | 2 | 6.223% | 471.1 | -8.8 | 24.536 | 7.232 | 15.8 | -0.081 | 2 | 5.563% | -3.94 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 522.1 | 315.6 | 45 | 12.6 | 464.5 | 469.9 | 5.4 | -1.09 | 6.492 | 7.039 | 0.922 | 13.22% | 470 | -1.5 | 6.959 | 6.906 | 5.5 | -0.081 | 1.008 | 12.82% | -11.54 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 518.6 | 344.3 | 45 | 10.3 | 463.3 | 467.9 | 4.6 | 0.39 | 4.219 | 6.988 | 0.604 | 15.41% | 475.4 | 0.5 | 11.562 | 6.856 | 12.1 | -0.081 | 1.686 | 5.788% | -5.23 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 742.2 | 479.9 | 45.1 | 205.3 | 491.8 | 510.7 | 18.9 | 1.3 | 17.637 | 10.284 | 1.715 | 5.368% | 522.1 | 1.8 | 28.501 | 10.09 | 30.3 | -0.081 | 2 | 3.308% | -2.22 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 275 | 225 | 0 | 49.8 | 225.2 | 232.9 | 7.7 | 0.59 | 7.117 | 4.057 | 1.754 | 4.885% | 233.6 | 0.8 | 7.586 | 3.981 | 8.4 | -0.081 | 1.906 | 4.423% | -3.66 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.082 | 56.1 | 22.5 | 0 | 32.8 | 23.3 | 24.9 | 1.6 | 0.02 | 1.619 | 0.975 | 1.66 | 4.81% | 28.3 | 0 | 4.953 | 0.955 | 5 | -0.081 | 2 | 1.52% | -0.63 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.082 | 382 | 223 | 0 | 38.4 | 343.6 | 351.3 | 7.7 | 0.3 | 7.386 | 7.196 | 1.026 | 6.784% | 351.7 | 0.4 | 7.689 | 7.064 | 8.1 | -0.081 | 1.089 | 6.37% | -5.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 934.4 | 322 | 0 | 39 | 895.4 | 916.2 | 20.8 | 3.99 | 16.874 | 12.978 | 1.3 | 6.141% | 922 | 5.5 | 21.093 | 12.741 | 26.6 | -0.081 | 1.656 | 4.743% | -4.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 934.4 | 322 | 0 | 39 | 895.4 | 916.2 | 20.8 | 3.99 | 16.874 | 12.978 | 1.3 | 6.141% | 922 | 5.5 | 21.093 | 12.741 | 26.6 | -0.081 | 1.656 | 4.743% | -4.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 934.4 | 322 | 0 | 39 | 895.4 | 916.2 | 20.8 | 3.99 | 16.874 | 12.978 | 1.3 | 6.141% | 922 | 5.5 | 21.093 | 12.741 | 26.6 | -0.081 | 1.656 | 4.743% | -4.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 934.4 | 322 | 0 | 39 | 895.4 | 916.2 | 20.8 | 3.99 | 16.874 | 12.978 | 1.3 | 6.141% | 922 | 5.5 | 21.093 | 12.741 | 26.6 | -0.081 | 1.656 | 4.743% | -4.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.082 | 155 | 80 | 0 | 20 | 135 | 137.8 | 2.8 | 0 | 2.848 | 2.746 | 1.037 | 7.576% | 139.6 | 0 | 4.656 | 2.696 | 4.6 | -0.081 | 1.727 | 4.555% | -4 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.082 | 153 | 80 | 0 | 19.5 | 133.5 | 137 | 3.5 | -0.14 | 3.597 | 2.712 | 1.326 | 5.982% | 138.3 | -0.2 | 4.945 | 2.662 | 4.8 | -0.081 | 1.857 | 4.309% | -3.8 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.082 | 664 | 156 | 0 | 301.2 | 362.8 | 366.3 | 3.5 | -7.03 | 10.574 | 11.153 | 0.948 | 25.94% | 362.9 | -9.8 | 9.898 | 10.949 | 0.1 | -0.081 | 0.904 | 896.7% | -495.54 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.082 | 555 | 156 | 0 | 205.3 | 349.7 | 364.6 | 14.9 | -0.58 | 15.462 | 9.344 | 1.655 | 5.093% | 365.8 | -0.8 | 16.936 | 9.173 | 16.1 | -0.081 | 1.846 | 4.655% | -2.97 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.082 | 577 | 156 | 0 | 251.9 | 325.1 | 335.9 | 10.8 | 0.29 | 10.519 | 9.596 | 1.096 | 7.304% | 335.5 | 0.4 | 9.917 | 9.421 | 10.4 | -0.081 | 1.053 | 7.493% | -4.27 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 1081 | 379 | 152 | 200.4 | 728.6 | 755.9 | 27.3 | 0.78 | 26.444 | 13.706 | 1.929 | 5.413% | 766.4 | 1.1 | 36.725 | 13.447 | 37.8 | -0.081 | 2 | 3.861% | -2.63 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.073 | 426.7 | 133.7 | 72.5 | 202.2 | 152 | 150.6 | -1.4 | -5.64 | 4.272 | 3.442 | 1.241 | -37.1% | 152.5 | -7.8 | 8.396 | 3.125 | 0.5 | -0.069 | 2 | 98.2% | -36.93 | 0.017 | 0.0578 | 5.933% | 5.163%
Hydro | NA | HYDR | -0.073 | 30 | 0 | 0 | 28.6 | 1.4 | 29.9 | 28.5 | 2.92 | 25.519 | 0.388 | 2 | 0.1291% | 29.9 | 4.1 | 24.443 | 0.354 | 28.5 | -0.069 | 2 | 0.122% | 0 | 0.017 | 0.05 | 0.2285% | 0.2528%
CombinedCycle | CC | COGN | -0.073 | 478 | 300 | 0 | 24.8 | 453.2 | 457.7 | 4.5 | -3.06 | 7.566 | 4.645 | 1.629 | 12.93% | 458.3 | -4.3 | 9.348 | 4.218 | 5.1 | -0.069 | 2 | 10.78% | -10.81 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.073 | 494 | 269 | 30 | 109 | 355 | 359.8 | 4.8 | 0 | 4.753 | 4.509 | 1.054 | 12.53% | 359.8 | 0 | 4.771 | 4.094 | 4.8 | -0.069 | 1.165 | 11.84% | -8.99 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.073 | 215 | 162 | 0 | 46.1 | 168.9 | 170.2 | 1.3 | 0.58 | 0.627 | 2.089 | 0.3 | 20.14% | 169.5 | 0.8 | -0.257 | 1.897 | 0.6 | -0.069 | 0 | 41.26% | -34.2 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.073 | 560 | 135 | 0 | 50.4 | 509.6 | 519.2 | 9.6 | 1.13 | 8.46 | 7.246 | 1.168 | 7.1% | 519.7 | 1.6 | 8.497 | 6.606 | 10.1 | -0.069 | 1.286 | 6.379% | -6.14 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.073 | 417 | 125 | 0 | 103.2 | 313.8 | 318.8 | 5 | 0.23 | 4.834 | 4.103 | 1.178 | 10.15% | 317.5 | 0.3 | 3.42 | 3.741 | 3.7 | -0.069 | 0.914 | 12.97% | -10.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.073 | 420 | 70 | 0 | 348.7 | 71.3 | 76.2 | 4.9 | 0.71 | 4.225 | 3.97 | 1.064 | 10.43% | 75.2 | 1 | 2.955 | 3.619 | 3.9 | -0.069 | 0.816 | 12.39% | -2.22 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.073 | 742 | 310 | 0 | 431 | 311 | 321.5 | 10.5 | 0.04 | 10.409 | 4.453 | 2 | 8.603% | 322.3 | 0.1 | 11.196 | 3.672 | 11.3 | -0.069 | 2 | 7.556% | -3.34 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.073 | 645 | 300 | 0 | 41.8 | 603.2 | 616.8 | 13.6 | 1.12 | 12.473 | 7.076 | 1.763 | 5.772% | 619.8 | 1.6 | 15.04 | 6.451 | 16.6 | -0.069 | 2 | 4.47% | -4.42 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.073 | 329 | 243 | 0 | 68.6 | 260.4 | 267.3 | 6.9 | 0.04 | 6.81 | 3.197 | 2 | 5.805% | 267.6 | 0.1 | 7.114 | 2.903 | 7.2 | -0.069 | 2 | 5.259% | -4.4 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.073 | 477 | 271 | 0 | 17 | 460 | 464.4 | 4.4 | 0.94 | 3.485 | 4.635 | 0.752 | 13.2% | 465.3 | 1.3 | 3.972 | 4.209 | 5.3 | -0.069 | 0.944 | 10.36% | -10.55 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.073 | 140 | 80 | 0 | 53.8 | 86.2 | 90.2 | 4 | 0.19 | 3.782 | 1.606 | 2 | 4.265% | 89.9 | 0.3 | 3.404 | 1.446 | 3.7 | -0.069 | 2 | 4.359% | -2.83 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.073 | 339 | 146 | 11 | 45.6 | 282.4 | 291.4 | 9 | 2.88 | 6.193 | 3.187 | 1.943 | 4.586% | 293.5 | 4 | 7.104 | 2.894 | 11.1 | -0.069 | 2 | 3.515% | -3.09 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.073 | 585.7 | 152.4 | 0 | 51.1 | 534.6 | 547.1 | 12.5 | 1.27 | 11.253 | 5.385 | 2 | 5.703% | 546.5 | 1.8 | 10.145 | 4.91 | 11.9 | -0.069 | 2 | 5.663% | -5.46 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.073 | 585.7 | 152.4 | 0 | 51.1 | 534.6 | 547.1 | 12.5 | 1.27 | 11.253 | 5.385 | 2 | 5.703% | 546.5 | 1.8 | 10.145 | 4.91 | 11.9 | -0.069 | 2 | 5.663% | -5.46 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.073 | 593.7 | 152.3 | 0 | 33.6 | 560.1 | 569.2 | 9.1 | 0.21 | 8.974 | 5.415 | 1.657 | 7.941% | 568.3 | 0.3 | 7.907 | 4.937 | 8.2 | -0.069 | 1.602 | 8.33% | -8.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.073 | 593.7 | 152.3 | 0 | 33.6 | 560.1 | 569.2 | 9.1 | 0.21 | 8.974 | 5.415 | 1.657 | 7.941% | 568.3 | 0.3 | 7.907 | 4.937 | 8.2 | -0.069 | 1.602 | 8.33% | -8.31 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.073 | 887.8 | 461 | 99.5 | 63.4 | 724.9 | 742.2 | 17.3 | 0.61 | 16.671 | 7.66 | 2 | 6.245% | 746.1 | 0.9 | 20.306 | 6.956 | 21.2 | -0.069 | 2 | 4.817% | -4.16 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.073 | 403 | 215 | 85 | 89.6 | 228.4 | 233.4 | 5 | 0 | 4.938 | 3.09 | 1.598 | 9.812% | 236.5 | 0 | 8.104 | 2.806 | 8.1 | -0.069 | 2 | 5.725% | -3.43 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | STM | -0.073 | 127.9 | 19.9 | 0 | 103.1 | 24.8 | 26.3 | 1.5 | -0.2 | 1.777 | 1.65 | 1.077 | 10.39% | 26 | -0.3 | 1.519 | 1.505 | 1.2 | -0.069 | 1.009 | 12.28% | -2.49 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.073 | 240 | 171 | 32 | 14.9 | 193.1 | 194.5 | 1.4 | 0.55 | 0.822 | 2.021 | 0.407 | 20.88% | 193.5 | 0.8 | -0.308 | 1.835 | 0.4 | -0.069 | 0 | 69.07% | -58.66 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.073 | 237 | 150 | 21 | 22.7 | 193.3 | 196.3 | 3 | 0.5 | 2.486 | 2.497 | 0.996 | 9.621% | 197.1 | 0.7 | 3.039 | 2.277 | 3.8 | -0.069 | 1.335 | 7.18% | -6.18 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.073 | 244 | 150 | 21 | 14 | 209 | 211.7 | 2.7 | 0.94 | 1.766 | 2.701 | 0.654 | 11.01% | 212.2 | 1.3 | 1.866 | 2.463 | 3.2 | -0.069 | 0.758 | 8.778% | -7.94 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.073 | 286 | 165 | 40 | 25.2 | 220.8 | 222 | 1.2 | -0.4 | 1.6 | 2.39 | 0.669 | 29.02% | 222.4 | -0.6 | 2.115 | 2.171 | 1.6 | -0.069 | 0.975 | 20.57% | -16.77 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.073 | 824 | 260 | 0 | 70.7 | 753.3 | 763.9 | 10.6 | -1.43 | 11.992 | 7.166 | 1.674 | 9.461% | 765.2 | -2 | 13.894 | 6.534 | 11.9 | -0.069 | 2 | 7.965% | -7.7 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.073 | 812 | 258 | 0 | 60.3 | 751.7 | 761.3 | 9.6 | -0.7 | 10.251 | 7.609 | 1.347 | 10.29% | 760.9 | -1 | 10.143 | 6.937 | 9.2 | -0.069 | 1.462 | 10.15% | -9.94 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.073 | 102 | 59 | 0 | 21.2 | 80.8 | 83.7 | 2.9 | 0 | 2.979 | 1.17 | 2 | 4.289% | 83.9 | 0 | 3.15 | 1.054 | 3.1 | -0.069 | 2 | 3.793% | -3.16 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.073 | 533.1 | 303.6 | 29.2 | 13.6 | 490.3 | 497.7 | 7.4 | -0.26 | 7.592 | 4.897 | 1.55 | 8.769% | 496 | -0.4 | 6.058 | 4.447 | 5.7 | -0.069 | 1.362 | 10.76% | -10.46 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.073 | 537.2 | 294.7 | 24.4 | 18.3 | 494.5 | 502.3 | 7.8 | -0.61 | 8.473 | 4.983 | 1.7 | 8.383% | 502.8 | -0.9 | 9.208 | 4.525 | 8.3 | -0.069 | 2 | 7.447% | -7.25 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.073 | 250 | 150 | 21 | 53.2 | 175.8 | 180.6 | 4.8 | 0.24 | 4.628 | 2.195 | 2 | 6.343% | 181.2 | 0.3 | 5.049 | 2.002 | 5.4 | -0.069 | 2 | 5.329% | -3.96 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.073 | 248 | 150 | 21 | 76.1 | 150.9 | 155.1 | 4.2 | -0.01 | 4.184 | 2.141 | 1.954 | 7.191% | 155.2 | 0 | 4.315 | 1.952 | 4.3 | -0.069 | 2 | 6.639% | -4.26 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.073 | 75 | 20 | 0 | 54.3 | 20.7 | 22 | 1.3 | 0.69 | 0.583 | 0.951 | 0.613 | 7.041% | 20.9 | 1 | -0.721 | 0.867 | 0.2 | -0.069 | 0 | 43.27% | -12.45 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.073 | 88 | 38 | 0 | 47.1 | 40.9 | 45.2 | 4.3 | 0.85 | 3.433 | 1.12 | 2 | 2.497% | 45.9 | 1.2 | 3.845 | 1.021 | 5 | -0.069 | 2 | 2.03% | -0.99 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | LIG | FOSS | -0.073 | 815 | 300 | 0 | 100.7 | 714.3 | 722.7 | 8.4 | 0.17 | 8.267 | 10.552 | 0.783 | 11.81% | 720.8 | 0.2 | 6.269 | 9.621 | 6.5 | -0.069 | 0.652 | 14.42% | -13.37 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.073 | 820 | 300 | 0 | 418.1 | 401.9 | 409 | 7.1 | 0.32 | 6.731 | 10.617 | 0.634 | 14.06% | 409.6 | 0.5 | 7.26 | 9.68 | 7.7 | -0.069 | 0.75 | 12.25% | -6.35 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.073 | 775 | 300 | 0 | 26.3 | 748.7 | 759.1 | 10.4 | 2.48 | 7.881 | 10.034 | 0.785 | 9.069% | 758.4 | 3.5 | 6.186 | 9.149 | 9.7 | -0.069 | 0.676 | 9.191% | -9.39 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.073 | 500 | 210 | 0 | 12.1 | 487.9 | 492.2 | 4.3 | 0.58 | 3.669 | 6.474 | 0.567 | 14.15% | 495.1 | 0.8 | 6.409 | 5.903 | 7.2 | -0.069 | 1.086 | 7.99% | -8.24 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.073 | 515 | 210 | 0 | 12.2 | 502.8 | 506.1 | 3.3 | -0.7 | 3.963 | 6.668 | 0.594 | 19% | 508.7 | -1 | 6.845 | 6.08 | 5.9 | -0.069 | 1.126 | 10.04% | -10.36 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.073 | 755 | 300 | 0 | 27.7 | 727.3 | 734 | 6.7 | 1.52 | 5.218 | 9.775 | 0.534 | 13.71% | 736.4 | 2.1 | 7.037 | 8.913 | 9.1 | -0.069 | 0.79 | 9.544% | -9.72 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.073 | 678 | 442 | 36 | 67.3 | 574.7 | 581.5 | 6.8 | 1.24 | 5.579 | 6.238 | 0.894 | 12.14% | 586.6 | 1.7 | 10.219 | 5.665 | 11.9 | -0.069 | 1.804 | 6.554% | -5.87 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.073 | 745.9 | 487.4 | 34.4 | 144.5 | 567 | 579.5 | 12.5 | 0.35 | 12.094 | 6.914 | 1.749 | 7.262% | 584.2 | 0.5 | 16.693 | 6.278 | 17.2 | -0.069 | 2 | 4.989% | -4.01 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.073 | 215 | 170 | 18.2 | 21.8 | 175 | 177.5 | 2.5 | -0.35 | 2.847 | 1.912 | 1.489 | 10.47% | 178.1 | -0.5 | 3.635 | 1.736 | 3.1 | -0.069 | 2 | 7.985% | -6.86 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.073 | 55.9 | 22.5 | 0 | 33.4 | 22.5 | 23.4 | 0.9 | 0.06 | 0.756 | 0.642 | 1.178 | 7.588% | 23.5 | 0.1 | 0.838 | 0.578 | 1 | -0.069 | 1.451 | 6.457% | -2.71 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.073 | 55.8 | 22.5 | 0 | 33.3 | 22.5 | 24.3 | 1.8 | -0.03 | 1.831 | 0.64 | 2 | 3.787% | 25.2 | 0 | 2.707 | 0.576 | 2.7 | -0.069 | 2 | 2.387% | -1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.073 | 78 | 57 | 0 | 19.8 | 58.2 | 59.9 | 1.7 | 0.06 | 1.658 | 0.895 | 1.852 | 5.599% | 59.7 | 0.1 | 1.428 | 0.806 | 1.5 | -0.069 | 1.772 | 5.999% | -4.7 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.073 | 527 | 93 | 0 | 399 | 128 | 127.9 | -0.1 | -3.93 | 3.891 | 2.405 | 1.618 | -641.8% | 131.3 | -5.5 | 8.778 | 1.983 | 3.3 | -0.069 | 2 | 18.38% | -4.7 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.073 | 695 | 300 | 40 | 65 | 590 | 604.1 | 14.1 | -2.59 | 16.761 | 6.365 | 2 | 5.999% | 601.5 | -3.6 | 15.121 | 5.78 | 11.5 | -0.069 | 2 | 6.952% | -6.24 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.073 | 1089 | 379 | 152 | 248.1 | 688.9 | 708.8 | 19.9 | 0.41 | 19.498 | 9.105 | 2 | 6.659% | 717.1 | 0.6 | 27.612 | 8.268 | 28.2 | -0.069 | 2 | 4.442% | -2.97 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 533 | 275 | 12 | 122.2 | 398.8 | 410.7 | 11.9 | -1.12 | 13.061 | 9.675 | 1.35 | 7.318% | 415.9 | -1.6 | 18.644 | 8.771 | 17.1 | -0.091 | 2 | 4.729% | -3.81 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 214.5 | 153.5 | 0 | 14.3 | 200.2 | 207.8 | 7.6 | -0.79 | 8.439 | 3.983 | 2 | 4.614% | 208.9 | -1.1 | 9.825 | 3.611 | 8.7 | -0.091 | 2 | 3.743% | -3.76 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.098 | 170 | 125 | 0 | 13.5 | 156.5 | 166.6 | 10.1 | 0.32 | 9.72 | 2.846 | 2 | 2.752% | 189.3 | 0.4 | 32.296 | 2.586 | 32.8 | -0.091 | 2 | 0.7869% | -0.78 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.098 | 417 | 125 | 0 | 15.1 | 401.9 | 410.9 | 9 | 0.4 | 8.648 | 8.067 | 1.072 | 7.571% | 408.8 | 0.6 | 6.379 | 7.331 | 6.9 | -0.091 | 0.87 | 9.17% | -9.51 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.098 | 245 | 160 | 18 | 39.6 | 187.4 | 192.7 | 5.3 | -0.06 | 5.305 | 4.216 | 1.258 | 7.556% | 193.2 | -0.1 | 5.875 | 3.821 | 5.8 | -0.091 | 1.537 | 6.411% | -5.27 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 657 | 475 | 20 | 42 | 595 | 606.2 | 11.2 | 0.22 | 10.991 | 11.83 | 0.929 | 9.584% | 608.3 | 0.3 | 13.014 | 10.723 | 13.3 | -0.091 | 1.214 | 7.494% | -7.3 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 531.8 | 351.3 | 0 | 66.5 | 465.3 | 479.8 | 14.5 | -0.66 | 15.195 | 9.875 | 1.539 | 5.992% | 481.3 | -0.9 | 16.947 | 8.952 | 16 | -0.091 | 1.893 | 5.043% | -4.75 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.098 | 592.6 | 152.4 | 0 | 56.7 | 535.9 | 551.6 | 15.7 | -1.39 | 17.07 | 10.217 | 1.671 | 6.167% | 550.4 | -1.9 | 16.487 | 9.285 | 14.5 | -0.091 | 1.776 | 6.2% | -6.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.098 | 592.6 | 152.4 | 0 | 56.7 | 535.9 | 551.6 | 15.7 | -1.39 | 17.07 | 10.217 | 1.671 | 6.167% | 550.4 | -1.9 | 16.487 | 9.285 | 14.5 | -0.091 | 1.776 | 6.2% | -6.03 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.098 | 574 | 285 | 88.9 | 197.9 | 287.2 | 297.9 | 10.7 | 0 | 10.731 | 9.009 | 1.191 | 8.765% | 307.4 | 0 | 20.259 | 8.167 | 20.2 | -0.091 | 2 | 4.311% | -2.32 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.098 | 235 | 150 | 21 | 44 | 170 | 175.6 | 5.6 | 0.02 | 5.64 | 4.332 | 1.302 | 6.859% | 176 | 0 | 5.979 | 3.937 | 6 | -0.091 | 1.518 | 5.945% | -4.62 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.098 | 238 | 150 | 21 | 41.8 | 175.2 | 180.7 | 5.5 | 0.03 | 5.48 | 4.466 | 1.227 | 7.073% | 181 | 0 | 5.696 | 4.059 | 5.8 | -0.091 | 1.403 | 6.228% | -4.93 | 0.017 | 0.05 | 5.933% | 5.163%
Wind | WND | WIND | -0.098 | 21.4 | 0 | 0 | 8 | 13.4 | 14.1 | 0.7 | -0.25 | 0.901 | 0.52 | 1.733 | 5.034% | 14.6 | -0.4 | 1.548 | 0.472 | 1.2 | -0.091 | 2 | 2.728% | -1.8 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.098 | 616 | 305 | 111 | 45.2 | 459.8 | 467.4 | 7.6 | 0.16 | 7.49 | 9.378 | 0.799 | 13.24% | 467.7 | 0.2 | 7.745 | 8.501 | 7.9 | -0.091 | 0.911 | 11.83% | -9.5 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.098 | 824 | 260 | 0 | 53.2 | 770.8 | 795.5 | 24.7 | -0.19 | 24.918 | 13.201 | 1.888 | 5.45% | 796.3 | -0.3 | 25.789 | 11.997 | 25.5 | -0.091 | 2 | 4.902% | -4.94 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.098 | 836 | 258 | 0 | 46.5 | 789.5 | 808.7 | 19.2 | -4.53 | 23.788 | 14.38 | 1.654 | 7.113% | 806.9 | -6.3 | 23.76 | 13.068 | 17.4 | -0.091 | 1.818 | 7.289% | -7.41 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.098 | 104 | 62 | 0 | 21.3 | 82.7 | 88.6 | 5.9 | 0 | 5.911 | 2.275 | 2 | 2.884% | 88.6 | 0 | 5.909 | 2.044 | 5.9 | -0.091 | 2 | 2.678% | -2.28 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 498 | 357 | 0 | 87.7 | 410.3 | 426.9 | 16.6 | -0.53 | 17.208 | 9.248 | 1.861 | 4.902% | 428.4 | -0.7 | 18.882 | 8.383 | 18.1 | -0.091 | 2 | 4.174% | -3.7 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 537.8 | 303.6 | 37.9 | 27 | 472.9 | 482.7 | 9.8 | -3.99 | 13.784 | 9.283 | 1.485 | 8.966% | 484.8 | -5.5 | 17.419 | 8.415 | 11.9 | -0.091 | 2 | 6.857% | -6.49 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 548.4 | 300 | 32.2 | 43 | 473.2 | 481.5 | 8.3 | -3.37 | 11.611 | 9.585 | 1.211 | 10.8% | 483.6 | -4.7 | 15.076 | 8.688 | 10.4 | -0.091 | 1.735 | 8% | -7.43 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.098 | 253 | 150 | 21 | 43.1 | 188.9 | 195 | 6.1 | 0.24 | 5.874 | 4.136 | 1.42 | 6.779% | 195 | 0.3 | 5.757 | 3.759 | 6.1 | -0.091 | 1.532 | 6.295% | -5.05 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.098 | 820 | 300 | 0 | 219.2 | 600.8 | 615.7 | 14.9 | 0.14 | 14.756 | 19.964 | 0.739 | 8.991% | 615 | 0.2 | 13.958 | 18.143 | 14.2 | -0.091 | 0.769 | 8.76% | -6.91 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.098 | 775 | 300 | 0 | 191.2 | 583.8 | 593.1 | 9.3 | -0.65 | 9.934 | 18.868 | 0.527 | 13.61% | 591.7 | -0.9 | 8.794 | 17.147 | 7.9 | -0.091 | 0.513 | 14.88% | -12.07 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.098 | 324 | 208 | 18 | 54.8 | 251.2 | 255.7 | 4.5 | 0 | 4.518 | 5.683 | 0.795 | 11.77% | 260 | 0 | 8.771 | 5.151 | 8.8 | -0.091 | 1.703 | 5.587% | -4.66 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 641.7 | 250 | 144.4 | 17.3 | 480 | 502 | 22 | 0.03 | 22.045 | 9.235 | 2 | 4.765% | 505.7 | 0 | 25.716 | 8.371 | 25.7 | -0.091 | 2 | 3.788% | -3.05 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 748.7 | 490.8 | 31.1 | 146.2 | 571.4 | 589.5 | 18.1 | -1.3 | 19.307 | 13.327 | 1.449 | 6.758% | 595.2 | -1.8 | 25.556 | 12.08 | 23.8 | -0.091 | 2 | 4.772% | -3.92 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.098 | 49.9 | 24 | 0 | 25.8 | 24.1 | 26.7 | 2.6 | 0.18 | 2.377 | 1.09 | 2 | 3.146% | 31.4 | 0.2 | 7.013 | 0.98 | 7.3 | -0.091 | 2 | 1.041% | -0.54 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.098 | 463.6 | 230 | 0 | 145.4 | 318.2 | 319.6 | 1.4 | -4.66 | 6.047 | 8.61 | 0.702 | 54.11% | 319.8 | -6.5 | 8.05 | 7.804 | 1.6 | -0.091 | 1.032 | 43.96% | -32.47 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.098 | 56.1 | 22.5 | 0 | 33.5 | 22.6 | 24.2 | 1.6 | -0.18 | 1.806 | 1.226 | 1.473 | 5.745% | 24 | -0.2 | 1.615 | 1.102 | 1.4 | -0.091 | 1.466 | 6.098% | -2.62 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.098 | 932.6 | 360 | 0 | 71.6 | 861 | 887.9 | 26.9 | -1.83 | 28.711 | 16.247 | 1.767 | 5.664% | 890.9 | -2.5 | 32.466 | 14.765 | 29.9 | -0.091 | 2 | 4.732% | -4.7 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.098 | 932.6 | 360 | 0 | 71.6 | 861 | 887.9 | 26.9 | -1.83 | 28.711 | 16.247 | 1.767 | 5.664% | 890.9 | -2.5 | 32.466 | 14.765 | 29.9 | -0.091 | 2 | 4.732% | -4.7 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.098 | 932.6 | 360 | 0 | 71.6 | 861 | 887.9 | 26.9 | -1.83 | 28.711 | 16.247 | 1.767 | 5.664% | 890.9 | -2.5 | 32.466 | 14.765 | 29.9 | -0.091 | 2 | 4.732% | -4.7 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.098 | 932.6 | 360 | 0 | 71.6 | 861 | 887.9 | 26.9 | -1.83 | 28.711 | 16.247 | 1.767 | 5.664% | 890.9 | -2.5 | 32.466 | 14.765 | 29.9 | -0.091 | 2 | 4.732% | -4.7 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.098 | 280 | 200 | 0 | 6.7 | 273.3 | 277 | 3.7 | -0.25 | 3.957 | 4.8 | 0.824 | 12.37% | 275.5 | -0.4 | 2.481 | 4.362 | 2.2 | -0.091 | 0.569 | 19.32% | -20.28 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.098 | 80 | 57 | 0 | 22.8 | 57.2 | 59.8 | 2.6 | 0.14 | 2.432 | 1.75 | 1.39 | 5.037% | 59.7 | 0.2 | 2.249 | 1.572 | 2.5 | -0.091 | 1.431 | 4.865% | -3.73 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.098 | 80 | 57 | 0 | 21.6 | 58.4 | 60.9 | 2.5 | 0.15 | 2.414 | 1.75 | 1.379 | 5.238% | 60.8 | 0.2 | 2.245 | 1.572 | 2.4 | -0.091 | 1.428 | 5.067% | -3.96 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.098 | 1088 | 379 | 152 | 232.5 | 703.5 | 735.6 | 32.1 | -1.09 | 33.226 | 17.382 | 1.911 | 5.537% | 740.5 | -1.5 | 38.555 | 15.757 | 37 | -0.091 | 2 | 4.461% | -3.1 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.074 | 576 | 220 | 0 | 349.3 | 226.7 | 232.3 | 5.6 | -0.51 | 6.054 | 7.826 | 0.774 | 12.69% | 231.7 | -0.7 | 5.687 | 7.917 | 5 | -0.075 | 0.718 | 14.41% | -5.59 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.074 | 592 | 220 | 0 | 364 | 228 | 234.1 | 6.1 | 0.14 | 5.971 | 8.044 | 0.742 | 11.97% | 233.8 | 0.2 | 5.659 | 8.137 | 5.8 | -0.075 | 0.695 | 12.76% | -4.84 | 0.017 | 0.05 | 6.284% | 5.784%
Wind | WND | WIND | -0.074 | 140.5 | 0 | 0 | 11.7 | 128.8 | 129.9 | 1.1 | -1.19 | 2.31 | 1.91 | 1.21 | 15.78% | 133 | -1.6 | 5.914 | 1.932 | 4.2 | -0.075 | 2 | 4.188% | -3.78 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.074 | 235 | 162 | 10 | 52.8 | 172.2 | 175.2 | 3 | 0 | 2.907 | 2.285 | 1.272 | 9.671% | 176 | 0 | 3.757 | 2.313 | 3.8 | -0.075 | 1.624 | 7.738% | -5.58 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 478 | 300 | 0 | 170.6 | 307.4 | 314.6 | 7.2 | -0.04 | 7.189 | 4.855 | 1.481 | 8.192% | 317.3 | -0.1 | 9.941 | 4.914 | 9.9 | -0.075 | 2 | 6.038% | -3.83 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 289 | 95 | 67 | 126.9 | 95.1 | 100.8 | 5.7 | -0.06 | 5.722 | 2.255 | 2 | 6.258% | 100.7 | -0.1 | 5.639 | 2.282 | 5.6 | -0.075 | 2 | 6.456% | -2.09 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 213 | 152 | 0 | 59 | 154 | 159 | 5 | -0.34 | 5.403 | 2.163 | 2 | 5.26% | 160.3 | -0.5 | 6.749 | 2.19 | 6.3 | -0.075 | 2 | 4.231% | -3.01 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.074 | 560 | 135 | 0 | 408.6 | 151.4 | 160 | 8.6 | -0.04 | 8.627 | 5.707 | 1.512 | 8.034% | 161.9 | -0.1 | 10.517 | 5.773 | 10.5 | -0.075 | 1.822 | 6.669% | -1.78 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 420 | 125 | 0 | 275.7 | 144.3 | 143.9 | -0.4 | -4.78 | 4.457 | 3.972 | 1.122 | -129.6% | 143.2 | -6.7 | 5.584 | 4.018 | -1.1 | -0.075 | 1.39 | -47.75% | 16.15 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 417 | 125 | 0 | 276 | 141 | 144.2 | 3.2 | -0.41 | 3.671 | 3.943 | 0.931 | 16.08% | 142.6 | -0.6 | 2.213 | 3.988 | 1.6 | -0.075 | 0.555 | 32.6% | -10.85 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 64 | 12 | 35 | 13.6 | 15.4 | 17.4 | 2 | 0.35 | 1.69 | 0.295 | 2 | 3.961% | 16.3 | 0.5 | 0.407 | 0.298 | 0.9 | -0.075 | 1.367 | 8.92% | -2.08 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.074 | 58.1 | 0 | 0 | 15.6 | 42.5 | 43.2 | 0.7 | 0.5 | 0.255 | 0.789 | 0.323 | 10.28% | 43.5 | 0.7 | 0.376 | 0.799 | 1 | -0.075 | 0.471 | 7.291% | -5.21 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.074 | 58.1 | 0 | 0 | 8.7 | 49.4 | 50.3 | 0.9 | 0.56 | 0.27 | 0.789 | 0.342 | 7.993% | 50.4 | 0.8 | 0.143 | 0.799 | 1 | -0.075 | 0.179 | 7.291% | -6.06 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.074 | 456 | 340 | 34 | 41.1 | 380.9 | 389.5 | 8.6 | -0.52 | 9.15 | 4.286 | 2 | 6.543% | 388.2 | -0.7 | 8.026 | 4.338 | 7.3 | -0.075 | 1.85 | 7.812% | -6.43 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 993 | 472 | 273 | 226.3 | 493.7 | 503.4 | 9.7 | 1.53 | 8.1 | 7.313 | 1.108 | 12.63% | 505 | 2.1 | 9.137 | 7.401 | 11.3 | -0.075 | 1.235 | 10.99% | -5.39 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 229 | 156 | 0 | 70.4 | 158.6 | 160.3 | 1.7 | 0.18 | 1.603 | 2.326 | 0.689 | 16.63% | 159.2 | 0.2 | 0.397 | 2.354 | 0.6 | -0.075 | 0.168 | 47.76% | -32.55 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.074 | 592.6 | 152.4 | 0 | 377.5 | 215.1 | 222.2 | 7.1 | -2.05 | 9.121 | 5.655 | 1.613 | 10.3% | 225.7 | -2.8 | 13.419 | 5.72 | 10.6 | -0.075 | 2 | 6.991% | -2.5 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 592.6 | 152.4 | 0 | 377.5 | 215.1 | 222.2 | 7.1 | -2.05 | 9.121 | 5.655 | 1.613 | 10.3% | 225.7 | -2.8 | 13.419 | 5.72 | 10.6 | -0.075 | 2 | 6.991% | -2.5 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 424.7 | 180.3 | 0 | 225.6 | 199.1 | 207.5 | 8.4 | 0.06 | 8.298 | 4.977 | 1.667 | 6.239% | 208.2 | 0.1 | 8.996 | 5.035 | 9.1 | -0.075 | 1.787 | 5.837% | -2.7 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 282 | 175 | 47.5 | 58.8 | 175.7 | 180.2 | 4.5 | 0 | 4.432 | 2.382 | 1.861 | 7.735% | 180.8 | 0 | 5.065 | 2.41 | 5.1 | -0.075 | 2 | 6.917% | -4.24 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.074 | 104.3 | 0 | 0 | 25.7 | 78.6 | 79.5 | 0.9 | 0 | 0.885 | 1.417 | 0.624 | 14.32% | 79.9 | 0 | 1.35 | 1.434 | 1.3 | -0.075 | 0.942 | 10.05% | -7.44 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.074 | 97.1 | 0 | 0 | 22.7 | 74.4 | 75.2 | 0.8 | 0.28 | 0.513 | 1.319 | 0.389 | 15% | 75.7 | 0.4 | 0.913 | 1.335 | 1.3 | -0.075 | 0.684 | 9.358% | -7.04 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | LIG | FOSS | -0.074 | 777 | 259 | 0 | 515.8 | 261.2 | 277.3 | 16.1 | -0.4 | 16.462 | 6.778 | 2 | 5.954% | 278.1 | -0.6 | 17.461 | 6.857 | 16.9 | -0.075 | 2 | 5.749% | -1.9 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.074 | 836 | 258 | 0 | 574.7 | 261.3 | 277.2 | 15.9 | 1.49 | 14.476 | 7.447 | 1.944 | 6.486% | 278.8 | 2.1 | 15.473 | 7.533 | 17.5 | -0.075 | 2 | 5.973% | -1.84 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.074 | 450 | 220 | 0 | 166.4 | 283.6 | 285.6 | 2 | -2.09 | 4.086 | 6.114 | 0.668 | 27.76% | 284.7 | -2.9 | 3.968 | 6.185 | 1.1 | -0.075 | 0.642 | 51.16% | -31.77 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.074 | 450 | 220 | 0 | 163.5 | 286.5 | 286 | -0.5 | -4.23 | 3.718 | 6.114 | 0.608 | -111.1% | 285.1 | -5.9 | 4.434 | 6.185 | -1.4 | -0.075 | 0.717 | -40.2% | 25.22 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.074 | 450 | 230 | 0 | 181.6 | 268.4 | 273.5 | 5.1 | -3.58 | 8.632 | 6.114 | 1.412 | 10.89% | 275 | -5 | 11.568 | 6.185 | 6.6 | -0.075 | 1.87 | 8.527% | -5.01 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.074 | 515 | 485 | 0 | 29.6 | 485.4 | 489.8 | 4.4 | 0.02 | 4.39 | 6.997 | 0.627 | 14.44% | 495.3 | 0 | 9.844 | 7.078 | 9.9 | -0.075 | 1.391 | 6.505% | -6.04 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.074 | 510 | 210 | 0 | 148.9 | 361.1 | 365.4 | 4.3 | -1 | 5.213 | 6.929 | 0.752 | 14.63% | 367.7 | -1.4 | 7.9 | 7.009 | 6.6 | -0.075 | 1.127 | 9.663% | -6.74 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 726.5 | 451.7 | 67.9 | 202.9 | 455.7 | 466.9 | 11.2 | -6.73 | 17.905 | 6.689 | 2 | 8.003% | 478.2 | -9.4 | 31.845 | 6.77 | 22.5 | -0.075 | 2 | 4.037% | -2.5 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.074 | 392.8 | 190 | 7.5 | 143.8 | 241.5 | 246.8 | 5.3 | -0.24 | 5.512 | 3.913 | 1.408 | 9.146% | 250.1 | -0.3 | 8.886 | 3.961 | 8.6 | -0.075 | 2 | 5.713% | -3.46 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.074 | 932.6 | 360 | 0 | 563.8 | 368.8 | 383.4 | 14.6 | -0.34 | 15.028 | 5.642 | 2 | 7.88% | 385.7 | -0.5 | 17.445 | 5.707 | 16.9 | -0.075 | 2 | 6.9% | -2.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 932.6 | 360 | 0 | 563.8 | 368.8 | 383.4 | 14.6 | -0.34 | 15.028 | 5.642 | 2 | 7.88% | 385.7 | -0.5 | 17.445 | 5.707 | 16.9 | -0.075 | 2 | 6.9% | -2.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 932.6 | 360 | 0 | 563.8 | 368.8 | 383.4 | 14.6 | -0.34 | 15.028 | 5.642 | 2 | 7.88% | 385.7 | -0.5 | 17.445 | 5.707 | 16.9 | -0.075 | 2 | 6.9% | -2.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.074 | 932.6 | 360 | 0 | 563.8 | 368.8 | 383.4 | 14.6 | -0.34 | 15.028 | 5.642 | 2 | 7.88% | 385.7 | -0.5 | 17.445 | 5.707 | 16.9 | -0.075 | 2 | 6.9% | -2.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.074 | 575 | 295 | 0 | 54.9 | 520.1 | 524.9 | 4.8 | 1.4 | 3.432 | 7.813 | 0.439 | 14.78% | 527.6 | 1.9 | 5.516 | 7.903 | 7.5 | -0.075 | 0.698 | 9.587% | -8.55 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.074 | 80 | 62 | 0 | 17.7 | 62.3 | 64.1 | 1.8 | 0.01 | 1.787 | 0.96 | 1.861 | 5.497% | 64.1 | 0 | 1.753 | 0.973 | 1.8 | -0.075 | 1.803 | 5.571% | -4.25 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.074 | 155 | 80 | 0 | 20.1 | 134.9 | 136.7 | 1.8 | -0.06 | 1.931 | 1.918 | 1.007 | 10.64% | 138.2 | -0.1 | 3.385 | 1.94 | 3.3 | -0.075 | 1.745 | 5.88% | -5.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.074 | 469 | 156 | 0 | 160.3 | 308.7 | 313.6 | 4.9 | 1.62 | 3.262 | 5.623 | 0.58 | 11.81% | 318.8 | 2.3 | 7.823 | 5.688 | 10.1 | -0.075 | 1.375 | 5.807% | -3.77 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.074 | 555 | 156 | 0 | 251.8 | 303.2 | 316.4 | 13.2 | 5.69 | 7.491 | 6.655 | 1.126 | 5.188% | 318 | 7.9 | 6.862 | 6.732 | 14.8 | -0.075 | 1.019 | 4.689% | -2.52 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.074 | 577 | 156 | 0 | 272.5 | 304.5 | 321.1 | 16.6 | 7.72 | 8.916 | 6.756 | 1.32 | 4.289% | 325.4 | 10.7 | 10.168 | 6.834 | 20.9 | -0.075 | 1.488 | 3.452% | -1.8 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.074 | 1082 | 379 | 152 | 543.7 | 386.3 | 402.6 | 16.3 | -2.02 | 18.311 | 9.446 | 1.939 | 8.189% | 411.5 | -2.8 | 27.949 | 9.56 | 25.2 | -0.075 | 2 | 5.368% | -1.89 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.121 | 478 | 300 | 0 | 112.4 | 365.6 | 383.3 | 17.7 | 1.15 | 16.552 | 12.441 | 1.33 | 5.448% | 381.8 | 1.6 | 14.594 | 11.931 | 16.2 | -0.117 | 1.223 | 5.755% | -4.55 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.121 | 301 | 95 | 88.8 | 117.1 | 95.1 | 115.9 | 20.8 | 0 | 20.816 | 5.523 | 2 | 2.92% | 117.3 | 0 | 22.229 | 5.297 | 22.2 | -0.117 | 2 | 2.645% | -0.86 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.121 | 219 | 150 | 0 | 68.8 | 150.2 | 164.7 | 14.5 | -0.75 | 15.202 | 5.7 | 2 | 3.048% | 168 | -1 | 18.787 | 5.466 | 17.8 | -0.117 | 2 | 2.401% | -1.7 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.121 | 560 | 135 | 0 | 348.2 | 211.8 | 225 | 13.2 | -0.03 | 13.217 | 14.229 | 0.929 | 8.558% | 225.9 | 0 | 14.187 | 13.657 | 14.1 | -0.117 | 1.039 | 7.747% | -3.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.121 | 670 | 300 | 0 | 231.1 | 438.9 | 461.4 | 22.5 | 3.01 | 19.518 | 16.344 | 1.194 | 6.006% | 465.2 | 4.2 | 22.14 | 15.686 | 26.3 | -0.117 | 1.411 | 4.969% | -3.36 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.121 | 420 | 125 | 0 | 274.7 | 145.3 | 154.7 | 9.4 | 2.73 | 6.633 | 9.847 | 0.674 | 9.014% | 155.7 | 3.8 | 6.616 | 9.451 | 10.4 | -0.117 | 0.7 | 7.878% | -2.81 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.121 | 58 | 12 | 35 | 8.2 | 14.8 | 19.3 | 4.5 | -0.3 | 4.787 | 0.599 | 2 | 2.606% | 16.6 | -0.4 | 2.196 | 0.574 | 1.8 | -0.117 | 2 | 6.299% | -1.64 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.121 | 645 | 300 | 0 | 259.5 | 385.5 | 413.5 | 28 | -2.71 | 30.667 | 19.194 | 1.598 | 4.647% | 404.8 | -3.8 | 23.048 | 18.422 | 19.3 | -0.117 | 1.251 | 6.518% | -4.03 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.121 | 650 | 496 | 37 | 78.7 | 534.3 | 561.3 | 27 | 0.54 | 26.411 | 15.954 | 1.655 | 4.856% | 565.9 | 0.7 | 30.798 | 15.301 | 31.6 | -0.117 | 2 | 4.012% | -3.41 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.121 | 105 | 12 | 0 | 92.6 | 12.4 | 16.1 | 3.7 | 0.22 | 3.44 | 3.519 | 0.977 | 5.731% | 15.7 | 0.3 | 2.908 | 3.378 | 3.3 | -0.117 | 0.861 | 6.213% | -0.75 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.121 | 592.6 | 152.4 | 0 | 63.1 | 529.5 | 553.7 | 24.2 | -0.64 | 24.858 | 14.166 | 1.755 | 4.94% | 549.9 | -0.9 | 21.32 | 13.597 | 20.4 | -0.117 | 1.568 | 5.666% | -5.23 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.121 | 592.6 | 152.4 | 0 | 63.1 | 529.5 | 553.7 | 24.2 | -0.64 | 24.858 | 14.166 | 1.755 | 4.94% | 549.9 | -0.9 | 21.32 | 13.597 | 20.4 | -0.117 | 1.568 | 5.666% | -5.23 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.121 | 424.7 | 180.3 | 0 | 37.1 | 387.6 | 406.4 | 18.8 | 0.01 | 18.864 | 14.389 | 1.311 | 4.557% | 405.5 | 0 | 17.942 | 13.81 | 17.9 | -0.117 | 1.299 | 4.628% | -4.37 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.121 | 927.9 | 461 | 141 | 56.4 | 730.5 | 761.5 | 31 | -1.13 | 32.071 | 20.48 | 1.566 | 6.037% | 775.1 | -1.6 | 46.119 | 19.641 | 44.6 | -0.117 | 2 | 4.058% | -3.3 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.121 | 927.8 | 461 | 141 | 43.9 | 742.9 | 770.5 | 27.6 | -1.06 | 28.7 | 20.477 | 1.402 | 6.78% | 776.7 | -1.5 | 35.301 | 19.638 | 33.8 | -0.117 | 1.798 | 5.354% | -4.43 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.121 | 287 | 150 | 39.9 | 71.4 | 175.7 | 184.1 | 8.4 | -0.6 | 8.954 | 6.431 | 1.392 | 6.894% | 184.9 | -0.8 | 9.948 | 6.167 | 9.2 | -0.117 | 1.613 | 6.086% | -3.85 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.121 | 185.6 | 0 | 40 | 86.3 | 59.3 | 77.8 | 18.5 | -0.53 | 19.025 | 3.789 | 2 | 2.025% | 83.3 | -0.7 | 24.768 | 3.634 | 24 | -0.117 | 2 | 1.509% | -0.5 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.121 | 534.1 | 303.6 | 58.4 | 67.2 | 408.5 | 425.5 | 17 | -0.68 | 17.722 | 12.381 | 1.431 | 6.338% | 423.6 | -1 | 16.129 | 11.874 | 15.1 | -0.117 | 1.358 | 6.899% | -5.45 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.121 | 531.9 | 300 | 47.3 | 76.3 | 408.3 | 425.7 | 17.4 | -0.42 | 17.847 | 12.612 | 1.415 | 6.166% | 423.9 | -0.6 | 16.208 | 12.096 | 15.6 | -0.117 | 1.34 | 6.651% | -5.28 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.121 | 815 | 300 | 0 | 513.5 | 301.5 | 327.7 | 26.2 | -0.29 | 26.483 | 27.612 | 0.959 | 6.274% | 326.1 | -0.4 | 25.031 | 26.501 | 24.6 | -0.117 | 0.945 | 6.462% | -2.47 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.121 | 825 | 300 | 0 | 521.5 | 303.5 | 326 | 22.5 | -0.63 | 23.094 | 27.951 | 0.826 | 7.396% | 324.2 | -0.9 | 21.548 | 26.827 | 20.7 | -0.117 | 0.803 | 7.773% | -2.96 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.121 | 775 | 300 | 0 | 472.8 | 302.2 | 326.8 | 24.6 | -0.97 | 25.576 | 26.257 | 0.974 | 6.354% | 324.1 | -1.4 | 23.229 | 25.201 | 21.9 | -0.117 | 0.922 | 6.902% | -2.78 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.121 | 334 | 213 | 23 | 70.5 | 240.5 | 247.7 | 7.2 | -1.24 | 8.381 | 8.094 | 1.035 | 9.359% | 251.2 | -1.7 | 12.41 | 7.763 | 10.7 | -0.117 | 1.599 | 6.09% | -4.53 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.121 | 647.1 | 250 | 153.3 | 241.7 | 252.1 | 279.7 | 27.6 | -0.2 | 27.763 | 12.85 | 2 | 4.729% | 285.2 | -0.3 | 33.391 | 12.324 | 33.1 | -0.117 | 2 | 3.813% | -1.54 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.121 | 745 | 475.3 | 46.4 | 194.3 | 504.3 | 534.2 | 29.9 | 4.66 | 25.291 | 18.182 | 1.391 | 5.026% | 543 | 6.5 | 32.228 | 17.438 | 38.7 | -0.117 | 1.848 | 3.755% | -2.63 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.121 | 399.4 | 210 | 9 | 172.4 | 218 | 239.3 | 21.3 | 1.59 | 19.744 | 10.161 | 1.943 | 3.783% | 239.6 | 2.2 | 19.426 | 9.745 | 21.6 | -0.117 | 1.993 | 3.607% | -2.03 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.121 | 289.2 | 118 | 65 | 46.1 | 178.1 | 185.7 | 7.6 | 2.14 | 5.446 | 5.835 | 0.933 | 7.678% | 185.8 | 3 | 4.742 | 5.596 | 7.7 | -0.117 | 0.847 | 7.328% | -4.66 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.121 | 932.6 | 360 | 0 | 132.4 | 800.2 | 849.5 | 49.3 | -2.93 | 52.194 | 22.785 | 2 | 3.815% | 848.2 | -4.1 | 52.055 | 21.869 | 48 | -0.117 | 2 | 3.789% | -3.36 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.121 | 932.6 | 360 | 0 | 132.4 | 800.2 | 849.5 | 49.3 | -2.93 | 52.194 | 22.785 | 2 | 3.815% | 848.2 | -4.1 | 52.055 | 21.869 | 48 | -0.117 | 2 | 3.789% | -3.36 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.121 | 932.6 | 360 | 0 | 132.4 | 800.2 | 849.5 | 49.3 | -2.93 | 52.194 | 22.785 | 2 | 3.815% | 848.2 | -4.1 | 52.055 | 21.869 | 48 | -0.117 | 2 | 3.789% | -3.36 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.121 | 932.6 | 360 | 0 | 132.4 | 800.2 | 849.5 | 49.3 | -2.93 | 52.194 | 22.785 | 2 | 3.815% | 848.2 | -4.1 | 52.055 | 21.869 | 48 | -0.117 | 2 | 3.789% | -3.36 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.121 | 81 | 62 | 0 | 18.3 | 62.7 | 65.7 | 3 | -0.27 | 3.203 | 2.48 | 1.292 | 5.454% | 65.3 | -0.4 | 2.906 | 2.37 | 2.6 | -0.117 | 1.226 | 6.086% | -4.85 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.121 | 664 | 155 | 0 | 270.9 | 393.1 | 416.3 | 23.2 | -1.56 | 24.783 | 18.984 | 1.305 | 5.773% | 414.4 | -2.2 | 23.449 | 18.22 | 21.3 | -0.117 | 1.287 | 6.08% | -3.72 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.121 | 555 | 156 | 0 | 174.5 | 380.5 | 396.4 | 15.9 | -1.47 | 17.315 | 16.037 | 1.08 | 7.041% | 396.7 | -2 | 18.254 | 15.392 | 16.2 | -0.117 | 1.186 | 6.682% | -4.73 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.121 | 577 | 159 | 0 | 168.4 | 408.6 | 426 | 17.4 | -0.75 | 18.214 | 15.962 | 1.141 | 6.689% | 426.2 | -1.1 | 18.713 | 15.32 | 17.6 | -0.117 | 1.221 | 6.395% | -4.68 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.121 | 547 | 159 | 0 | 104 | 443 | 458.9 | 15.9 | -0.24 | 16.14 | 14.893 | 1.084 | 6.94% | 457 | -0.3 | 14.397 | 14.294 | 14 | -0.117 | 1.007 | 7.621% | -6.38 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.121 | 1090 | 379 | 152 | 146.5 | 791.5 | 834.4 | 42.9 | 5.1 | 37.793 | 24.413 | 1.548 | 5.125% | 831.9 | 7.1 | 33.287 | 23.413 | 40.4 | -0.117 | 1.422 | 5.262% | -3.95 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.039 | 666.5 | 253 | 145.5 | 265.2 | 255.8 | 270.7 | 14.9 | 0.59 | 14.331 | 3.218 | 2 | 2.909% | 273.1 | 0.8 | 16.502 | 3.034 | 17.3 | -0.037 | 2 | 2.377% | -0.96 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.039 | 553.7 | 275 | 12 | 108.1 | 433.6 | 439.7 | 6.1 | -2.07 | 8.151 | 3.345 | 2 | 5.905% | 441.6 | -2.9 | 10.859 | 3.154 | 8 | -0.037 | 2 | 4.272% | -3.52 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.039 | 233 | 150 | 0 | 47 | 186 | 188.6 | 2.6 | 0.2 | 2.449 | 1.439 | 1.702 | 5.836% | 188 | 0.3 | 1.782 | 1.357 | 2 | -0.037 | 1.314 | 7.198% | -6.03 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.039 | 255.5 | 153.5 | 0 | 41.9 | 213.6 | 214.1 | 0.5 | 0.38 | 0.142 | 1.578 | 0.09 | 33.27% | 214.6 | 0.5 | 0.498 | 1.488 | 1 | -0.037 | 0.335 | 15.78% | -13.86 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.039 | 560 | 135 | 0 | 236.8 | 323.2 | 330 | 6.8 | -0.05 | 6.826 | 3.568 | 1.913 | 5.357% | 329.5 | -0.1 | 6.378 | 3.379 | 6.3 | -0.037 | 1.887 | 5.486% | -3.33 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.039 | 670 | 300 | 0 | 115.4 | 554.6 | 563.6 | 9 | 0.17 | 8.82 | 4.552 | 1.938 | 4.842% | 565.7 | 0.2 | 10.87 | 4.311 | 11.1 | -0.037 | 2 | 3.725% | -3.25 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.039 | 1164 | 420 | 165.8 | 169.8 | 828.4 | 854.3 | 25.9 | 7.33 | 18.603 | 6.164 | 2 | 2.922% | 855.9 | 10.2 | 17.327 | 5.812 | 27.5 | -0.037 | 2 | 2.611% | -1.96 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.039 | 645 | 300 | 0 | 344.5 | 300.5 | 310.7 | 10.2 | -0.53 | 10.778 | 4.793 | 2 | 4.113% | 311.6 | -0.7 | 11.839 | 4.539 | 11.1 | -0.037 | 2 | 3.586% | -1.76 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.039 | 358 | 256 | 0 | 61.4 | 296.6 | 297.9 | 1.3 | -0.07 | 1.392 | 2.211 | 0.63 | 17.92% | 299.7 | -0.1 | 3.265 | 2.085 | 3.1 | -0.037 | 1.566 | 7.131% | -6.21 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.039 | 105 | 12 | 0 | 60.6 | 44.4 | 43.7 | -0.7 | -1.27 | 0.519 | 0.866 | 0.599 | -9.79% | 43 | -1.8 | 0.403 | 0.82 | -1.4 | -0.037 | 0.491 | -4.645% | 2.04 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.039 | 497 | 271 | 0 | 148 | 349 | 354.5 | 5.5 | 2.42 | 3.156 | 3.069 | 1.028 | 5.879% | 353.1 | 3.4 | 0.762 | 2.894 | 4.1 | -0.037 | 0.263 | 7.482% | -5.53 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.039 | 162 | 80 | 0 | 22.3 | 139.7 | 143 | 3.3 | -0.3 | 3.58 | 1.187 | 2 | 3.199% | 142.9 | -0.4 | 3.573 | 1.114 | 3.2 | -0.037 | 2 | 3.131% | -2.83 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.039 | 361 | 159 | 11 | 16.5 | 333.5 | 337.3 | 3.8 | 0.08 | 3.678 | 2.161 | 1.702 | 6.182% | 337.4 | 0.1 | 3.758 | 2.038 | 3.9 | -0.037 | 1.844 | 5.715% | -5.55 | 0.017 | 0.0578 | 5.933% | 5.163%
Hydro | WAT | HYDR | -0.039 | 9.5 | 4 | 0 | 5 | 4.5 | 4.5 | 0 | 0.02 | 0.007 | 0.027 | 0.253 | 0% | 4.7 | 0 | 0.169 | 0.022 | 0.2 | -0.037 | 2 | 3.212% | -1.18 | 0.034 | 0.05 | 0.2285% | 0.2528%
Thermal | SUB | FOSS | -0.039 | 592.6 | 152.4 | 0 | 67.6 | 525 | 525.7 | 0.7 | -1.27 | 1.937 | 3.619 | 0.535 | 55.07% | 523.4 | -1.8 | 0.166 | 3.427 | -1.6 | -0.037 | 0.049 | -22.86% | 21.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.039 | 592.6 | 152.4 | 0 | 67.6 | 525 | 525.7 | 0.7 | -1.27 | 1.937 | 3.619 | 0.535 | 55.07% | 523.4 | -1.8 | 0.166 | 3.427 | -1.6 | -0.037 | 0.049 | -22.86% | 21.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.039 | 599.7 | 152.3 | 0 | 29.8 | 569.9 | 574.2 | 4.3 | -0.22 | 4.478 | 3.585 | 1.249 | 9.072% | 572.4 | -0.3 | 2.802 | 3.395 | 2.5 | -0.037 | 0.825 | 14.8% | -14.81 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.039 | 599.7 | 152.3 | 0 | 29.8 | 569.9 | 574.2 | 4.3 | -0.22 | 4.478 | 3.585 | 1.249 | 9.072% | 572.4 | -0.3 | 2.802 | 3.395 | 2.5 | -0.037 | 0.825 | 14.8% | -14.81 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.039 | 251 | 150 | 21 | 6.4 | 223.6 | 226.8 | 3.2 | -0.16 | 3.314 | 1.908 | 1.737 | 5.107% | 226.6 | -0.2 | 3.179 | 1.807 | 3 | -0.037 | 1.759 | 5.169% | -4.84 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.039 | 255 | 150 | 21 | 33.8 | 200.2 | 203.3 | 3.1 | -0.21 | 3.266 | 1.811 | 1.803 | 5.356% | 203.6 | -0.3 | 3.732 | 1.715 | 3.4 | -0.037 | 2 | 4.633% | -3.82 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.039 | 824 | 259 | 0 | 108.4 | 715.6 | 723.1 | 7.5 | 0.23 | 7.253 | 4.825 | 1.503 | 7.145% | 721.7 | 0.3 | 5.814 | 4.569 | 6.1 | -0.037 | 1.272 | 8.335% | -7.62 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.039 | 118 | 68 | 0 | 21.4 | 96.6 | 98.5 | 1.9 | 0.23 | 1.712 | 0.865 | 1.981 | 4.052% | 98.5 | 0.3 | 1.558 | 0.811 | 1.9 | -0.037 | 1.92 | 3.845% | -3.29 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.039 | 79 | 30 | 0 | 48.8 | 30.2 | 31.1 | 0.9 | 0.08 | 0.795 | 0.579 | 1.373 | 5.737% | 31.4 | 0.1 | 1.063 | 0.543 | 1.2 | -0.037 | 1.956 | 4.083% | -1.61 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.039 | 700 | 300 | 0 | 26.1 | 673.9 | 679 | 5.1 | -0.82 | 5.949 | 5.947 | 1 | 8.927% | 677.8 | -1.1 | 5.032 | 5.632 | 3.9 | -0.037 | 0.893 | 11.08% | -11.22 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.039 | 743 | 483 | 39 | 101.9 | 602.1 | 615 | 12.9 | 5.31 | 7.53 | 4.347 | 1.732 | 3.746% | 621.4 | 7.4 | 11.882 | 4.099 | 19.3 | -0.037 | 2 | 2.375% | -2.03 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.039 | 747 | 486 | 33.2 | 137.8 | 576 | 587.1 | 11.1 | 0.06 | 11.074 | 4.408 | 2 | 4.377% | 589.3 | 0.1 | 13.232 | 4.156 | 13.3 | -0.037 | 2 | 3.466% | -2.81 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.039 | 348.4 | 227.5 | 15.4 | 62.5 | 270.5 | 278.2 | 7.7 | -0.71 | 8.399 | 2.056 | 2 | 2.945% | 282.4 | -1 | 12.864 | 1.939 | 11.9 | -0.037 | 2 | 1.808% | -1.48 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.039 | 75 | 41 | 0 | 33.3 | 41.7 | 43.3 | 1.6 | -0.01 | 1.601 | 0.55 | 2 | 3.065% | 43.2 | 0 | 1.536 | 0.516 | 1.5 | -0.037 | 2 | 3.102% | -1.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.039 | 74 | 41 | 0 | 32.9 | 41.1 | 42.9 | 1.8 | -0.03 | 1.801 | 0.542 | 2 | 2.688% | 43.1 | 0 | 2.017 | 0.509 | 2 | -0.037 | 2 | 2.296% | -1.32 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.039 | 75 | 41 | 0 | 33.5 | 41.5 | 42.8 | 1.3 | 0.03 | 1.313 | 0.55 | 2 | 3.772% | 43 | 0 | 1.521 | 0.516 | 1.5 | -0.037 | 2 | 3.102% | -1.78 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.039 | 540.5 | 230 | 1.3 | 189.4 | 349.8 | 360.7 | 10.9 | 0.53 | 10.399 | 3.33 | 2 | 3.226% | 373.4 | 0.7 | 22.854 | 3.14 | 23.6 | -0.037 | 2 | 1.414% | -0.96 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.039 | 168 | 75 | 0 | 75.5 | 92.5 | 102.6 | 10.1 | 1.27 | 8.759 | 1.037 | 2 | 1.084% | 103.9 | 1.8 | 9.637 | 0.978 | 11.4 | -0.037 | 2 | 0.9113% | -0.52 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.039 | 56.2 | 22.5 | 0 | 27.9 | 28.3 | 28.9 | 0.6 | -0.36 | 0.972 | 0.412 | 2 | 6.136% | 29.3 | -0.5 | 1.494 | 0.386 | 1 | -0.037 | 2 | 3.494% | -1.81 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.039 | 56.1 | 22.5 | 0 | 27.4 | 28.7 | 28.6 | -0.1 | -0.15 | 0.008 | 0.411 | 0.019 | -36.75% | 28.4 | -0.2 | -0.139 | 0.386 | -0.3 | -0.037 | 0 | -11.63% | 6.12 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.039 | 764 | 420 | 0 | 213.9 | 550.1 | 564.1 | 14 | 0.41 | 13.495 | 4.718 | 2 | 3.549% | 562.2 | 0.6 | 11.441 | 4.449 | 12.1 | -0.037 | 2 | 3.896% | -2.95 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.039 | 293 | 118 | 65 | 39.6 | 188.4 | 190.9 | 2.5 | -0.26 | 2.749 | 1.408 | 1.952 | 7.629% | 190.9 | -0.4 | 2.829 | 1.328 | 2.5 | -0.037 | 2 | 7.239% | -4.89 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.039 | 75 | 60 | 0 | 12.7 | 62.3 | 62.9 | 0.6 | 0 | 0.568 | 0.611 | 0.929 | 8.172% | 63 | 0 | 0.676 | 0.579 | 0.7 | -0.037 | 1.169 | 6.648% | -5.74 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.039 | 263.5 | 130 | 0 | 43 | 220.5 | 222.2 | 1.7 | 0.14 | 1.585 | 1.627 | 0.974 | 10.09% | 222.5 | 0.2 | 1.809 | 1.534 | 2 | -0.037 | 1.179 | 8.139% | -7.15 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.039 | 253 | 175 | 35 | 42.6 | 175.4 | 179.1 | 3.7 | -0.07 | 3.799 | 1.346 | 2 | 4.452% | 180.2 | -0.1 | 4.872 | 1.269 | 4.8 | -0.037 | 2 | 3.256% | -2.37 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.039 | 1137 | 379 | 152 | 208.8 | 776.2 | 790.2 | 14 | -0.08 | 14.068 | 6.083 | 2 | 5.281% | 798.8 | -0.1 | 22.685 | 5.736 | 22.6 | -0.037 | 2 | 3.104% | -2.23 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.039 | 45 | 13 | 0 | 23.6 | 21.4 | 20.5 | -0.9 | -1.83 | 0.945 | 0.33 | 2 | -3.281% | 20.5 | -2.5 | 1.624 | 0.309 | -0.9 | -0.037 | 2 | -3.115% | 1.51 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.039 | 45 | 13 | 0 | 23.8 | 21.2 | 20.1 | -1.1 | -1.59 | 0.429 | 0.33 | 1.302 | -2.685% | 20 | -2.2 | 0.981 | 0.309 | -1.2 | -0.037 | 2 | -2.336% | 1.12 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.039 | 45 | 13 | 0 | 23 | 22 | 20.8 | -1.2 | -1.77 | 0.528 | 0.33 | 1.6 | -2.461% | 20.7 | -2.5 | 1.149 | 0.309 | -1.3 | -0.037 | 2 | -2.156% | 1.08 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.028 | 656.3 | 254 | 81.5 | 115.7 | 459.1 | 477.4 | 18.3 | -1.79 | 20.154 | 3.866 | 2 | 1.675% | 483.7 | -2.5 | 27.095 | 3.24 | 24.6 | -0.023 | 2 | 1.024% | -0.87 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 559.1 | 275 | 12 | 121.4 | 425.7 | 435.5 | 9.8 | 9.62 | 0.227 | 3.68 | 0.062 | 2.665% | 434.5 | 13.4 | -4.574 | 3.084 | 8.8 | -0.023 | 0 | 2.439% | -2.25 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 133.3 | 76 | 9 | 47 | 77.3 | 80.7 | 3.4 | -3.66 | 7.052 | 0.836 | 2 | 1.838% | 81.4 | -5.1 | 9.19 | 0.7 | 4.1 | -0.023 | 2 | 1.253% | -0.87 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 1166 | 420 | 170 | 290.5 | 705.5 | 700.1 | -5.4 | -21.75 | 16.311 | 6.699 | 2 | -10.08% | 704.2 | -30.3 | 28.93 | 5.614 | -1.3 | -0.023 | 2 | -34.4% | 25.3 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 692 | 514 | 45 | 93 | 554 | 564.3 | 10.3 | 0.52 | 9.785 | 4.352 | 2 | 3.138% | 565.9 | 0.7 | 11.145 | 3.647 | 11.9 | -0.023 | 2 | 2.232% | -2.17 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.028 | 105 | 12 | 0 | 92.2 | 12.8 | 14.6 | 1.8 | -0.49 | 2.296 | 0.959 | 2 | 2.738% | 14.3 | -0.7 | 2.186 | 0.814 | 1.5 | -0.023 | 2 | 2.702% | -0.38 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.028 | 357 | 161 | 11 | 80 | 266 | 277 | 11 | 3.59 | 7.472 | 2.327 | 2 | 1.517% | 280 | 5 | 9.014 | 1.95 | 14 | -0.023 | 2 | 0.9795% | -0.88 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 840 | 461 | 115.5 | 50.7 | 673.8 | 689.4 | 15.6 | 5.97 | 9.58 | 4.873 | 1.966 | 2.515% | 690.6 | 8.3 | 8.469 | 4.084 | 16.8 | -0.023 | 2 | 1.918% | -1.87 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.028 | 251 | 150 | 21 | 52.7 | 177.3 | 182 | 4.7 | -0.03 | 4.708 | 1.805 | 2 | 2.498% | 183.2 | 0 | 5.888 | 1.532 | 5.9 | -0.023 | 2 | 1.636% | -1.4 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.028 | 255 | 150 | 21 | 47.1 | 186.9 | 190.9 | 4 | 1.34 | 2.638 | 1.891 | 1.395 | 2.982% | 191.7 | 1.9 | 2.945 | 1.605 | 4.8 | -0.023 | 1.835 | 2.042% | -1.81 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 278.4 | 35 | 40 | 87.9 | 150.5 | 158.8 | 8.3 | 3.04 | 5.247 | 1.604 | 2 | 1.569% | 159.1 | 4.2 | 4.334 | 1.344 | 8.6 | -0.023 | 2 | 1.244% | -0.81 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 625 | 305 | 111 | 69.2 | 444.8 | 454.3 | 9.5 | 2.57 | 6.937 | 3.457 | 2 | 3.073% | 456.8 | 3.6 | 8.418 | 2.897 | 12 | -0.023 | 2 | 1.999% | -1.73 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 643 | 305 | 111 | 60.9 | 471.1 | 479 | 7.9 | 4.86 | 3.055 | 3.578 | 0.854 | 3.802% | 480.6 | 6.8 | 2.733 | 2.999 | 9.5 | -0.023 | 0.911 | 2.598% | -2.31 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 633.8 | 300 | 125.6 | 121.4 | 386.8 | 386.9 | 0.1 | -2.74 | 2.879 | 3.418 | 0.842 | 296.1% | 392.2 | -3.8 | 9.242 | 2.865 | 5.4 | -0.023 | 2 | 4.504% | -3.34 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 633.9 | 260 | 127.2 | 119.8 | 386.9 | 385.7 | -1.2 | -2.21 | 1.036 | 3.408 | 0.304 | -24.68% | 392.1 | -3.1 | 8.278 | 2.856 | 5.2 | -0.023 | 2 | 4.678% | -3.47 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.028 | 120 | 69 | 0 | 21.5 | 98.5 | 101.4 | 2.9 | 0 | 2.906 | 0.957 | 2 | 1.941% | 101.2 | 0 | 2.759 | 0.79 | 2.7 | -0.023 | 2 | 1.714% | -1.69 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 544 | 360 | 0 | 153.7 | 390.3 | 397.7 | 7.4 | 0.06 | 7.363 | 3.659 | 2 | 3.434% | 397.8 | 0.1 | 7.396 | 3.066 | 7.5 | -0.023 | 2 | 2.784% | -2.42 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 540 | 300.5 | 0.2 | 22.3 | 517.5 | 522.8 | 5.3 | -0.31 | 5.653 | 3.631 | 1.557 | 4.76% | 523.2 | -0.4 | 6.167 | 3.043 | 5.7 | -0.023 | 2 | 3.637% | -4.23 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 540 | 310.2 | 0 | 17.8 | 522.2 | 528.4 | 6.2 | -0.05 | 6.196 | 3.632 | 1.706 | 4.069% | 526.9 | -0.1 | 4.734 | 3.044 | 4.7 | -0.023 | 1.555 | 4.41% | -5.18 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.028 | 276 | 150 | 21 | 40.1 | 214.9 | 217.4 | 2.5 | 0.11 | 2.355 | 1.843 | 1.278 | 5.163% | 216.8 | 0.2 | 1.735 | 1.565 | 1.9 | -0.023 | 1.108 | 5.583% | -5.26 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.028 | 208 | 40 | 0 | 165.3 | 42.7 | 47.7 | 5 | 0.42 | 4.632 | 1.857 | 2 | 1.947% | 48.5 | 0.6 | 5.217 | 1.577 | 5.8 | -0.023 | 2 | 1.38% | -0.34 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | LIG | FOSS | -0.028 | 775 | 280 | 0 | 21.8 | 753.2 | 762.9 | 9.7 | 0.67 | 9.043 | 7.148 | 1.265 | 3.731% | 762.1 | 0.9 | 7.949 | 6.068 | 8.9 | -0.023 | 1.31 | 3.341% | -3.95 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.028 | 671.4 | 250 | 157.1 | 72.4 | 441.9 | 460.9 | 19 | 0.07 | 18.854 | 3.459 | 2 | 1.651% | 464.5 | 0.1 | 22.484 | 2.899 | 22.6 | -0.023 | 2 | 1.14% | -0.91 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 730 | 513.8 | 43.6 | 152.5 | 533.9 | 547.3 | 13.4 | 0 | 13.418 | 4.617 | 2 | 2.544% | 551.8 | 0 | 17.893 | 3.869 | 17.9 | -0.023 | 2 | 1.565% | -1.39 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 746 | 486 | 49.2 | 205.6 | 491.2 | 506.5 | 15.3 | 0 | 15.251 | 4.687 | 2 | 2.277% | 515.2 | 0 | 23.986 | 3.928 | 24 | -0.023 | 2 | 1.193% | -0.95 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 746.3 | 492.6 | 45.2 | 179.3 | 521.8 | 540.9 | 19.1 | 2.01 | 17.014 | 4.716 | 2 | 1.825% | 548.8 | 2.8 | 24.166 | 3.952 | 27 | -0.023 | 2 | 1.061% | -0.9 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.028 | 50 | 24 | 0 | 25.8 | 24.2 | 25 | 0.8 | 0.1 | 0.783 | 0.399 | 1.964 | 2.952% | 29.2 | 0.1 | 4.955 | 0.329 | 5 | -0.023 | 2 | 0.389% | -0.22 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.028 | 542.5 | 240 | 2 | 290.7 | 249.8 | 256.6 | 6.8 | 1.89 | 4.872 | 3.636 | 1.34 | 3.727% | 257.3 | 2.6 | 4.851 | 3.047 | 7.5 | -0.023 | 1.592 | 2.777% | -1.55 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.028 | 56.3 | 22.5 | 0 | 33.7 | 22.6 | 24.8 | 2.2 | -0.01 | 2.173 | 0.449 | 2 | 1.207% | 28.1 | 0 | 5.504 | 0.371 | 5.5 | -0.023 | 2 | 0.3975% | -0.19 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.028 | 746 | 420 | 0 | 146.4 | 599.6 | 612.4 | 12.8 | 3.96 | 8.785 | 5.018 | 1.751 | 2.722% | 611.1 | 5.5 | 5.968 | 4.205 | 11.5 | -0.023 | 1.419 | 2.489% | -2.43 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 245 | 118 | 0 | 38.1 | 206.9 | 213.4 | 6.5 | 0.6 | 5.894 | 1.648 | 2 | 1.763% | 215.4 | 0.8 | 7.625 | 1.381 | 8.5 | -0.023 | 2 | 1.108% | -1.13 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.028 | 86 | 70 | 0 | 14.4 | 71.6 | 72.2 | 0.6 | 0.08 | 0.495 | 0.686 | 0.722 | 6.736% | 72.1 | 0.1 | 0.301 | 0.566 | 0.5 | -0.023 | 0.532 | 6.65% | -6.63 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.028 | 86 | 70 | 0 | 13.7 | 72.3 | 73.1 | 0.8 | -0.04 | 0.891 | 0.686 | 1.298 | 5.052% | 72.7 | -0.1 | 0.5 | 0.566 | 0.4 | -0.023 | 0.882 | 8.312% | -8.36 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 890 | 475 | 123.7 | 104.6 | 661.7 | 676.4 | 14.7 | -2.14 | 16.844 | 5.155 | 2 | 2.827% | 679.4 | -3 | 20.681 | 4.32 | 17.7 | -0.023 | 2 | 1.929% | -1.74 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 95 | 79 | 3 | 12.2 | 79.8 | 80.1 | 0.3 | 0.06 | 0.187 | 0.619 | 0.301 | 14.87% | 81 | 0.1 | 1.082 | 0.519 | 1.2 | -0.023 | 2 | 3.058% | -3.08 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 755 | 340 | 40 | 213.5 | 501.5 | 492.5 | -9 | -13.83 | 4.851 | 4.81 | 1.009 | -3.918% | 488.6 | -19.2 | 6.374 | 4.031 | -12.9 | -0.023 | 1.581 | -2.246% | 1.81 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.028 | 1140 | 379 | 152 | 316 | 672 | 689.5 | 17.5 | 0.98 | 16.544 | 6.646 | 2 | 3.042% | 693.3 | 1.4 | 19.978 | 5.569 | 21.3 | -0.023 | 2 | 2.053% | -1.47 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.05 | 38 | 20 | 0 | 7.7 | 30.3 | 30.8 | 0.5 | 0.12 | 0.386 | 0.42 | 0.92 | 6.39% | 31.1 | 0.2 | 0.641 | 0.491 | 0.8 | -0.055 | 1.306 | 4.39% | -3.12 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.05 | 412 | 140 | 0 | 86.6 | 325.4 | 329.1 | 3.7 | 0.02 | 3.607 | 2.272 | 1.588 | 9.295% | 333.3 | 0 | 7.832 | 2.89 | 7.9 | -0.055 | 2 | 4.788% | -3.43 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.05 | 173.6 | 147.6 | 0 | 18.6 | 155 | 158.2 | 3.2 | 0.5 | 2.67 | 1.622 | 1.646 | 4.53% | 159.1 | 0.7 | 3.345 | 1.876 | 4.1 | -0.055 | 1.784 | 3.888% | -3.14 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.05 | 560 | 135 | 0 | 86.6 | 473.4 | 481.7 | 8.3 | 0.79 | 7.473 | 6.599 | 1.132 | 5.626% | 484.8 | 1.1 | 10.319 | 7.58 | 11.4 | -0.055 | 1.361 | 4.505% | -3.46 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.05 | 670 | 300 | 0 | 90.7 | 579.3 | 590.9 | 11.6 | -0.14 | 11.801 | 6.89 | 1.713 | 4.816% | 593.1 | -0.2 | 13.98 | 7.914 | 13.8 | -0.055 | 1.766 | 4.453% | -3.5 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.05 | 417 | 125 | 0 | 58.4 | 358.6 | 362.8 | 4.2 | 0.3 | 3.918 | 4.087 | 0.959 | 8.281% | 362.2 | 0.4 | 3.25 | 4.694 | 3.6 | -0.055 | 0.692 | 10.63% | -8.29 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.05 | 271.9 | 155 | 14.7 | 8.4 | 248.8 | 250.5 | 1.7 | 0.06 | 1.604 | 2.404 | 0.667 | 13.35% | 251 | 0.1 | 2.125 | 2.779 | 2.2 | -0.055 | 0.765 | 11.34% | -9.41 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.05 | 749 | 310 | 0 | 182.6 | 566.4 | 576 | 9.6 | -0.43 | 9.961 | 4.397 | 2 | 6.508% | 581.2 | -0.6 | 15.397 | 5.594 | 14.8 | -0.055 | 2 | 4.643% | -3.19 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.05 | 408 | 150 | 102 | 6.9 | 299.1 | 302.9 | 3.8 | 1.18 | 2.656 | 2.86 | 0.929 | 8.955% | 303.2 | 1.6 | 2.457 | 3.306 | 4.1 | -0.055 | 0.743 | 9.129% | -6.07 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.05 | 721 | 514 | 5 | 72 | 644 | 652.9 | 8.9 | 0.97 | 8.002 | 6.692 | 1.196 | 6.754% | 653.8 | 1.3 | 8.492 | 7.736 | 9.8 | -0.055 | 1.098 | 6.747% | -5.47 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.05 | 105 | 12 | 0 | 88.1 | 16.9 | 17.7 | 0.8 | -0.06 | 0.847 | 1.302 | 0.651 | 10.97% | 18.2 | -0.1 | 1.356 | 1.496 | 1.3 | -0.055 | 0.907 | 7.426% | -1.06 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.05 | 290 | 50 | 0 | 45.6 | 244.4 | 247.9 | 3.5 | -0.27 | 3.81 | 2.775 | 1.373 | 6.913% | 247 | -0.4 | 3.011 | 3.187 | 2.6 | -0.055 | 0.945 | 10.24% | -7.82 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.05 | 593.6 | 152.4 | 0 | 40.8 | 552.8 | 562.9 | 10.1 | -0.32 | 10.376 | 5.26 | 1.973 | 4.9% | 563 | -0.4 | 10.658 | 6.042 | 10.2 | -0.055 | 1.764 | 5.337% | -4.51 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.05 | 593.6 | 152.4 | 0 | 40.8 | 552.8 | 562.9 | 10.1 | -0.32 | 10.376 | 5.26 | 1.973 | 4.9% | 563 | -0.4 | 10.658 | 6.042 | 10.2 | -0.055 | 1.764 | 5.337% | -4.51 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.05 | 600.2 | 152.3 | 0 | 14.5 | 585.7 | 595.6 | 9.9 | -1.49 | 11.403 | 5.217 | 2 | 5.055% | 594.7 | -2.1 | 11.088 | 5.992 | 9 | -0.055 | 1.851 | 6.116% | -5.42 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.05 | 600.2 | 152.3 | 0 | 14.5 | 585.7 | 595.6 | 9.9 | -1.49 | 11.403 | 5.217 | 2 | 5.055% | 594.7 | -2.1 | 11.088 | 5.992 | 9 | -0.055 | 1.851 | 6.116% | -5.42 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.05 | 280 | 40 | 0 | 75.6 | 204.4 | 227.9 | 23.5 | 0.93 | 22.53 | 1.673 | 2 | 0.9953% | 229.4 | 1.3 | 23.695 | 2.128 | 25 | -0.055 | 2 | 1.029% | -0.68 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.05 | 259 | 150 | 21 | 12.9 | 225.1 | 228.2 | 3.1 | -0.48 | 3.56 | 2.927 | 1.216 | 6.972% | 228.4 | -0.7 | 3.912 | 3.362 | 3.3 | -0.055 | 1.163 | 7.203% | -5.68 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.05 | 265 | 150 | 21 | 50.3 | 193.7 | 197.9 | 4.2 | 0.18 | 4.038 | 2.737 | 1.475 | 5.265% | 199.3 | 0.2 | 5.379 | 3.144 | 5.6 | -0.055 | 1.711 | 4.343% | -2.88 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.05 | 268 | 150 | 21 | 48.3 | 198.7 | 201 | 2.3 | 0.21 | 2.1 | 2.812 | 0.747 | 9.722% | 202.7 | 0.3 | 3.757 | 3.23 | 4 | -0.055 | 1.163 | 6.149% | -4.13 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.05 | 375 | 100 | 0 | 132.8 | 242.2 | 261 | 18.8 | 2.07 | 16.803 | 1.932 | 2 | 1.665% | 247.6 | 2.9 | 2.529 | 2.458 | 5.4 | -0.055 | 1.029 | 6.376% | -3.73 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.05 | 250 | 120 | 0 | 25.6 | 224.4 | 234.4 | 10 | 1.02 | 8.944 | 2.647 | 2 | 2.086% | 234.5 | 1.4 | 8.607 | 3.041 | 10.1 | -0.055 | 2 | 2.272% | -1.85 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.05 | 130 | 69 | 0 | 22.5 | 107.5 | 110.7 | 3.2 | -0.23 | 3.403 | 1.436 | 2 | 3.394% | 110.7 | -0.3 | 3.482 | 1.679 | 3.2 | -0.055 | 2 | 3.733% | -2.79 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | GT | -0.05 | 265 | 150 | 21 | 49.8 | 194.2 | 197.1 | 2.9 | -0.54 | 3.472 | 2.371 | 1.465 | 7.625% | 197.5 | -0.8 | 4.133 | 2.723 | 3.3 | -0.055 | 1.518 | 7.37% | -4.9 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.05 | 110 | 35 | 0 | 23.3 | 86.7 | 87.5 | 0.8 | -0.4 | 1.255 | 1.215 | 1.033 | 11.49% | 88 | -0.6 | 1.848 | 1.42 | 1.3 | -0.055 | 1.301 | 7.778% | -5.54 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | WDS | STM | -0.05 | 105 | 70 | 0 | 34.4 | 70.6 | 71.8 | 1.2 | 0.18 | 1.025 | 1.16 | 0.883 | 7.315% | 72.1 | 0.2 | 1.218 | 1.356 | 1.5 | -0.055 | 0.898 | 6.436% | -3.9 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | LIG | FOSS | -0.05 | 770 | 348 | 0 | 35.4 | 734.6 | 741.7 | 7.1 | -3.01 | 10.111 | 9.664 | 1.046 | 9.042% | 741.7 | -4.2 | 11.301 | 11.1 | 7.1 | -0.055 | 1.018 | 9.945% | -8.62 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.05 | 94 | 50 | 0 | 40.2 | 53.8 | 55.4 | 1.6 | -0.3 | 1.914 | 1.038 | 1.843 | 4.914% | 55.6 | -0.4 | 2.189 | 1.214 | 1.8 | -0.055 | 1.803 | 4.803% | -2.47 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.05 | 750 | 519 | 29.5 | 106 | 614.5 | 622.9 | 8.4 | 0.71 | 7.662 | 6.734 | 1.138 | 7.444% | 626.5 | 1 | 11.022 | 7.784 | 12 | -0.055 | 1.416 | 5.732% | -4.26 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.05 | 750.3 | 526.1 | 0 | 18.7 | 731.6 | 738.7 | 7.1 | -0.12 | 7.224 | 7.012 | 1.03 | 8.81% | 739.1 | -0.2 | 7.714 | 8.107 | 7.5 | -0.055 | 0.952 | 9.174% | -8.13 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.05 | 77 | 50 | 0 | 18.6 | 58.4 | 64.6 | 6.2 | 3.86 | 2.36 | 0.851 | 2 | 1.04% | 67.2 | 5.4 | 3.476 | 0.994 | 8.8 | -0.055 | 2 | 0.8053% | -0.55 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.05 | 50.2 | 24 | 0 | 10.2 | 40 | 41.6 | 1.6 | 0.05 | 1.551 | 0.555 | 2 | 2.632% | 43.3 | 0.1 | 3.225 | 0.649 | 3.3 | -0.055 | 2 | 1.403% | -1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.05 | 50.1 | 24 | 0 | 10.2 | 39.9 | 40.8 | 0.9 | -0.2 | 1.116 | 0.553 | 2 | 4.67% | 41.6 | -0.3 | 2.034 | 0.647 | 1.7 | -0.055 | 2 | 2.718% | -1.94 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.05 | 170 | 70 | 0 | 20.8 | 149.2 | 156.8 | 7.6 | -0.13 | 7.677 | 1.589 | 2 | 1.868% | 158 | -0.2 | 9.001 | 1.837 | 8.8 | -0.055 | 2 | 1.774% | -1.41 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.05 | 380 | 222 | 0 | 33.4 | 346.6 | 350.3 | 3.7 | -0.35 | 3.999 | 4.615 | 0.866 | 8.566% | 351.4 | -0.5 | 5.25 | 5.301 | 4.8 | -0.055 | 0.99 | 7.263% | -6.01 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.05 | 26.7 | 4 | 0 | 9.8 | 16.9 | 20.3 | 3.4 | 2.61 | 0.785 | 0.295 | 2 | 0.6627% | 21 | 3.6 | 0.475 | 0.345 | 4.1 | -0.055 | 1.377 | 0.6039% | -0.34 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.05 | 26.7 | 4 | 0 | 10.3 | 16.4 | 20.2 | 3.8 | 3.05 | 0.739 | 0.295 | 2 | 0.593% | 23 | 4.2 | 2.379 | 0.345 | 6.6 | -0.055 | 2 | 0.3751% | -0.2 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.05 | 785 | 329 | 70 | 149.9 | 565.1 | 576.8 | 11.7 | -0.72 | 12.391 | 6.682 | 1.854 | 5.594% | 580.9 | -1 | 16.8 | 7.725 | 15.8 | -0.055 | 2 | 4.556% | -2.98 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.099 | 543 | 275 | 0 | 132.1 | 410.9 | 435.5 | 24.6 | 4.49 | 20.161 | 11.824 | 1.705 | 3.643% | 442 | 6.2 | 24.86 | 10.707 | 31.1 | -0.092 | 2 | 2.678% | -2.18 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.099 | 234 | 156 | 0 | 76.3 | 157.7 | 172.1 | 14.4 | 0.34 | 14.027 | 5.095 | 2 | 2.683% | 171.7 | 0.5 | 13.49 | 4.614 | 14 | -0.092 | 2 | 2.565% | -1.86 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.099 | 560 | 135 | 0 | 132.4 | 427.6 | 435.7 | 8.1 | -1.64 | 9.699 | 13.741 | 0.706 | 11.41% | 436.4 | -2.3 | 11.101 | 12.471 | 8.8 | -0.092 | 0.89 | 9.761% | -8.01 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 420 | 125 | 0 | 66.4 | 353.6 | 367.1 | 13.5 | -1.26 | 14.807 | 9.25 | 1.601 | 5.135% | 360.2 | -1.8 | 8.422 | 8.395 | 6.6 | -0.092 | 1.003 | 9.762% | -8.84 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 417 | 125 | 0 | 153.1 | 263.9 | 274.9 | 11 | -1.98 | 12.945 | 8.683 | 1.491 | 6.258% | 269.9 | -2.8 | 8.785 | 7.881 | 6 | -0.092 | 1.115 | 10.66% | -7.25 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 1117 | 420 | 169 | 56.4 | 891.6 | 924.5 | 32.9 | -3.87 | 36.746 | 20.642 | 1.78 | 5.603% | 926.9 | -5.4 | 40.733 | 18.693 | 35.3 | -0.092 | 2 | 4.853% | -4.17 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.099 | 657 | 508 | 40 | 67.9 | 549.1 | 569.6 | 20.5 | -0.44 | 20.907 | 13.435 | 1.556 | 5.289% | 569.4 | -0.6 | 20.89 | 12.166 | 20.3 | -0.092 | 1.717 | 4.964% | -4.46 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.099 | 105 | 12 | 0 | 92.2 | 12.8 | 15.8 | 3 | 0.45 | 2.583 | 2.955 | 0.874 | 5.784% | 15.6 | 0.6 | 2.163 | 2.682 | 2.8 | -0.092 | 0.807 | 5.76% | -0.74 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 558.9 | 342.1 | 0 | 30.4 | 528.5 | 548.9 | 20.4 | 2.48 | 17.996 | 12.169 | 1.479 | 4.522% | 552.1 | 3.4 | 20.192 | 11.02 | 23.6 | -0.092 | 1.832 | 3.632% | -3.69 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.099 | 600.2 | 152.3 | 0 | 98.6 | 501.6 | 525.2 | 23.6 | 0.96 | 22.616 | 12.176 | 1.857 | 4.198% | 522 | 1.3 | 19.081 | 11.051 | 20.4 | -0.092 | 1.727 | 4.513% | -4.06 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 600.2 | 152.3 | 0 | 98.6 | 501.6 | 525.2 | 23.6 | 0.96 | 22.616 | 12.176 | 1.857 | 4.198% | 522 | 1.3 | 19.081 | 11.051 | 20.4 | -0.092 | 1.727 | 4.513% | -4.06 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 431.5 | 180.3 | 0 | 56.5 | 375 | 392.8 | 17.8 | -0.42 | 18.242 | 12.272 | 1.486 | 4.001% | 392 | -0.6 | 17.587 | 11.138 | 17 | -0.092 | 1.579 | 3.894% | -3.64 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 840 | 461 | 29.1 | 50.8 | 760.1 | 794 | 33.9 | -0.54 | 34.392 | 17.656 | 1.948 | 4.089% | 809.9 | -0.8 | 50.49 | 15.989 | 49.8 | -0.092 | 2 | 2.587% | -2.52 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.099 | 840 | 461 | 68.8 | 37.3 | 733.9 | 763.7 | 29.8 | 0 | 29.827 | 16.792 | 1.776 | 4.652% | 773.9 | 0 | 40.046 | 15.206 | 40 | -0.092 | 2 | 3.221% | -3.03 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.099 | 368.1 | 220 | 45.1 | 97.6 | 225.4 | 231.4 | 6 | 0 | 5.983 | 7.033 | 0.851 | 10.13% | 234.5 | 0 | 9.116 | 6.369 | 9.1 | -0.092 | 1.431 | 6.206% | -4.08 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.099 | 241 | 150 | 21 | 60.3 | 159.7 | 166.5 | 6.8 | -0.16 | 7.021 | 5.105 | 1.375 | 5.852% | 166.6 | -0.2 | 7.151 | 4.633 | 6.9 | -0.092 | 1.544 | 5.36% | -3.81 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.099 | 245 | 150 | 21 | 55.7 | 168.3 | 174.9 | 6.6 | -0.25 | 6.891 | 5.269 | 1.308 | 6.129% | 174.8 | -0.3 | 6.883 | 4.782 | 6.5 | -0.092 | 1.439 | 5.784% | -4.27 | 0.017 | 0.05 | 5.933% | 5.163%
Wind | WND | WIND | -0.099 | 84.4 | 0 | 0 | 5 | 79.4 | 78.3 | -1.1 | -1.27 | 0.179 | 2.402 | 0.074 | -12.69% | 77.6 | -1.8 | -0.069 | 2.18 | -1.8 | -0.092 | 0 | -7.205% | 7.26 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.099 | 155 | 0 | 40 | 6.7 | 108.3 | 121.9 | 13.6 | -0.35 | 13.902 | 2.504 | 2 | 1.883% | 124.5 | -0.5 | 16.707 | 2.268 | 16.2 | -0.092 | 2 | 1.469% | -1.1 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.099 | 594 | 305 | 111 | 107.9 | 375.1 | 397.4 | 22.3 | 2.68 | 19.663 | 10.517 | 1.87 | 4.396% | 398.8 | 3.7 | 20.053 | 9.524 | 23.7 | -0.092 | 2 | 3.844% | -2.61 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.099 | 824 | 258 | 0 | 376 | 448 | 458.1 | 10.1 | -4.47 | 14.565 | 16.607 | 0.877 | 13.46% | 459.7 | -6.2 | 17.839 | 15.072 | 11.7 | -0.092 | 1.184 | 10.8% | -6.32 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.099 | 108 | 68 | 0 | 21.7 | 86.3 | 93.1 | 6.8 | -0.23 | 7.087 | 2.768 | 2 | 2.625% | 93 | -0.3 | 7.02 | 2.484 | 6.7 | -0.092 | 2 | 2.476% | -2.12 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.099 | 540 | 310 | 10.9 | 18.1 | 511 | 520.2 | 9.2 | -0.57 | 9.755 | 11.52 | 0.847 | 9.688% | 519.8 | -0.8 | 9.52 | 10.433 | 8.8 | -0.092 | 0.912 | 9.412% | -9.58 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.099 | 825 | 280 | 0 | 51.9 | 773.1 | 802.5 | 29.4 | 3.1 | 26.286 | 23.465 | 1.12 | 4.631% | 797.1 | 4.3 | 19.66 | 21.296 | 24 | -0.092 | 0.923 | 5.272% | -5.31 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 549.2 | 250 | 44.2 | 51.3 | 453.7 | 476.4 | 22.7 | -4.94 | 27.641 | 10.998 | 2 | 3.993% | 481.2 | -6.9 | 34.32 | 9.959 | 27.5 | -0.092 | 2 | 3.063% | -2.72 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.099 | 650 | 189.6 | 0 | 53.3 | 596.7 | 610.7 | 14 | -0.49 | 14.485 | 12.197 | 1.188 | 7.663% | 611.2 | -0.7 | 15.11 | 11.069 | 14.5 | -0.092 | 1.365 | 6.876% | -6.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 650 | 189.6 | 0 | 53.3 | 596.7 | 610.7 | 14 | -0.49 | 14.485 | 12.197 | 1.188 | 7.663% | 611.2 | -0.7 | 15.11 | 11.069 | 14.5 | -0.092 | 1.365 | 6.876% | -6.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 650 | 189.6 | 0 | 53.3 | 596.7 | 610.7 | 14 | -0.49 | 14.485 | 12.197 | 1.188 | 7.663% | 611.2 | -0.7 | 15.11 | 11.069 | 14.5 | -0.092 | 1.365 | 6.876% | -6.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 650 | 189.6 | 0 | 53.3 | 596.7 | 610.7 | 14 | -0.49 | 14.485 | 12.197 | 1.188 | 7.663% | 611.2 | -0.7 | 15.11 | 11.069 | 14.5 | -0.092 | 1.365 | 6.876% | -6.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 650 | 189.6 | 0 | 53.3 | 596.7 | 610.7 | 14 | -0.49 | 14.485 | 12.197 | 1.188 | 7.663% | 611.2 | -0.7 | 15.11 | 11.069 | 14.5 | -0.092 | 1.365 | 6.876% | -6.79 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 752 | 493.8 | 46.9 | 184.6 | 520.5 | 541.3 | 20.8 | 0.18 | 20.577 | 15.353 | 1.34 | 5.967% | 548.2 | 0.2 | 27.411 | 13.903 | 27.7 | -0.092 | 1.972 | 4.164% | -3.1 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.099 | 275 | 225 | 0 | 49.5 | 225.5 | 238.4 | 12.9 | -0.3 | 13.138 | 5.988 | 2 | 3.52% | 238.5 | -0.4 | 13.382 | 5.423 | 13 | -0.092 | 2 | 3.246% | -2.86 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.099 | 56 | 22.5 | 0 | 33.4 | 22.6 | 24.5 | 1.9 | -0.03 | 1.963 | 1.437 | 1.366 | 4.878% | 24.2 | 0 | 1.694 | 1.289 | 1.6 | -0.092 | 1.314 | 5.384% | -2.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.099 | 55.9 | 22.5 | 0 | 33.3 | 22.6 | 24.9 | 2.3 | -0.04 | 2.377 | 1.433 | 1.658 | 4.023% | 26.5 | -0.1 | 3.925 | 1.286 | 3.9 | -0.092 | 2 | 2.205% | -0.95 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.099 | 380 | 222 | 0 | 99.8 | 280.2 | 291.7 | 11.5 | 0 | 11.562 | 10.459 | 1.105 | 5.455% | 292.6 | 0 | 12.421 | 9.493 | 12.4 | -0.092 | 1.309 | 4.701% | -3.73 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 932.6 | 360 | 0 | 68.2 | 864.4 | 895.7 | 31.3 | 0.21 | 31.083 | 18.934 | 1.642 | 4.917% | 899.9 | 0.3 | 35.212 | 17.184 | 35.5 | -0.092 | 2 | 4.029% | -4.02 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 932.6 | 360 | 0 | 68.2 | 864.4 | 895.7 | 31.3 | 0.21 | 31.083 | 18.934 | 1.642 | 4.917% | 899.9 | 0.3 | 35.212 | 17.184 | 35.5 | -0.092 | 2 | 4.029% | -4.02 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 932.6 | 360 | 0 | 68.2 | 864.4 | 895.7 | 31.3 | 0.21 | 31.083 | 18.934 | 1.642 | 4.917% | 899.9 | 0.3 | 35.212 | 17.184 | 35.5 | -0.092 | 2 | 4.029% | -4.02 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.099 | 932.6 | 360 | 0 | 68.2 | 864.4 | 895.7 | 31.3 | 0.21 | 31.083 | 18.934 | 1.642 | 4.917% | 899.9 | 0.3 | 35.212 | 17.184 | 35.5 | -0.092 | 2 | 4.029% | -4.02 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.099 | 86 | 63 | 0 | 22.1 | 63.9 | 66.8 | 2.9 | -0.21 | 3.125 | 2.204 | 1.418 | 4.903% | 66.5 | -0.3 | 2.909 | 1.978 | 2.6 | -0.092 | 1.471 | 5.083% | -4.04 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.099 | 86 | 63 | 0 | 21.1 | 64.9 | 67.7 | 2.8 | -0.16 | 2.958 | 2.204 | 1.342 | 5.078% | 67.3 | -0.2 | 2.646 | 1.978 | 2.4 | -0.092 | 1.338 | 5.506% | -4.45 | 0.017 | 0.05 | 5.933% | 5.163%
Wind | WND | WIND | -0.099 | 130.9 | 0 | 0 | 14.2 | 116.7 | 117.4 | 0.7 | -4.17 | 4.885 | 3.723 | 1.312 | 30.9% | 117.3 | -5.8 | 6.438 | 3.379 | 0.6 | -0.092 | 1.905 | 33.5% | -32.05 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.099 | 268 | 100 | 0 | 108.9 | 159.1 | 170.9 | 11.8 | 2.91 | 8.874 | 5.836 | 1.521 | 3.75% | 177.1 | 4 | 13.94 | 5.285 | 18 | -0.092 | 2 | 2.285% | -1.46 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.099 | 88 | 69 | 3 | 14.3 | 70.7 | 73.4 | 2.7 | -0.06 | 2.761 | 1.851 | 1.492 | 5.388% | 74 | -0.1 | 3.396 | 1.676 | 3.3 | -0.092 | 2 | 4.097% | -3.53 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.099 | 577 | 159 | 0 | 178.3 | 398.7 | 408.4 | 9.7 | -3.7 | 13.447 | 13.525 | 0.994 | 9.818% | 406.4 | -5.1 | 12.843 | 12.275 | 7.7 | -0.092 | 1.046 | 11.49% | -8.54 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.099 | 562 | 303 | 0 | 258.7 | 303.3 | 318.7 | 15.4 | 0 | 15.361 | 13.805 | 1.113 | 6.023% | 318.1 | 0 | 14.833 | 12.529 | 14.8 | -0.092 | 1.184 | 5.824% | -3.38 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.099 | 1138 | 379 | 152 | 181.2 | 804.8 | 844.5 | 39.7 | -1.04 | 40.684 | 21.47 | 1.895 | 4.73% | 846 | -1.4 | 42.596 | 19.442 | 41.2 | -0.092 | 2 | 4.236% | -3.22 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.104 | 546.2 | 275 | 0 | 225 | 321.2 | 324.2 | 3 | -9.21 | 12.192 | 10.103 | 1.207 | 31.57% | 329.1 | -12.8 | 20.666 | 9.338 | 7.9 | -0.099 | 2 | 11.41% | -7.04 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.104 | 212 | 151 | 0 | 42.7 | 169.3 | 181.7 | 12.4 | -1.01 | 13.396 | 3.921 | 2 | 2.966% | 181.8 | -1.4 | 13.92 | 3.624 | 12.5 | -0.099 | 2 | 2.801% | -2.35 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.104 | 194 | 117 | 5 | 16.8 | 172.2 | 175.1 | 2.9 | 0.35 | 2.54 | 3.496 | 0.726 | 11.61% | 176.4 | 0.5 | 3.707 | 3.231 | 4.2 | -0.099 | 1.147 | 7.628% | -7.1 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.104 | 560 | 135 | 0 | 111.8 | 448.2 | 460.4 | 12.2 | 1.7 | 10.524 | 12.182 | 0.864 | 7.959% | 466.6 | 2.4 | 16.041 | 11.282 | 18.4 | -0.099 | 1.422 | 5.023% | -4.22 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.104 | 420 | 125 | 0 | 196.7 | 223.3 | 237 | 13.7 | 1.93 | 11.696 | 7.217 | 1.621 | 5.316% | 262.9 | 2.7 | 36.912 | 6.683 | 39.6 | -0.099 | 2 | 1.751% | -0.98 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.104 | 417 | 125 | 0 | 169.8 | 247.2 | 258.4 | 11.2 | 1.5 | 9.707 | 7.311 | 1.328 | 6.456% | 271.5 | 2.1 | 22.199 | 6.771 | 24.3 | -0.099 | 2 | 2.833% | -1.76 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.104 | 45 | 0 | 0 | 12.6 | 32.4 | 34.2 | 1.8 | 0.01 | 1.838 | 0.98 | 1.875 | 4.349% | 34.2 | 0 | 1.817 | 0.9 | 1.8 | -0.099 | 2 | 4.141% | -3.1 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.104 | 1121 | 420 | 170 | 20.4 | 930.6 | 951.2 | 20.6 | 2.05 | 18.614 | 17.591 | 1.058 | 9.434% | 955.8 | 2.9 | 22.405 | 16.258 | 25.2 | -0.099 | 1.378 | 7.341% | -6.4 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.104 | 665 | 508 | 39 | 28.5 | 597.5 | 613.3 | 15.8 | 0.88 | 14.986 | 11.579 | 1.294 | 7.297% | 614.3 | 1.2 | 15.568 | 10.702 | 16.8 | -0.099 | 1.455 | 6.533% | -6.16 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.104 | 105 | 12 | 0 | 92.9 | 12.1 | 14.8 | 2.7 | 0.12 | 2.608 | 2.521 | 1.034 | 6.751% | 14.6 | 0.2 | 2.29 | 2.335 | 2.5 | -0.099 | 0.981 | 6.941% | -0.83 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.104 | 502 | 271 | 10 | 16 | 476 | 489.7 | 13.7 | 0 | 13.772 | 9.101 | 1.513 | 6.353% | 489.8 | 0 | 13.829 | 8.411 | 13.8 | -0.099 | 1.644 | 6.004% | -5.98 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.104 | 562.8 | 343.8 | 0 | 25.6 | 537.2 | 553.7 | 16.5 | -1.23 | 17.75 | 10.41 | 1.705 | 5.914% | 559.4 | -1.7 | 23.959 | 9.621 | 22.2 | -0.099 | 2 | 4.184% | -4.19 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.104 | 594.6 | 152.4 | 0 | 111 | 483.6 | 502.8 | 19.2 | 0.32 | 18.917 | 10.381 | 1.822 | 5.369% | 501.1 | 0.4 | 17.06 | 9.614 | 17.5 | -0.099 | 1.774 | 5.608% | -4.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.104 | 594.6 | 152.4 | 0 | 111 | 483.6 | 502.8 | 19.2 | 0.32 | 18.917 | 10.381 | 1.822 | 5.369% | 501.1 | 0.4 | 17.06 | 9.614 | 17.5 | -0.099 | 1.774 | 5.608% | -4.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.104 | 428.6 | 180.3 | 0 | 48.5 | 380.1 | 395.9 | 15.8 | 1.19 | 14.62 | 10.394 | 1.407 | 4.704% | 396 | 1.7 | 14.322 | 9.626 | 15.9 | -0.099 | 1.488 | 4.45% | -4.14 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.104 | 620 | 305 | 111 | 65 | 444 | 453.2 | 9.2 | 0.18 | 8.989 | 9.415 | 0.955 | 11.68% | 454.5 | 0.2 | 10.285 | 8.702 | 10.5 | -0.099 | 1.182 | 9.746% | -7.33 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.104 | 635 | 305 | 111 | 109 | 415 | 426.6 | 11.6 | 1.03 | 10.589 | 9.693 | 1.093 | 9.491% | 428.9 | 1.4 | 12.486 | 8.958 | 13.9 | -0.099 | 1.394 | 7.54% | -5.17 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.104 | 824 | 258 | 0 | 337.8 | 486.2 | 496.4 | 10.2 | 3.19 | 7.016 | 14.363 | 0.489 | 14.01% | 496.2 | 4.4 | 5.575 | 13.302 | 10 | -0.099 | 0.419 | 13.6% | -8.42 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.104 | 836 | 258 | 0 | 189.7 | 646.3 | 666.1 | 19.8 | 3.54 | 16.25 | 15.194 | 1.07 | 7.32% | 666.5 | 4.9 | 15.267 | 14.071 | 20.2 | -0.099 | 1.085 | 6.83% | -5.54 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.104 | 111 | 68 | 0 | 22.1 | 88.9 | 95.1 | 6.2 | 0.23 | 5.945 | 2.418 | 2 | 3.108% | 95.3 | 0.3 | 6.088 | 2.219 | 6.4 | -0.099 | 2 | 2.866% | -2.4 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.104 | 540 | 310.2 | 4.7 | 10.9 | 524.4 | 535.9 | 11.5 | 0.61 | 10.827 | 9.901 | 1.093 | 8.142% | 536.3 | 0.9 | 11.009 | 9.151 | 11.9 | -0.099 | 1.203 | 7.49% | -7.64 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.104 | 805 | 300 | 0 | 130.5 | 674.5 | 702.8 | 28.3 | 0.39 | 27.857 | 19.523 | 1.427 | 4.932% | 699.9 | 0.5 | 24.819 | 18.081 | 25.4 | -0.099 | 1.373 | 5.23% | -4.6 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.104 | 524.8 | 317.8 | 44.8 | 41.9 | 438.1 | 441.9 | 3.8 | -5.17 | 9.027 | 8.878 | 1.017 | 23.95% | 449.7 | -7.2 | 18.798 | 8.205 | 11.6 | -0.099 | 2 | 7.467% | -6.54 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.104 | 650 | 189.6 | 0 | 281.3 | 368.7 | 383.3 | 14.6 | 0.53 | 13.997 | 9.508 | 1.472 | 7.719% | 386.7 | 0.7 | 17.2 | 8.806 | 18 | -0.099 | 1.953 | 5.96% | -3.55 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.104 | 650 | 189.6 | 0 | 281.3 | 368.7 | 383.3 | 14.6 | 0.53 | 13.997 | 9.508 | 1.472 | 7.719% | 386.7 | 0.7 | 17.2 | 8.806 | 18 | -0.099 | 1.953 | 5.96% | -3.55 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.104 | 650 | 189.6 | 0 | 281.3 | 368.7 | 383.3 | 14.6 | 0.53 | 13.997 | 9.508 | 1.472 | 7.719% | 386.7 | 0.7 | 17.2 | 8.806 | 18 | -0.099 | 1.953 | 5.96% | -3.55 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.104 | 650 | 189.6 | 0 | 281.3 | 368.7 | 383.3 | 14.6 | 0.53 | 13.997 | 9.508 | 1.472 | 7.719% | 386.7 | 0.7 | 17.2 | 8.806 | 18 | -0.099 | 1.953 | 5.96% | -3.55 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.104 | 650 | 189.6 | 0 | 281.3 | 368.7 | 383.3 | 14.6 | 0.53 | 13.997 | 9.508 | 1.472 | 7.719% | 386.7 | 0.7 | 17.2 | 8.806 | 18 | -0.099 | 1.953 | 5.96% | -3.55 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.104 | 752.3 | 490.5 | 45 | 185 | 522.3 | 539.5 | 17.2 | -0.18 | 17.365 | 13.083 | 1.327 | 7.583% | 544.1 | -0.2 | 22.053 | 12.092 | 21.8 | -0.099 | 1.824 | 5.695% | -4.15 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.104 | 752.8 | 482.7 | 41.3 | 175.5 | 536 | 559.2 | 23.2 | 0.53 | 22.645 | 13.161 | 1.721 | 5.626% | 567.4 | 0.7 | 30.618 | 12.164 | 31.4 | -0.099 | 2 | 3.957% | -2.96 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.104 | 509.9 | 238 | 0 | 226.4 | 283.5 | 300.9 | 17.4 | 0.77 | 16.691 | 9.432 | 1.77 | 5.081% | 311.8 | 1.1 | 27.276 | 8.717 | 28.3 | -0.099 | 2 | 2.974% | -1.74 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.104 | 305.6 | 118 | 65 | 75.5 | 165.1 | 171.6 | 6.5 | -0.87 | 7.441 | 4.451 | 1.672 | 8.154% | 175.5 | -1.2 | 11.611 | 4.114 | 10.4 | -0.099 | 2 | 4.851% | -2.75 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.104 | 387 | 222 | 0 | 40.8 | 346.2 | 354.2 | 8 | 0.77 | 7.266 | 9.083 | 0.8 | 8.389% | 354.6 | 1.1 | 7.376 | 8.412 | 8.4 | -0.099 | 0.877 | 7.605% | -7.14 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.104 | 932.6 | 360 | 0 | 124.2 | 808.4 | 845.6 | 37.2 | -2.79 | 39.988 | 16.337 | 2 | 4.346% | 843.2 | -3.9 | 38.686 | 15.13 | 34.8 | -0.099 | 2 | 4.423% | -4.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.104 | 932.6 | 360 | 0 | 124.2 | 808.4 | 845.6 | 37.2 | -2.79 | 39.988 | 16.337 | 2 | 4.346% | 843.2 | -3.9 | 38.686 | 15.13 | 34.8 | -0.099 | 2 | 4.423% | -4.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.104 | 932.6 | 360 | 0 | 124.2 | 808.4 | 845.6 | 37.2 | -2.79 | 39.988 | 16.337 | 2 | 4.346% | 843.2 | -3.9 | 38.686 | 15.13 | 34.8 | -0.099 | 2 | 4.423% | -4.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.104 | 932.6 | 360 | 0 | 124.2 | 808.4 | 845.6 | 37.2 | -2.79 | 39.988 | 16.337 | 2 | 4.346% | 843.2 | -3.9 | 38.686 | 15.13 | 34.8 | -0.099 | 2 | 4.423% | -4.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.104 | 85 | 64 | 0 | 20.5 | 64.5 | 67.4 | 2.9 | 0.1 | 2.769 | 1.852 | 1.495 | 5.09% | 67.1 | 0.1 | 2.445 | 1.7 | 2.6 | -0.099 | 1.439 | 5.405% | -4.29 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.104 | 900 | 510 | 123.3 | 34.9 | 741.8 | 757.4 | 15.6 | 2.06 | 13.506 | 14.367 | 0.94 | 10% | 758.3 | 2.9 | 13.565 | 13.279 | 16.5 | -0.099 | 1.022 | 9.002% | -7.79 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.104 | 89 | 68 | 3 | 15.2 | 70.8 | 72.7 | 1.9 | -0.06 | 2 | 1.591 | 1.257 | 8.134% | 73.1 | -0.1 | 2.411 | 1.47 | 2.3 | -0.099 | 1.64 | 6.397% | -5.32 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.104 | 669 | 156 | 0 | 128.9 | 540.1 | 569.2 | 29.1 | 4.69 | 24.367 | 12.762 | 1.909 | 3.986% | 570.5 | 6.5 | 23.913 | 11.819 | 30.4 | -0.099 | 2 | 3.632% | -3.08 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.104 | 577 | 159 | 0 | 102.6 | 474.4 | 483.1 | 8.7 | 0.76 | 7.898 | 11.082 | 0.713 | 11.5% | 482.5 | 1.1 | 6.949 | 10.264 | 8.1 | -0.099 | 0.677 | 11.76% | -10.15 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.104 | 562 | 159 | 0 | 16 | 546 | 555.6 | 9.6 | 2.52 | 7.095 | 10.389 | 0.683 | 10.15% | 555.5 | 3.5 | 5.965 | 9.621 | 9.5 | -0.099 | 0.62 | 9.764% | -9.96 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.104 | 1125 | 379 | 152 | 231.7 | 741.3 | 775.3 | 34 | 1.84 | 32.141 | 17.998 | 1.786 | 5.736% | 777.8 | 2.6 | 33.96 | 16.635 | 36.5 | -0.099 | 2 | 5.086% | -3.52 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.051 | 652.2 | 250 | 80.5 | 108.4 | 463.3 | 469.5 | 6.2 | -1.1 | 7.289 | 2.987 | 2 | 8.946% | 464.2 | -1.5 | 2.436 | 3.179 | 0.9 | -0.052 | 0.766 | 62.84% | -43.72 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.051 | 558.2 | 275 | 0 | 16 | 542.2 | 550.2 | 8 | -5.13 | 13.195 | 2.916 | 2 | 5.934% | 551 | -7.1 | 15.961 | 3.104 | 8.8 | -0.052 | 2 | 5.501% | -5.23 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.051 | 260 | 170 | 10 | 6.8 | 243.2 | 246.8 | 3.6 | 0.65 | 2.956 | 1.306 | 2 | 6.147% | 246.5 | 0.9 | 2.44 | 1.39 | 3.3 | -0.052 | 1.755 | 6.837% | -6.26 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.051 | 517 | 369 | 10 | 50.6 | 456.4 | 460.6 | 4.2 | -0.3 | 4.421 | 2.649 | 1.669 | 10.47% | 458.7 | -0.4 | 2.668 | 2.819 | 2.3 | -0.052 | 0.946 | 19.49% | -16.85 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.051 | 478 | 300 | 0 | 15.4 | 462.6 | 470.5 | 7.9 | -0.9 | 8.774 | 2.497 | 2 | 5.147% | 472.3 | -1.3 | 10.941 | 2.658 | 9.7 | -0.052 | 2 | 4.274% | -4.05 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.051 | 229 | 148 | 0 | 41.7 | 187.3 | 190.5 | 3.2 | -0.54 | 3.69 | 1.196 | 2 | 6.092% | 192.1 | -0.8 | 5.487 | 1.273 | 4.8 | -0.052 | 2 | 4.141% | -3.31 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.051 | 560 | 135 | 0 | 125.3 | 434.7 | 443.2 | 8.5 | 0.18 | 8.351 | 3.566 | 2 | 5.603% | 444 | 0.2 | 9.028 | 3.776 | 9.3 | -0.052 | 2 | 5.222% | -3.97 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.051 | 785 | 300 | 0 | 97.3 | 687.7 | 694.7 | 7 | 4.37 | 2.662 | 5.229 | 0.509 | 9.536% | 697.4 | 6.1 | 3.575 | 5.538 | 9.7 | -0.052 | 0.646 | 7.017% | -6.02 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.051 | 420 | 125 | 0 | 37.4 | 382.6 | 386.4 | 3.8 | -0.7 | 4.494 | 2.419 | 1.858 | 9.402% | 386.2 | -1 | 4.603 | 2.562 | 3.6 | -0.052 | 1.797 | 10.12% | -9.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.051 | 417 | 125 | 0 | 63.6 | 353.4 | 356.7 | 3.3 | -0.65 | 3.883 | 2.366 | 1.642 | 10.75% | 354.8 | -0.9 | 2.291 | 2.505 | 1.4 | -0.052 | 0.914 | 25.83% | -21.44 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.051 | 1143 | 420 | 170 | 204 | 769 | 782.3 | 13.3 | -0.37 | 13.724 | 5.084 | 2 | 7.307% | 783.6 | -0.5 | 15.166 | 5.411 | 14.6 | -0.052 | 2 | 6.787% | -4.48 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.051 | 665 | 508 | 25 | 33.3 | 606.7 | 614.4 | 7.7 | -0.01 | 7.708 | 3.344 | 2 | 7.345% | 613.1 | 0 | 6.439 | 3.559 | 6.4 | -0.052 | 1.809 | 9.01% | -8.05 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.051 | 105 | 12 | 0 | 90.3 | 14.7 | 15 | 0.3 | -0.51 | 0.767 | 0.757 | 1.014 | 29.84% | 15.2 | -0.7 | 1.136 | 0.802 | 0.5 | -0.052 | 1.417 | 18.26% | -2.44 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.051 | 52 | 26 | 0 | 13.7 | 38.3 | 40.6 | 2.3 | -0.2 | 2.505 | 0.272 | 2 | 1.934% | 40.7 | -0.3 | 2.604 | 0.289 | 2.4 | -0.052 | 2 | 1.89% | -1.34 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.051 | 158 | 80 | 0 | 14.7 | 143.3 | 146.8 | 3.5 | 0.04 | 3.497 | 0.982 | 2 | 3.845% | 150.2 | 0.1 | 6.885 | 1.049 | 6.9 | -0.052 | 2 | 1.989% | -1.76 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.051 | 340 | 156 | 11 | 26.8 | 302.2 | 306.5 | 4.3 | 1.04 | 3.321 | 1.719 | 1.932 | 6.728% | 306.7 | 1.4 | 3.097 | 1.83 | 4.5 | -0.052 | 1.693 | 6.554% | -5.7 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.051 | 594.6 | 152.4 | 0 | 59.2 | 535.4 | 540.6 | 5.2 | 0.32 | 4.89 | 3.089 | 1.583 | 9.725% | 539.3 | 0.4 | 3.452 | 3.272 | 3.9 | -0.052 | 1.055 | 13.22% | -11.66 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.051 | 594.6 | 152.4 | 0 | 59.2 | 535.4 | 540.6 | 5.2 | 0.32 | 4.89 | 3.089 | 1.583 | 9.725% | 539.3 | 0.4 | 3.452 | 3.272 | 3.9 | -0.052 | 1.055 | 13.22% | -11.66 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.051 | 600.2 | 152.3 | 0 | 49.6 | 550.6 | 556 | 5.4 | -0.32 | 5.793 | 3.098 | 1.869 | 9.453% | 554.4 | -0.4 | 4.275 | 3.281 | 3.8 | -0.052 | 1.303 | 13.7% | -12.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.051 | 600.2 | 152.3 | 0 | 49.6 | 550.6 | 556 | 5.4 | -0.32 | 5.793 | 3.098 | 1.869 | 9.453% | 554.4 | -0.4 | 4.275 | 3.281 | 3.8 | -0.052 | 1.303 | 13.7% | -12.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.051 | 428.6 | 180.3 | 0 | 30.5 | 398.1 | 401.6 | 3.5 | -0.24 | 3.759 | 3.12 | 1.205 | 10.42% | 401.4 | -0.3 | 3.732 | 3.305 | 3.3 | -0.052 | 1.129 | 11.26% | -10.25 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | STM | -0.051 | 325.9 | 55.9 | 0 | 76.9 | 249 | 252.7 | 3.7 | 0.55 | 3.09 | 2.277 | 1.357 | 7.495% | 253.9 | 0.8 | 4.134 | 2.411 | 4.9 | -0.052 | 1.715 | 5.77% | -4.31 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | COGN | -0.051 | 249 | 150 | 21 | 44.2 | 183.8 | 187.1 | 3.3 | -1.03 | 4.338 | 1.441 | 2 | 6.422% | 187.1 | -1.4 | 4.731 | 1.526 | 3.3 | -0.052 | 2 | 6.548% | -4.73 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.051 | 256 | 150 | 21 | 9.7 | 225.3 | 228.2 | 2.9 | -1.01 | 3.913 | 1.677 | 2 | 7.513% | 228.2 | -1.4 | 4.338 | 1.776 | 2.9 | -0.052 | 2 | 7.66% | -6.59 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.051 | 258 | 150 | 21 | 9.9 | 227.1 | 230.3 | 3.2 | -1.02 | 4.247 | 1.699 | 2 | 6.862% | 229.9 | -1.4 | 4.175 | 1.799 | 2.8 | -0.052 | 2 | 7.996% | -6.88 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.051 | 254 | 150 | 21 | 40.4 | 192.6 | 195.8 | 3.2 | -0.84 | 4.091 | 1.511 | 2 | 6.756% | 195.7 | -1.2 | 4.276 | 1.601 | 3.1 | -0.052 | 2 | 7.11% | -5.27 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | GT | -0.051 | 103 | 35 | 0 | 65.3 | 37.7 | 40.3 | 2.6 | 0.13 | 2.422 | 0.64 | 2 | 3.378% | 42.8 | 0.2 | 4.959 | 0.684 | 5.1 | -0.052 | 2 | 1.756% | -0.62 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | COGN | -0.051 | 107 | 68 | 0 | 21.9 | 85.1 | 87.7 | 2.6 | -0.23 | 2.814 | 0.665 | 2 | 3.509% | 87.5 | -0.3 | 2.683 | 0.711 | 2.4 | -0.052 | 2 | 3.876% | -3 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | GT | -0.051 | 262 | 150 | 21 | 9 | 232 | 234.1 | 2.1 | -0.71 | 2.862 | 1.466 | 1.953 | 10.62% | 234.6 | -1 | 3.622 | 1.552 | 2.6 | -0.052 | 2 | 8.744% | -7.57 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.051 | 208 | 75 | 0 | 65.5 | 142.5 | 148.9 | 6.4 | 1.99 | 4.445 | 1.364 | 2 | 2.767% | 151.2 | 2.8 | 5.929 | 1.445 | 8.7 | -0.052 | 2 | 2.075% | -1.39 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | GT | -0.051 | 118 | 35 | 0 | 28.9 | 89.1 | 91.3 | 2.2 | 1.78 | 0.448 | 0.733 | 0.611 | 4.572% | 94.1 | 2.5 | 2.51 | 0.784 | 5 | -0.052 | 2 | 2.051% | -1.51 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.051 | 670.4 | 250 | 154.4 | 24.2 | 491.8 | 499.8 | 8 | -1.38 | 9.375 | 2.696 | 2 | 7.127% | 496.7 | -1.9 | 6.772 | 2.869 | 4.9 | -0.052 | 2 | 11.86% | -8.53 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.051 | 650 | 189.4 | 0 | 203.7 | 446.3 | 454.1 | 7.8 | -0.89 | 8.752 | 2.992 | 2 | 7.087% | 454.2 | -1.2 | 9.177 | 3.169 | 7.9 | -0.052 | 2 | 7.134% | -4.8 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.051 | 650 | 189.4 | 0 | 203.7 | 446.3 | 454.1 | 7.8 | -0.89 | 8.752 | 2.992 | 2 | 7.087% | 454.2 | -1.2 | 9.177 | 3.169 | 7.9 | -0.052 | 2 | 7.134% | -4.8 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.051 | 650 | 189.4 | 0 | 203.7 | 446.3 | 454.1 | 7.8 | -0.89 | 8.752 | 2.992 | 2 | 7.087% | 454.2 | -1.2 | 9.177 | 3.169 | 7.9 | -0.052 | 2 | 7.134% | -4.8 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.051 | 650 | 189.4 | 0 | 203.7 | 446.3 | 454.1 | 7.8 | -0.89 | 8.752 | 2.992 | 2 | 7.087% | 454.2 | -1.2 | 9.177 | 3.169 | 7.9 | -0.052 | 2 | 7.134% | -4.8 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.051 | 650 | 189.4 | 0 | 203.7 | 446.3 | 454.1 | 7.8 | -0.89 | 8.752 | 2.992 | 2 | 7.087% | 454.2 | -1.2 | 9.177 | 3.169 | 7.9 | -0.052 | 2 | 7.134% | -4.8 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.051 | 751 | 488 | 31.8 | 141.1 | 578.1 | 589.1 | 11 | 0.3 | 10.785 | 3.758 | 2 | 5.806% | 592.2 | 0.4 | 13.732 | 4 | 14.1 | -0.052 | 2 | 4.618% | -3.48 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.051 | 50.2 | 24 | 0 | 25.1 | 25.1 | 26.5 | 1.4 | 0.33 | 1.071 | 0.312 | 2 | 3.068% | 28.8 | 0.5 | 3.212 | 0.333 | 3.7 | -0.052 | 2 | 1.184% | -0.57 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.051 | 170 | 65 | 0 | 83.3 | 86.7 | 95.4 | 8.7 | 0.59 | 8.062 | 0.888 | 2 | 1.664% | 95.9 | 0.8 | 8.332 | 0.945 | 9.2 | -0.052 | 2 | 1.605% | -0.8 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.051 | 56 | 22.5 | 0 | 31.4 | 24.6 | 25.1 | 0.5 | 0.38 | 0.192 | 0.348 | 0.552 | 9.577% | 28.7 | 0.5 | 3.648 | 0.372 | 4.1 | -0.052 | 2 | 1.191% | -0.5 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.051 | 304.7 | 118 | 65 | 47.5 | 192.2 | 195.1 | 2.9 | -0.64 | 3.604 | 1.252 | 2 | 8.941% | 195.3 | -0.9 | 4.074 | 1.333 | 3.1 | -0.052 | 2 | 8.528% | -5.26 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.051 | 48 | 15 | 0 | 5.2 | 42.8 | 43.7 | 0.9 | 0.36 | 0.571 | 0.298 | 1.914 | 4.565% | 44.6 | 0.5 | 1.278 | 0.319 | 1.8 | -0.052 | 2 | 2.327% | -2.01 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | SUB | FOSS | -0.051 | 932.6 | 360 | 0 | 45.3 | 887.3 | 899.7 | 12.4 | 3.09 | 9.316 | 4.869 | 1.913 | 6.395% | 901 | 4.3 | 9.312 | 5.157 | 13.7 | -0.052 | 1.806 | 5.902% | -5.5 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.051 | 932.6 | 360 | 0 | 45.3 | 887.3 | 899.7 | 12.4 | 3.09 | 9.316 | 4.869 | 1.913 | 6.395% | 901 | 4.3 | 9.312 | 5.157 | 13.7 | -0.052 | 1.806 | 5.902% | -5.5 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.051 | 932.6 | 360 | 0 | 45.3 | 887.3 | 899.7 | 12.4 | 3.09 | 9.316 | 4.869 | 1.913 | 6.395% | 901 | 4.3 | 9.312 | 5.157 | 13.7 | -0.052 | 1.806 | 5.902% | -5.5 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.051 | 932.6 | 360 | 0 | 45.3 | 887.3 | 899.7 | 12.4 | 3.09 | 9.316 | 4.869 | 1.913 | 6.395% | 901 | 4.3 | 9.312 | 5.157 | 13.7 | -0.052 | 1.806 | 5.902% | -5.5 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.051 | 262.8 | 130 | 0 | 44.2 | 218.6 | 222.2 | 3.6 | -0.84 | 4.418 | 1.373 | 2 | 6.213% | 221.2 | -1.2 | 3.794 | 1.461 | 2.6 | -0.052 | 2 | 8.771% | -7.14 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.051 | 527 | 250 | 0 | 112.1 | 414.9 | 443.2 | 28.3 | 13.85 | 14.394 | 0.787 | 2 | 1.585% | 452.3 | 19.3 | 18.066 | 1.001 | 37.4 | -0.052 | 2 | 1.223% | -0.94 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.051 | 780 | 305 | 70 | 83.4 | 626.6 | 634.1 | 7.5 | 0.69 | 6.783 | 3.71 | 1.828 | 8.844% | 633.7 | 1 | 6.153 | 3.948 | 7.1 | -0.052 | 1.558 | 9.525% | -7.5 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.032 | 544 | 275 | 0 | 150.3 | 393.7 | 407.6 | 13.9 | 2.95 | 10.926 | 4.227 | 2 | 2.089% | 408.6 | 4.1 | 10.745 | 3.817 | 14.9 | -0.029 | 2 | 1.767% | -1.41 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.032 | 149.8 | 0 | 0 | 6.6 | 143.2 | 142.8 | -0.4 | -0.7 | 0.228 | 1.59 | 0.143 | -20.04% | 144.7 | -1 | 2.43 | 1.446 | 1.5 | -0.029 | 1.681 | 4.846% | -5.07 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.032 | 540 | 336 | 10 | 188.1 | 341.9 | 347.5 | 5.6 | 0.06 | 5.458 | 4.118 | 1.325 | 5.148% | 348.5 | 0.1 | 6.475 | 3.719 | 6.6 | -0.029 | 1.741 | 3.959% | -2.76 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.032 | 478 | 300 | 0 | 56.7 | 421.3 | 428.9 | 7.6 | 3.17 | 4.479 | 3.714 | 1.206 | 3.358% | 431.1 | 4.4 | 5.402 | 3.354 | 9.8 | -0.029 | 1.611 | 2.36% | -2.29 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.032 | 254 | 93 | 56 | 98.6 | 99.4 | 105.5 | 6.1 | -0.06 | 6.181 | 1.538 | 2 | 2.225% | 105.7 | -0.1 | 6.361 | 1.389 | 6.3 | -0.029 | 2 | 1.953% | -0.84 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.032 | 211 | 146 | 0 | 63.5 | 147.5 | 152.8 | 5.3 | -0.52 | 5.797 | 1.639 | 2 | 2.129% | 152.7 | -0.7 | 5.905 | 1.48 | 5.2 | -0.029 | 2 | 1.967% | -1.51 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.032 | 185 | 105 | 5 | 73.9 | 106.1 | 108 | 1.9 | -0.12 | 2.055 | 1.399 | 1.47 | 5.208% | 108.5 | -0.2 | 2.614 | 1.263 | 2.4 | -0.029 | 2 | 3.737% | -2.35 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.032 | 560 | 135 | 0 | 365 | 195 | 207.5 | 12.5 | 2.87 | 9.603 | 4.458 | 2 | 2.392% | 209.7 | 4 | 10.698 | 4.053 | 14.7 | -0.029 | 2 | 1.843% | -0.71 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.032 | 417 | 125 | 0 | 175.5 | 241.5 | 247.4 | 5.9 | 0.63 | 5.283 | 3.195 | 1.653 | 3.774% | 245.7 | 0.9 | 3.359 | 2.905 | 4.2 | -0.029 | 1.156 | 4.806% | -3.06 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.032 | 1115 | 420 | 170 | 25.5 | 919.5 | 939.2 | 19.7 | 1.12 | 18.605 | 7.343 | 2 | 3.02% | 939.7 | 1.6 | 18.653 | 6.631 | 20.2 | -0.029 | 2 | 2.669% | -2.43 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.032 | 617 | 313 | 118 | 172.3 | 326.7 | 335.9 | 9.2 | 1.9 | 7.318 | 3.877 | 1.887 | 3.58% | 340 | 2.6 | 10.643 | 3.501 | 13.3 | -0.029 | 2 | 2.244% | -1.31 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.032 | 645 | 300 | 0 | 337.8 | 307.2 | 315.7 | 8.5 | 0.53 | 8.024 | 5.998 | 1.338 | 4.05% | 315.2 | 0.7 | 7.275 | 5.453 | 8 | -0.029 | 1.334 | 3.9% | -2.04 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.032 | 651 | 508 | 0 | 99.2 | 551.8 | 560.6 | 8.8 | 0.97 | 7.885 | 5.058 | 1.559 | 3.949% | 562.3 | 1.3 | 9.187 | 4.568 | 10.5 | -0.029 | 2 | 2.999% | -2.8 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.032 | 105 | 12 | 0 | 92.2 | 12.8 | 14 | 1.2 | 0.01 | 1.207 | 1.104 | 1.094 | 4.69% | 13.5 | 0 | 0.745 | 1.004 | 0.7 | -0.029 | 0.743 | 7.29% | -0.93 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.032 | 55 | 21 | 0 | 31.2 | 23.8 | 26.9 | 3.1 | 0.59 | 2.558 | 0.427 | 2 | 0.9554% | 29.1 | 0.8 | 4.44 | 0.386 | 5.3 | -0.029 | 2 | 0.5069% | -0.23 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.032 | 534 | 337.8 | 0 | 159.2 | 374.8 | 390.3 | 15.5 | 5.45 | 10.005 | 4.149 | 2 | 1.839% | 392.3 | 7.6 | 9.892 | 3.747 | 17.5 | -0.029 | 2 | 1.476% | -1.14 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.032 | 520.9 | 155.4 | 0 | 272.9 | 248 | 261.1 | 13.1 | 1.27 | 11.785 | 4.042 | 2 | 2.123% | 259.6 | 1.8 | 9.785 | 3.675 | 11.6 | -0.029 | 2 | 2.173% | -1.14 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.032 | 520.9 | 155.4 | 0 | 272.9 | 248 | 261.1 | 13.1 | 1.27 | 11.785 | 4.042 | 2 | 2.123% | 259.6 | 1.8 | 9.785 | 3.675 | 11.6 | -0.029 | 2 | 2.173% | -1.14 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.032 | 600.2 | 155.3 | 0 | 263.3 | 336.9 | 347.7 | 10.8 | 0.21 | 10.63 | 4.815 | 2 | 2.967% | 347.9 | 0.3 | 10.785 | 4.378 | 11 | -0.029 | 2 | 2.64% | -1.63 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.032 | 600.2 | 155.3 | 0 | 263.3 | 336.9 | 347.7 | 10.8 | 0.21 | 10.63 | 4.815 | 2 | 2.967% | 347.9 | 0.3 | 10.785 | 4.378 | 11 | -0.029 | 2 | 2.64% | -1.63 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.032 | 404.5 | 180.3 | 0 | 158.4 | 246.1 | 250.5 | 4.4 | -0.94 | 5.409 | 3.849 | 1.405 | 4.909% | 251.2 | -1.3 | 6.494 | 3.5 | 5.1 | -0.029 | 1.856 | 3.839% | -2.57 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.032 | 242 | 126 | 10 | 104.1 | 127.9 | 131 | 3.1 | 0 | 3.131 | 1.803 | 1.737 | 4.173% | 130.7 | 0 | 2.8 | 1.628 | 2.8 | -0.029 | 1.72 | 4.188% | -2.43 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.032 | 904.9 | 461 | 141 | 35.3 | 728.6 | 744.5 | 15.9 | 2.53 | 13.424 | 5.936 | 2 | 3.037% | 749.3 | 3.5 | 17.183 | 5.36 | 20.7 | -0.029 | 2 | 2.114% | -1.88 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.032 | 513 | 348 | 44 | 10.9 | 458.1 | 462.4 | 4.3 | -0.24 | 4.555 | 3.644 | 1.25 | 6.369% | 463.2 | -0.3 | 5.457 | 3.291 | 5.1 | -0.029 | 1.658 | 4.867% | -4.79 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.032 | 205.6 | 0 | 0 | 5.8 | 199.8 | 199.4 | -0.4 | -0.53 | 0.122 | 2.183 | 0.056 | -27.48% | 200 | -0.7 | 0.939 | 1.984 | 0.2 | -0.029 | 0.473 | 49.83% | -53.14 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.032 | 609.9 | 260 | 126.7 | 161.1 | 322.1 | 328.9 | 6.8 | 0.01 | 6.851 | 3.754 | 1.825 | 4.788% | 337.4 | 0 | 15.353 | 3.39 | 15.3 | -0.029 | 2 | 1.929% | -1.12 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.032 | 610.1 | 260 | 126.3 | 162.1 | 321.7 | 328.2 | 6.5 | -0.5 | 6.972 | 3.759 | 1.855 | 5.01% | 335.4 | -0.7 | 14.457 | 3.395 | 13.7 | -0.029 | 2 | 2.154% | -1.25 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.032 | 767 | 260 | 0 | 502.1 | 264.9 | 276.8 | 11.9 | 0.97 | 10.906 | 5.25 | 2 | 3.44% | 275.7 | 1.4 | 9.488 | 4.773 | 10.8 | -0.029 | 1.988 | 3.435% | -1.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.032 | 102 | 68 | 0 | 31.9 | 70.1 | 73.2 | 3.1 | 0 | 3.016 | 0.939 | 2 | 1.764% | 73.7 | 0 | 3.519 | 0.841 | 3.6 | -0.029 | 2 | 1.377% | -1.03 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.032 | 523 | 344 | 0 | 134.6 | 388.4 | 408.4 | 20 | 6.08 | 13.919 | 4.064 | 2 | 1.396% | 413.4 | 8.5 | 16.565 | 3.67 | 25 | -0.029 | 2 | 1.012% | -0.83 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.032 | 450 | 220 | 0 | 221.2 | 228.8 | 240 | 11.2 | 1.47 | 9.753 | 4.776 | 2 | 2.145% | 239.8 | 2 | 8.978 | 4.342 | 11 | -0.029 | 2 | 1.98% | -1.11 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.032 | 450 | 220 | 0 | 221.2 | 228.8 | 238.6 | 9.8 | 1.33 | 8.522 | 4.776 | 1.784 | 2.452% | 239.1 | 1.9 | 8.51 | 4.342 | 10.3 | -0.029 | 1.96 | 2.114% | -1.18 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.032 | 820 | 280 | 0 | 538.7 | 281.3 | 287.3 | 6 | -0.41 | 6.37 | 8.703 | 0.732 | 7.294% | 285 | -0.6 | 4.224 | 7.913 | 3.7 | -0.029 | 0.534 | 10.72% | -4.05 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.032 | 645.9 | 250 | 154.5 | 227.5 | 263.9 | 274 | 10.1 | -0.41 | 10.516 | 3.818 | 2 | 3.413% | 272.6 | -0.6 | 9.286 | 3.448 | 8.7 | -0.029 | 2 | 3.592% | -1.61 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.032 | 650 | 189.5 | 0 | 458.4 | 191.6 | 200.8 | 9.2 | 0.5 | 8.781 | 3.908 | 2 | 3.771% | 197.3 | 0.7 | 5.056 | 3.553 | 5.7 | -0.029 | 1.423 | 5.517% | -1.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.032 | 650 | 189.5 | 0 | 458.4 | 191.6 | 200.8 | 9.2 | 0.5 | 8.781 | 3.908 | 2 | 3.771% | 197.3 | 0.7 | 5.056 | 3.553 | 5.7 | -0.029 | 1.423 | 5.517% | -1.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.032 | 650 | 189.5 | 0 | 458.4 | 191.6 | 200.8 | 9.2 | 0.5 | 8.781 | 3.908 | 2 | 3.771% | 197.3 | 0.7 | 5.056 | 3.553 | 5.7 | -0.029 | 1.423 | 5.517% | -1.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.032 | 650 | 189.5 | 0 | 458.4 | 191.6 | 200.8 | 9.2 | 0.5 | 8.781 | 3.908 | 2 | 3.771% | 197.3 | 0.7 | 5.056 | 3.553 | 5.7 | -0.029 | 1.423 | 5.517% | -1.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.032 | 650 | 189.5 | 0 | 458.4 | 191.6 | 200.8 | 9.2 | 0.5 | 8.781 | 3.908 | 2 | 3.771% | 197.3 | 0.7 | 5.056 | 3.553 | 5.7 | -0.029 | 1.423 | 5.517% | -1.79 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.032 | 738.2 | 463 | 50.9 | 197.7 | 489.6 | 506.5 | 16.9 | 4.54 | 12.318 | 5.34 | 2 | 2.331% | 515.5 | 6.3 | 19.543 | 4.822 | 25.9 | -0.029 | 2 | 1.379% | -1.01 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.032 | 734.3 | 453.1 | 48.8 | 200.1 | 485.4 | 503.4 | 18 | 4.78 | 13.262 | 5.326 | 2 | 2.177% | 514.9 | 6.7 | 22.9 | 4.81 | 29.5 | -0.029 | 2 | 1.204% | -0.88 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.032 | 55.2 | 0 | 0 | 46.9 | 8.3 | 9 | 0.7 | -0.55 | 1.272 | 0.586 | 2 | 4.246% | 8.9 | -0.8 | 1.391 | 0.532 | 0.6 | -0.029 | 2 | 4.494% | -0.69 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.032 | 65.7 | 0 | 0 | 56.6 | 9.1 | 9.4 | 0.3 | 0.15 | 0.208 | 0.697 | 0.299 | 11.77% | 9.3 | 0.2 | 0.033 | 0.634 | 0.2 | -0.029 | 0.053 | 16.02% | -2.28 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.032 | 54.8 | 0 | 0 | 50.1 | 4.7 | 5.5 | 0.8 | -0.11 | 0.911 | 0.582 | 1.567 | 3.689% | 5 | -0.1 | 0.507 | 0.529 | 0.3 | -0.029 | 0.959 | 8.923% | -0.74 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.032 | 66 | 0 | 0 | 54.4 | 11.6 | 12.3 | 0.7 | -0.72 | 1.427 | 0.701 | 2 | 5.069% | 12.9 | -1 | 2.312 | 0.637 | 1.3 | -0.029 | 2 | 2.476% | -0.45 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.032 | 517.9 | 273 | 0 | 184.8 | 333.1 | 364.2 | 31.1 | 8.44 | 22.652 | 4.024 | 2 | 0.8891% | 376.9 | 11.7 | 32.045 | 3.634 | 43.8 | -0.029 | 2 | 0.5721% | -0.4 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.032 | 249 | 178 | 10 | 57.8 | 181.2 | 183.1 | 1.9 | -0.12 | 2.055 | 1.857 | 1.106 | 7.004% | 183.8 | -0.2 | 2.807 | 1.677 | 2.6 | -0.029 | 1.674 | 4.64% | -3.71 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.032 | 56 | 22.5 | 0 | 29.1 | 26.9 | 31 | 4.1 | 0.68 | 3.444 | 0.516 | 2 | 0.7354% | 35 | 0.9 | 7.196 | 0.462 | 8.1 | -0.029 | 2 | 0.3377% | -0.17 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.032 | 56 | 22.5 | 0 | 28.9 | 27.1 | 31.2 | 4.1 | -0.01 | 4.095 | 0.516 | 2 | 0.7354% | 35.6 | 0 | 8.48 | 0.462 | 8.5 | -0.029 | 2 | 0.3218% | -0.17 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.032 | 289.3 | 118 | 65 | 24.1 | 200.2 | 205.4 | 5.2 | 0.26 | 4.94 | 1.743 | 2 | 2.973% | 204.7 | 0.4 | 4.077 | 1.574 | 4.5 | -0.029 | 2 | 3.114% | -2.37 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.032 | 81 | 62 | 0 | 18.7 | 62.3 | 63.3 | 1 | 0.03 | 1.016 | 0.746 | 1.362 | 4.348% | 63.3 | 0 | 0.953 | 0.668 | 1 | -0.029 | 1.427 | 3.943% | -3.29 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.032 | 81 | 62 | 0 | 17.5 | 63.5 | 64.2 | 0.7 | -0.14 | 0.851 | 0.746 | 1.14 | 6.212% | 63.9 | -0.2 | 0.583 | 0.668 | 0.4 | -0.029 | 0.873 | 9.858% | -8.4 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.032 | 669 | 156 | 0 | 450.7 | 218.3 | 229 | 10.7 | 0.84 | 9.927 | 6.491 | 1.529 | 3.337% | 230.4 | 1.2 | 10.926 | 5.901 | 12.1 | -0.029 | 1.851 | 2.675% | -0.96 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.032 | 663 | 156 | 0 | 418 | 245 | 258.4 | 13.4 | 0.76 | 12.689 | 6.362 | 1.995 | 2.641% | 260.7 | 1.1 | 14.603 | 5.784 | 15.7 | -0.029 | 2 | 2.043% | -0.83 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.032 | 516 | 159 | 0 | 241.9 | 274.1 | 281.6 | 7.5 | 0.54 | 6.968 | 4.812 | 1.448 | 3.673% | 281.2 | 0.7 | 6.382 | 4.376 | 7.1 | -0.029 | 1.459 | 3.517% | -2.05 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.032 | 1086 | 379 | 152 | 434.9 | 499.1 | 518.1 | 19 | 4.02 | 14.949 | 7.257 | 2 | 3.05% | 527.2 | 5.6 | 22.504 | 6.553 | 28.1 | -0.029 | 2 | 1.869% | -0.95 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.084 | 56 | 30 | 0 | 25.9 | 30.1 | 31.5 | 1.4 | 0.38 | 1.032 | 0.921 | 1.121 | 5.62% | 31.3 | 0.5 | 0.675 | 0.884 | 1.2 | -0.082 | 0.763 | 6.401% | -3.49 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 56 | 30 | 0 | 25.8 | 30.2 | 33.4 | 3.2 | 0.27 | 2.988 | 0.921 | 2 | 2.459% | 37.8 | 0.4 | 7.321 | 0.884 | 7.6 | -0.082 | 2 | 1.011% | -0.55 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.084 | 189.3 | 85 | 0 | 78.8 | 110.5 | 118.3 | 7.8 | -0.37 | 8.176 | 3.112 | 2 | 3.401% | 124.7 | -0.5 | 14.74 | 2.987 | 14.2 | -0.082 | 2 | 1.824% | -1.09 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.084 | 478 | 300 | 0 | 14.1 | 463.9 | 475.8 | 11.9 | 0.44 | 11.457 | 6.664 | 1.719 | 5.626% | 476 | 0.6 | 11.428 | 6.418 | 12.1 | -0.082 | 1.781 | 5.401% | -5.37 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 208.5 | 147.5 | 0 | 40.1 | 168.4 | 180.6 | 12.2 | 0.48 | 11.692 | 2.907 | 2 | 2.395% | 181.1 | 0.7 | 12.011 | 2.799 | 12.7 | -0.082 | 2 | 2.246% | -1.85 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.084 | 560 | 135 | 0 | 116.5 | 443.5 | 451.6 | 8.1 | -6.34 | 14.404 | 9.176 | 1.57 | 9.683% | 456.2 | -8.8 | 21.506 | 8.847 | 12.7 | -0.082 | 2 | 6.028% | -4.89 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.084 | 765 | 300 | 0 | 29.3 | 735.7 | 749.4 | 13.7 | -4.33 | 17.983 | 13.62 | 1.32 | 7.82% | 748.9 | -6 | 19.193 | 13.132 | 13.2 | -0.082 | 1.462 | 7.923% | -7.8 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.084 | 420 | 125 | 0 | 60.6 | 359.4 | 367.5 | 8.1 | 0.15 | 7.956 | 6.032 | 1.319 | 7.263% | 365.5 | 0.2 | 5.887 | 5.816 | 6.1 | -0.082 | 1.012 | 9.414% | -8.24 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.084 | 417 | 125 | 0 | 112.8 | 304.2 | 309.1 | 4.9 | -3.85 | 8.67 | 5.805 | 1.493 | 11.92% | 305.4 | -5.4 | 6.478 | 5.598 | 1.2 | -0.082 | 1.157 | 47.52% | -35.47 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 370 | 70 | 0 | 105.8 | 264.2 | 264.7 | 0.5 | -2.69 | 3.145 | 6.003 | 0.524 | 103.7% | 261.7 | -3.7 | 1.255 | 5.788 | -2.5 | -0.082 | 0.217 | -20.24% | 14.78 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 749 | 93 | 0 | 462.4 | 286.6 | 292.3 | 5.7 | -7.23 | 12.883 | 8.867 | 1.453 | 18.41% | 290.6 | -10.1 | 14.05 | 8.408 | 4 | -0.082 | 1.671 | 25.61% | -10.02 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 518 | 382 | 0 | 135.8 | 382.2 | 390.7 | 8.5 | 0.36 | 8.091 | 7.222 | 1.12 | 8.535% | 391.5 | 0.5 | 8.791 | 6.955 | 9.3 | -0.082 | 1.264 | 7.615% | -5.75 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 328 | 147 | 61 | 59.8 | 207.2 | 217.7 | 10.5 | -0.77 | 11.281 | 3.722 | 2 | 4.376% | 216.4 | -1.1 | 10.282 | 3.585 | 9.2 | -0.082 | 2 | 4.876% | -3.15 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 632 | 508 | 22 | 100.5 | 509.5 | 525.4 | 15.9 | 0.7 | 15.199 | 8.505 | 1.787 | 5.567% | 527.1 | 1 | 16.558 | 8.19 | 17.6 | -0.082 | 2 | 4.909% | -4.05 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.084 | 322 | 50 | 0 | 81.3 | 240.7 | 251.7 | 11 | -2.77 | 13.783 | 4.459 | 2 | 4.101% | 250.4 | -3.9 | 13.583 | 4.3 | 9.7 | -0.082 | 2 | 4.54% | -3.47 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.084 | 142 | 90 | 0 | 50.1 | 91.9 | 100.5 | 8.6 | 0 | 8.604 | 2.335 | 2 | 2.315% | 105.7 | 0 | 13.746 | 2.241 | 13.8 | -0.082 | 2 | 1.408% | -0.93 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.084 | 335 | 146 | 11 | 30.3 | 293.7 | 302.5 | 8.8 | 0.42 | 8.404 | 4.517 | 1.86 | 5.333% | 304.1 | 0.6 | 9.827 | 4.35 | 10.4 | -0.082 | 2 | 4.405% | -3.95 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 212 | 130 | 9.7 | 39.8 | 162.5 | 170.9 | 8.4 | -0.17 | 8.526 | 2.82 | 2 | 3.537% | 171 | -0.2 | 8.674 | 2.715 | 8.5 | -0.082 | 2 | 3.412% | -2.67 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.084 | 594.6 | 155.4 | 0 | 129.2 | 465.4 | 478.5 | 13.1 | 2.34 | 10.81 | 7.969 | 1.356 | 6.357% | 479 | 3.3 | 10.326 | 7.684 | 13.6 | -0.082 | 1.344 | 5.977% | -4.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.084 | 594.6 | 155.4 | 0 | 129.2 | 465.4 | 478.5 | 13.1 | 2.34 | 10.81 | 7.969 | 1.356 | 6.357% | 479 | 3.3 | 10.326 | 7.684 | 13.6 | -0.082 | 1.344 | 5.977% | -4.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.084 | 599.2 | 155.3 | 0 | 92.8 | 506.4 | 520.5 | 14.1 | -0.42 | 14.481 | 7.915 | 1.829 | 5.952% | 520.6 | -0.6 | 14.734 | 7.632 | 14.2 | -0.082 | 1.931 | 5.769% | -4.99 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.084 | 599.2 | 155.3 | 0 | 92.8 | 506.4 | 520.5 | 14.1 | -0.42 | 14.481 | 7.915 | 1.829 | 5.952% | 520.6 | -0.6 | 14.734 | 7.632 | 14.2 | -0.082 | 1.931 | 5.769% | -4.99 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 915 | 461 | 69 | 78.4 | 767.6 | 786.9 | 19.3 | -3.16 | 22.497 | 11.795 | 1.907 | 6.639% | 796.7 | -4.4 | 33.475 | 11.358 | 29.1 | -0.082 | 2 | 4.298% | -3.69 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 914.6 | 461 | 99 | 65.9 | 749.7 | 773.2 | 23.5 | 0.31 | 23.284 | 11.372 | 2 | 5.45% | 788.9 | 0.4 | 38.836 | 10.951 | 39.2 | -0.082 | 2 | 3.189% | -2.68 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | STM | -0.084 | 326.1 | 56.1 | 0 | 148.2 | 177.9 | 186.7 | 8.8 | 0.01 | 8.804 | 5.83 | 1.51 | 5.191% | 185.6 | 0 | 7.688 | 5.622 | 7.7 | -0.082 | 1.368 | 5.792% | -3.23 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | COGN | -0.084 | 243 | 150 | 21 | 35 | 187 | 193.1 | 6.1 | 0.21 | 5.851 | 3.585 | 1.632 | 5.582% | 192.7 | 0.3 | 5.384 | 3.457 | 5.7 | -0.082 | 1.557 | 5.831% | -4.59 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.084 | 395 | 100 | 0 | 293.4 | 101.6 | 132.9 | 31.3 | 0.78 | 30.607 | 3.358 | 2 | 1.769% | 119.2 | 1.1 | 16.594 | 3.184 | 17.6 | -0.082 | 2 | 3.07% | -0.8 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 280 | 165 | 40 | 11.7 | 228.3 | 231.4 | 3.1 | -0.3 | 3.434 | 3.346 | 1.026 | 12.65% | 231.3 | -0.4 | 3.402 | 3.222 | 3 | -0.082 | 1.056 | 12.77% | -10.64 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 250 | 182 | 0 | 38 | 212 | 216.8 | 4.8 | -1.95 | 6.784 | 3.485 | 1.946 | 7.298% | 219.5 | -2.7 | 10.209 | 3.356 | 7.5 | -0.082 | 2 | 4.559% | -3.95 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 515 | 336 | 9.9 | 39.6 | 465.5 | 476.8 | 11.3 | 0.61 | 10.669 | 7.042 | 1.515 | 6.383% | 481.7 | 0.9 | 15.369 | 6.782 | 16.2 | -0.082 | 2 | 4.346% | -4.02 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 508.1 | 310.2 | 5.3 | 19.7 | 483.1 | 490.5 | 7.4 | 0.19 | 7.222 | 7.011 | 1.03 | 9.617% | 490.5 | 0.3 | 7.12 | 6.751 | 7.4 | -0.082 | 1.055 | 9.388% | -9.14 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.084 | 122 | 15 | 0 | 106.7 | 15.3 | 20.6 | 5.3 | -0.11 | 5.357 | 1.834 | 2 | 3.228% | 19.8 | -0.2 | 4.661 | 1.768 | 4.5 | -0.082 | 2 | 3.711% | -0.47 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.084 | 245 | 150 | 21 | 10.9 | 213.1 | 217.3 | 4.2 | 0.32 | 3.838 | 3.325 | 1.154 | 8.173% | 217.8 | 0.5 | 4.216 | 3.206 | 4.7 | -0.082 | 1.315 | 7.13% | -6.34 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.084 | 240 | 150 | 21 | 42.8 | 176.2 | 181.8 | 5.6 | 0.21 | 5.344 | 2.992 | 1.786 | 6.005% | 182.2 | 0.3 | 5.654 | 2.884 | 6 | -0.082 | 1.96 | 5.471% | -4.11 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.084 | 245 | 150 | 21 | 11.6 | 212.4 | 216.3 | 3.9 | 0.28 | 3.641 | 3.32 | 1.097 | 8.802% | 217 | 0.4 | 4.188 | 3.201 | 4.6 | -0.082 | 1.308 | 7.285% | -6.46 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.084 | 254 | 150 | 21 | 10.8 | 222.2 | 227.2 | 5 | 0.28 | 4.666 | 3.411 | 1.368 | 7.118% | 227.6 | 0.4 | 4.946 | 3.289 | 5.4 | -0.082 | 1.504 | 6.434% | -5.76 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.084 | 256 | 110 | 21 | 10.6 | 224.4 | 229.3 | 4.9 | 0.27 | 4.643 | 3.458 | 1.343 | 7.32% | 229.8 | 0.4 | 4.961 | 3.334 | 5.4 | -0.082 | 1.488 | 6.484% | -5.81 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.084 | 208 | 40 | 0 | 167 | 41 | 48 | 7 | -1.46 | 8.464 | 3.71 | 2 | 4.164% | 49.9 | -2 | 11.005 | 3.577 | 8.9 | -0.082 | 2 | 3.197% | -0.64 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | GT | -0.084 | 107 | 35 | 0 | 71.3 | 35.7 | 40 | 4.3 | 0.18 | 4.149 | 1.759 | 2 | 3.49% | 44.3 | 0.3 | 8.356 | 1.689 | 8.6 | -0.082 | 2 | 1.704% | -0.58 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.084 | 643.4 | 250 | 154.8 | 13.4 | 475.2 | 493 | 17.8 | -0.1 | 17.887 | 6.812 | 2 | 5.062% | 496.5 | -0.1 | 21.484 | 6.56 | 21.3 | -0.082 | 2 | 4.13% | -3.12 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 709 | 444 | 61.3 | 197.2 | 450.5 | 466.3 | 15.8 | -1.36 | 17.201 | 9.03 | 1.905 | 6.284% | 470.9 | -1.9 | 22.288 | 8.696 | 20.4 | -0.082 | 2 | 4.751% | -3.09 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.084 | 49.9 | 24 | 0 | 25.8 | 24.1 | 25.8 | 1.7 | 0.12 | 1.613 | 0.82 | 1.968 | 4.126% | 27.9 | 0.2 | 3.628 | 0.787 | 3.8 | -0.082 | 2 | 1.802% | -0.88 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 391.4 | 210 | 5.2 | 138.8 | 247.4 | 250.3 | 2.9 | -7.73 | 10.66 | 5.384 | 1.98 | 18.9% | 249.5 | -10.8 | 12.855 | 5.185 | 2.1 | -0.082 | 2 | 25.49% | -16.48 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 513 | 341 | 26 | 39.8 | 447.2 | 453.9 | 6.7 | 0.12 | 6.514 | 6.79 | 0.959 | 10.72% | 456.9 | 0.2 | 9.493 | 6.538 | 9.7 | -0.082 | 1.452 | 7.231% | -6.45 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.084 | 55.9 | 22.5 | 0 | 33.4 | 22.5 | 24.6 | 2.1 | -0.05 | 2.167 | 0.919 | 2 | 3.74% | 25.9 | -0.1 | 3.485 | 0.882 | 3.4 | -0.082 | 2 | 2.255% | -0.92 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 56 | 22.5 | 0 | 33.4 | 22.6 | 24.7 | 2.1 | 0.02 | 2.119 | 0.92 | 2 | 3.747% | 29.8 | 0 | 7.17 | 0.883 | 7.2 | -0.082 | 2 | 1.067% | -0.44 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.084 | 55.8 | 22.5 | 0 | 33.3 | 22.5 | 24.4 | 1.9 | -0.02 | 1.886 | 0.917 | 2 | 4.126% | 26.6 | 0 | 4.045 | 0.88 | 4.1 | -0.082 | 2 | 1.867% | -0.76 | 0.017 | 0.05 | 6.284% | 5.784%
Wind | WND | WIND | -0.084 | 150.4 | 0 | 0 | 60.1 | 90.3 | 93 | 2.7 | -0.24 | 2.988 | 2.771 | 1.078 | 7.809% | 92.8 | -0.3 | 2.843 | 2.672 | 2.5 | -0.082 | 1.064 | 8.233% | -5.05 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.084 | 98.1 | 0 | 0 | 36.7 | 61.4 | 63.1 | 1.7 | -0.18 | 1.906 | 1.808 | 1.055 | 8.095% | 62.8 | -0.2 | 1.632 | 1.743 | 1.4 | -0.082 | 0.936 | 9.597% | -6.12 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | COGN | -0.084 | 81 | 57 | 0 | 23.5 | 57.5 | 59.5 | 2 | -0.01 | 1.957 | 1.332 | 1.47 | 5.684% | 59.1 | 0 | 1.567 | 1.278 | 1.6 | -0.082 | 1.226 | 6.936% | -5.01 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 288 | 165 | 35 | 84.9 | 168.1 | 176.8 | 8.7 | 0.03 | 8.613 | 3.527 | 2 | 4.638% | 177.3 | 0 | 9.113 | 3.397 | 9.2 | -0.082 | 2 | 4.281% | -2.55 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.084 | 527 | 93 | 0 | 432.2 | 94.8 | 101.4 | 6.6 | -0.83 | 7.466 | 4.174 | 1.789 | 11.19% | 111.4 | -1.1 | 17.829 | 3.958 | 16.6 | -0.082 | 2 | 4.342% | -0.8 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.084 | 691 | 340 | 40 | 165.3 | 485.7 | 511 | 25.3 | 0 | 25.275 | 9.077 | 2 | 3.825% | 509.2 | 0 | 23.443 | 8.741 | 23.5 | -0.082 | 2 | 4.02% | -2.89 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.084 | 1082 | 379 | 152 | 170.7 | 759.3 | 785.8 | 26.5 | 1.55 | 25 | 12.966 | 1.928 | 5.717% | 783.8 | 2.2 | 22.406 | 12.486 | 24.5 | -0.082 | 1.795 | 6.037% | -4.34 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.076 | 145.3 | 0 | 0 | 14.3 | 131 | 137.2 | 6.2 | -2.32 | 8.499 | 2.023 | 2 | 2.973% | 138.7 | -3.2 | 10.861 | 1.76 | 7.7 | -0.07 | 2 | 2.205% | -2.15 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.076 | 478 | 300 | 0 | 170.9 | 307.1 | 316.8 | 9.7 | -1.33 | 10.992 | 5.011 | 2 | 6.245% | 318.5 | -1.8 | 13.248 | 4.333 | 11.4 | -0.07 | 2 | 4.894% | -3.41 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.076 | 124.3 | 0 | 0 | 42.5 | 81.8 | 83.7 | 1.9 | -0.18 | 2.101 | 1.731 | 1.214 | 8.302% | 83.8 | -0.2 | 2.289 | 1.506 | 2 | -0.07 | 1.52 | 7.265% | -5.17 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.076 | 188 | 120 | 5 | 60.5 | 122.5 | 124.2 | 1.7 | 0.3 | 1.433 | 1.918 | 0.747 | 14.02% | 124.9 | 0.4 | 1.99 | 1.659 | 2.4 | -0.07 | 1.199 | 9.151% | -6.45 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.076 | 560 | 135 | 0 | 421.5 | 138.5 | 144.6 | 6.1 | -0.13 | 6.185 | 5.85 | 1.057 | 11.63% | 149.3 | -0.2 | 10.954 | 5.089 | 10.8 | -0.07 | 2 | 6.052% | -1.62 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 760 | 300 | 0 | 449.3 | 310.7 | 321.3 | 10.6 | -0.27 | 10.829 | 7.622 | 1.421 | 9.084% | 323.5 | -0.4 | 13.135 | 6.63 | 12.8 | -0.07 | 1.981 | 6.929% | -3.07 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 417 | 125 | 0 | 291.2 | 125.8 | 131.7 | 5.9 | -1.99 | 7.897 | 4.069 | 1.94 | 8.957% | 129.6 | -2.8 | 6.597 | 3.54 | 3.8 | -0.07 | 1.864 | 12.81% | -4.19 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 374 | 150 | 109 | 113.7 | 151.3 | 157.1 | 5.8 | -0.6 | 6.397 | 2.778 | 2 | 8.173% | 159.4 | -0.8 | 8.937 | 2.402 | 8.1 | -0.07 | 2 | 5.39% | -2.36 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 466 | 356 | 20 | 73.3 | 372.7 | 380.1 | 7.4 | -0.44 | 7.787 | 4.675 | 1.666 | 7.98% | 380.5 | -0.6 | 8.357 | 4.043 | 7.8 | -0.07 | 2 | 6.974% | -6.05 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 554 | 320 | 59 | 151.5 | 343.5 | 352.6 | 9.1 | 1.06 | 7.973 | 5.189 | 1.536 | 7.714% | 354.3 | 1.5 | 9.301 | 4.487 | 10.8 | -0.07 | 2 | 5.987% | -4.03 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 48 | 10 | 0 | 33.9 | 14.1 | 15.8 | 1.7 | 0.3 | 1.485 | 0.503 | 2 | 3.593% | 25.4 | 0.4 | 10.902 | 0.435 | 11.3 | -0.07 | 2 | 0.4981% | -0.16 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.076 | 599.2 | 155.3 | 0 | 437.4 | 161.8 | 171.3 | 9.5 | -0.42 | 9.897 | 5.89 | 1.68 | 7.992% | 172.3 | -0.6 | 11.025 | 5.123 | 10.5 | -0.07 | 2 | 6.66% | -1.95 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 599.2 | 155.3 | 0 | 437.4 | 161.8 | 171.3 | 9.5 | -0.42 | 9.897 | 5.89 | 1.68 | 7.992% | 172.3 | -0.6 | 11.025 | 5.123 | 10.5 | -0.07 | 2 | 6.66% | -1.95 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 482 | 295 | 10 | 169.9 | 302.1 | 306.5 | 4.4 | -0.06 | 4.415 | 4.948 | 0.892 | 13.88% | 305 | -0.1 | 2.982 | 4.279 | 2.9 | -0.07 | 0.697 | 19.4% | -13.19 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 254 | 172 | 35 | 44.6 | 174.4 | 178.5 | 4.1 | -0.09 | 4.13 | 2.296 | 1.799 | 7.854% | 178.7 | -0.1 | 4.462 | 1.985 | 4.3 | -0.07 | 2 | 6.898% | -5.13 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.076 | 103.6 | 0 | 0 | 54.6 | 49 | 50.7 | 1.7 | -0.02 | 1.698 | 1.443 | 1.177 | 7.736% | 50.3 | 0 | 1.237 | 1.255 | 1.3 | -0.07 | 0.986 | 9.319% | -4.75 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.076 | 199.5 | 0 | 0 | 86.4 | 113.1 | 117.6 | 4.5 | 0.03 | 4.542 | 2.779 | 1.635 | 5.622% | 116.1 | 0 | 3.018 | 2.417 | 3 | -0.07 | 1.249 | 7.768% | -4.77 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.076 | 125.3 | 0 | 0 | 15.6 | 109.7 | 111.2 | 1.5 | 0.59 | 0.939 | 1.745 | 0.538 | 10.6% | 112.9 | 0.8 | 2.386 | 1.518 | 3.2 | -0.07 | 1.572 | 4.577% | -4.33 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.076 | 207.7 | 0 | 0 | 80.8 | 126.9 | 131.3 | 4.4 | -0.06 | 4.422 | 2.893 | 1.528 | 5.986% | 130.1 | -0.1 | 3.282 | 2.517 | 3.2 | -0.07 | 1.304 | 7.581% | -5.01 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.076 | 106.7 | 0 | 0 | 50.8 | 55.9 | 56.9 | 1 | 0 | 0.989 | 1.486 | 0.666 | 13.54% | 57.1 | 0 | 1.232 | 1.292 | 1.2 | -0.07 | 0.953 | 10.4% | -5.88 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.076 | 615 | 260 | 133.2 | 220.3 | 261.5 | 262.6 | 1.1 | 0.27 | 0.898 | 5.05 | 0.178 | 70.84% | 265.8 | 0.4 | 3.919 | 4.368 | 4.3 | -0.07 | 0.897 | 16.69% | -7.7 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.076 | 824 | 260 | 0 | 497.9 | 326.1 | 341.2 | 15.1 | -2.9 | 17.946 | 7.661 | 2 | 6.914% | 341.3 | -4 | 19.193 | 6.664 | 15.2 | -0.07 | 2 | 6.326% | -2.72 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.076 | 836 | 258 | 0 | 535 | 301 | 317.6 | 16.6 | -1.65 | 18.181 | 7.847 | 2 | 6.381% | 319.4 | -2.3 | 20.683 | 6.826 | 18.4 | -0.07 | 2 | 5.302% | -2.07 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.076 | 100 | 73 | 0 | 26 | 74 | 76.8 | 2.8 | 0 | 2.843 | 1.237 | 2 | 4.534% | 77.2 | 0 | 3.24 | 1.056 | 3.2 | -0.07 | 2 | 3.655% | -2.92 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.076 | 710 | 280 | 0 | 66.5 | 643.5 | 649.3 | 5.8 | -3.97 | 9.825 | 9.889 | 0.993 | 15.51% | 643.9 | -5.5 | 5.92 | 8.602 | 0.4 | -0.07 | 0.688 | 207.2% | -203.7 | 0.017 | 0.05 | 6.284% | 5.784%
Wind | WND | WIND | -0.076 | 21 | 0 | 0 | 6.5 | 14.5 | 15.2 | 0.7 | -0.64 | 1.336 | 0.292 | 2 | 3.84% | 15.4 | -0.9 | 1.796 | 0.254 | 0.9 | -0.07 | 2 | 2.754% | -2.01 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.076 | 119.3 | 0 | 0 | 23.5 | 95.8 | 102.4 | 6.6 | 0.65 | 5.96 | 1.662 | 2 | 2.294% | 104.5 | 0.9 | 7.803 | 1.446 | 8.7 | -0.07 | 2 | 1.603% | -1.39 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | SUB | FOSS | -0.076 | 650 | 189.5 | 0 | 460.1 | 189.9 | 200.4 | 10.5 | -0.53 | 10.983 | 5.13 | 2 | 7.844% | 200.1 | -0.7 | 10.927 | 4.462 | 10.2 | -0.07 | 2 | 7.437% | -2.36 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 650 | 189.5 | 0 | 460.1 | 189.9 | 200.4 | 10.5 | -0.53 | 10.983 | 5.13 | 2 | 7.844% | 200.1 | -0.7 | 10.927 | 4.462 | 10.2 | -0.07 | 2 | 7.437% | -2.36 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 650 | 189.5 | 0 | 460.1 | 189.9 | 200.4 | 10.5 | -0.53 | 10.983 | 5.13 | 2 | 7.844% | 200.1 | -0.7 | 10.927 | 4.462 | 10.2 | -0.07 | 2 | 7.437% | -2.36 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 650 | 189.5 | 0 | 460.1 | 189.9 | 200.4 | 10.5 | -0.53 | 10.983 | 5.13 | 2 | 7.844% | 200.1 | -0.7 | 10.927 | 4.462 | 10.2 | -0.07 | 2 | 7.437% | -2.36 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 650 | 189.5 | 0 | 460.1 | 189.9 | 200.4 | 10.5 | -0.53 | 10.983 | 5.13 | 2 | 7.844% | 200.1 | -0.7 | 10.927 | 4.462 | 10.2 | -0.07 | 2 | 7.437% | -2.36 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 406.8 | 205 | 4.2 | 189.4 | 213.2 | 221.9 | 8.7 | -2.3 | 11.021 | 4.22 | 2 | 5.926% | 234.5 | -3.2 | 24.488 | 3.65 | 21.3 | -0.07 | 2 | 2.229% | -1.27 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 487 | 275 | 0 | 203.1 | 283.9 | 292.1 | 8.2 | -1.79 | 9.992 | 5.105 | 1.957 | 7.526% | 292.2 | -2.5 | 10.82 | 4.415 | 8.3 | -0.07 | 2 | 6.849% | -4.33 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 221 | 118 | 65 | 37.5 | 118.5 | 123.3 | 4.8 | -0.3 | 5.078 | 1.635 | 2 | 5.838% | 126.7 | -0.4 | 8.523 | 1.414 | 8.2 | -0.07 | 2 | 3.148% | -1.83 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.076 | 932.6 | 360 | 0 | 566.8 | 365.8 | 379.3 | 13.5 | -0.01 | 13.511 | 5.748 | 2 | 8.752% | 382 | 0 | 16.148 | 5 | 16.2 | -0.07 | 2 | 6.718% | -2.86 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 932.6 | 360 | 0 | 566.8 | 365.8 | 379.3 | 13.5 | -0.01 | 13.511 | 5.748 | 2 | 8.752% | 382 | 0 | 16.148 | 5 | 16.2 | -0.07 | 2 | 6.718% | -2.86 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 932.6 | 360 | 0 | 566.8 | 365.8 | 379.3 | 13.5 | -0.01 | 13.511 | 5.748 | 2 | 8.752% | 382 | 0 | 16.148 | 5 | 16.2 | -0.07 | 2 | 6.718% | -2.86 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 932.6 | 360 | 0 | 566.8 | 365.8 | 379.3 | 13.5 | -0.01 | 13.511 | 5.748 | 2 | 8.752% | 382 | 0 | 16.148 | 5 | 16.2 | -0.07 | 2 | 6.718% | -2.86 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.076 | 83 | 58 | 0 | 24.9 | 58.1 | 60.1 | 2 | -0.1 | 2.07 | 1.027 | 2 | 5.271% | 59.9 | -0.1 | 1.978 | 0.876 | 1.8 | -0.07 | 2 | 5.395% | -4.07 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.076 | 155 | 80 | 0 | 19.9 | 135.1 | 137 | 1.9 | 0.03 | 1.789 | 1.966 | 0.91 | 10.35% | 137.8 | 0 | 2.591 | 1.71 | 2.7 | -0.07 | 1.515 | 6.708% | -6.33 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.076 | 155 | 80 | 0 | 19.9 | 135.1 | 137.8 | 2.7 | -0.27 | 2.978 | 1.965 | 1.515 | 7.282% | 138.7 | -0.4 | 3.985 | 1.709 | 3.6 | -0.07 | 2 | 5.031% | -4.75 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.076 | 669 | 156 | 0 | 488.2 | 180.8 | 188 | 7.2 | -2.22 | 9.423 | 8.661 | 1.088 | 11.77% | 188 | -3.1 | 10.298 | 7.534 | 7.2 | -0.07 | 1.367 | 10.84% | -3.18 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.076 | 663 | 156 | 0 | 507 | 156 | 166.5 | 10.5 | 0.08 | 10.345 | 8.664 | 1.194 | 8.001% | 168 | 0.1 | 11.868 | 7.537 | 12 | -0.07 | 1.575 | 6.448% | -1.64 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.076 | 577 | 159 | 0 | 417.3 | 159.7 | 170 | 10.3 | 0.12 | 10.18 | 7.448 | 1.367 | 7.099% | 169.4 | 0.2 | 9.481 | 6.479 | 9.7 | -0.07 | 1.463 | 6.943% | -2.08 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.076 | 610 | 303 | 0 | 302.4 | 307.6 | 314.4 | 6.8 | -0.24 | 7.013 | 7.353 | 0.954 | 11.37% | 314.9 | -0.3 | 7.664 | 6.396 | 7.3 | -0.07 | 1.198 | 9.753% | -5.33 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.058 | 260.4 | 140 | 6 | 108.6 | 145.8 | 149.7 | 3.9 | 0.83 | 3.12 | 1.825 | 1.71 | 6.462% | 150.1 | 1.2 | 3.155 | 1.815 | 4.3 | -0.057 | 1.738 | 5.76% | -3.27 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.058 | 147.6 | 0 | 0 | 142.3 | 5.3 | 5.3 | 0 | 0 | 0.019 | 1.443 | 0.013 | 0% | 5.4 | 0 | 0.021 | 1.435 | 0.1 | -0.057 | 0.014 | 140.5% | -4.84 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.058 | 345 | 95 | 27.1 | 141.6 | 176.3 | 182.9 | 6.6 | -0.47 | 7.024 | 2.281 | 2 | 5.057% | 184.2 | -0.7 | 8.55 | 2.268 | 7.9 | -0.057 | 2 | 4.152% | -2.15 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.058 | 202 | 153 | 0 | 43.5 | 158.5 | 161.4 | 2.9 | -0.1 | 3.018 | 1.449 | 2 | 6.743% | 160.7 | -0.1 | 2.382 | 1.441 | 2.2 | -0.057 | 1.653 | 8.736% | -6.95 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.058 | 181 | 127 | 5 | 48.9 | 127.1 | 128.5 | 1.4 | 0.18 | 1.271 | 1.263 | 1.007 | 12.52% | 128.6 | 0.2 | 1.289 | 1.256 | 1.5 | -0.057 | 1.027 | 11.48% | -8.17 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.058 | 560 | 135 | 0 | 163.2 | 396.8 | 401.6 | 4.8 | 0.25 | 4.586 | 4.441 | 1.033 | 11.28% | 402.2 | 0.4 | 5.099 | 4.417 | 5.4 | -0.057 | 1.154 | 9.857% | -7.1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.058 | 760 | 300 | 0 | 122.8 | 637.2 | 648 | 10.8 | -0.27 | 11.033 | 6.431 | 1.716 | 6.805% | 649.4 | -0.4 | 12.599 | 6.397 | 12.2 | -0.057 | 1.97 | 5.92% | -5.05 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.058 | 420 | 125 | 0 | 80.5 | 339.5 | 344.5 | 5 | -0.08 | 5.029 | 3.17 | 1.587 | 8.126% | 343.8 | -0.1 | 4.327 | 3.153 | 4.3 | -0.057 | 1.372 | 9.286% | -7.63 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.058 | 417 | 125 | 0 | 169.6 | 247.4 | 252.6 | 5.2 | 0.1 | 5.086 | 2.957 | 1.72 | 7.757% | 250.6 | 0.1 | 3.106 | 2.942 | 3.2 | -0.057 | 1.056 | 12.39% | -7.46 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.058 | 1103 | 420 | 170 | 395.4 | 537.6 | 550.2 | 12.6 | 1.91 | 10.667 | 6.694 | 1.594 | 8.464% | 566.7 | 2.7 | 26.447 | 6.656 | 29.1 | -0.057 | 2 | 3.602% | -1.78 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.058 | 621 | 430 | 119 | 66.5 | 435.5 | 439.7 | 4.2 | -0.36 | 4.555 | 3.602 | 1.265 | 14.3% | 440.7 | -0.5 | 5.646 | 3.581 | 5.2 | -0.057 | 1.577 | 11.35% | -8.09 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.058 | 463 | 356 | 32 | 61.4 | 369.6 | 376.1 | 6.5 | 2.66 | 3.851 | 3.092 | 1.245 | 6.89% | 376.2 | 3.7 | 2.908 | 3.075 | 6.6 | -0.057 | 0.946 | 6.669% | -5.41 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.058 | 1215 | 558 | 212 | 253.1 | 749.9 | 759.3 | 9.4 | 5.07 | 4.413 | 7.196 | 0.613 | 12.5% | 761.3 | 7.1 | 4.382 | 7.156 | 11.4 | -0.057 | 0.612 | 10.13% | -6.36 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.058 | 320 | 50 | 0 | 261.8 | 58.2 | 60.2 | 2 | -2.12 | 4.137 | 2.24 | 1.847 | 15.48% | 58.4 | -2.9 | 3.105 | 2.228 | 0.2 | -0.057 | 1.394 | 152.1% | -27.99 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.058 | 594.6 | 155.4 | 0 | 427.9 | 166.7 | 174.6 | 7.9 | -0.11 | 7.992 | 4.094 | 1.952 | 7.279% | 173.2 | -0.1 | 6.602 | 4.072 | 6.5 | -0.057 | 1.621 | 8.695% | -2.47 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.058 | 594.6 | 155.4 | 0 | 427.9 | 166.7 | 174.6 | 7.9 | -0.11 | 7.992 | 4.094 | 1.952 | 7.279% | 173.2 | -0.1 | 6.602 | 4.072 | 6.5 | -0.057 | 1.621 | 8.695% | -2.47 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.058 | 599.2 | 155.3 | 0 | 409.8 | 189.4 | 196.1 | 6.7 | -0.74 | 7.507 | 4.075 | 1.842 | 8.649% | 195.1 | -1 | 6.794 | 4.053 | 5.7 | -0.057 | 1.676 | 9.992% | -3.21 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.058 | 599.2 | 155.3 | 0 | 409.8 | 189.4 | 196.1 | 6.7 | -0.74 | 7.507 | 4.075 | 1.842 | 8.649% | 195.1 | -1 | 6.794 | 4.053 | 5.7 | -0.057 | 1.676 | 9.992% | -3.21 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.058 | 502.1 | 310 | 88.9 | 102.7 | 310.5 | 312.9 | 2.4 | 0 | 2.406 | 2.965 | 0.811 | 20.24% | 315.5 | 0 | 5.065 | 2.948 | 5 | -0.057 | 1.718 | 9.546% | -6 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.058 | 105.9 | 0 | 0 | 22.9 | 83 | 84.9 | 1.9 | -0.15 | 2.032 | 1.035 | 1.964 | 5.403% | 84.5 | -0.2 | 1.695 | 1.03 | 1.5 | -0.057 | 1.647 | 6.726% | -5.33 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.058 | 205.1 | 0 | 0 | 32.1 | 173 | 176.6 | 3.6 | -0.03 | 3.557 | 2.005 | 1.775 | 5.515% | 175.5 | 0 | 2.472 | 1.994 | 2.5 | -0.057 | 1.239 | 7.805% | -6.68 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.058 | 211.5 | 0 | 0 | 21 | 190.5 | 193.3 | 2.8 | 0.06 | 2.737 | 2.067 | 1.324 | 7.312% | 192.9 | 0.1 | 2.289 | 2.056 | 2.4 | -0.057 | 1.113 | 8.384% | -7.66 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.058 | 105.8 | 0 | 0 | 17 | 88.8 | 89.9 | 1.1 | 0.48 | 0.623 | 1.034 | 0.603 | 9.323% | 90.6 | 0.7 | 1.061 | 1.028 | 1.8 | -0.057 | 1.032 | 5.6% | -4.75 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | LIG | FOSS | -0.058 | 824 | 260 | 0 | 458.4 | 365.6 | 370.6 | 5 | 0.23 | 4.845 | 5.516 | 0.878 | 15.94% | 370.3 | 0.3 | 4.406 | 5.486 | 4.7 | -0.057 | 0.803 | 16.66% | -7.51 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.058 | 836 | 258 | 0 | 473.5 | 362.5 | 371.1 | 8.6 | -0.97 | 9.608 | 5.742 | 1.673 | 9.4% | 371.3 | -1.3 | 10.163 | 5.712 | 8.8 | -0.057 | 1.779 | 9.028% | -3.98 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.058 | 99 | 73 | 0 | 25.3 | 73.7 | 76.1 | 2.4 | -0.23 | 2.679 | 0.842 | 2 | 3.999% | 76.4 | -0.3 | 3.08 | 0.836 | 2.7 | -0.057 | 2 | 3.494% | -2.63 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.058 | 530 | 345 | 0 | 184 | 346 | 352.4 | 6.4 | -0.65 | 7.06 | 3.803 | 1.857 | 8.01% | 353.1 | -0.9 | 7.989 | 3.781 | 7.1 | -0.057 | 2 | 7.096% | -4.71 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.058 | 104.9 | 0 | 0 | 8.2 | 96.7 | 96.8 | 0.1 | -0.31 | 0.4 | 1.025 | 0.391 | 101.7% | 97.1 | -0.4 | 0.83 | 1.02 | 0.4 | -0.057 | 0.814 | 24.98% | -23.3 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | GT | -0.058 | 245 | 150 | 16 | 68.5 | 160.5 | 163.7 | 3.2 | 0.26 | 2.965 | 1.624 | 1.826 | 7.41% | 164 | 0.4 | 3.179 | 1.615 | 3.5 | -0.057 | 1.968 | 6.658% | -4.42 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.058 | 243 | 150 | 16 | 74.8 | 152.2 | 155.6 | 3.4 | 0.12 | 3.246 | 1.62 | 2 | 6.917% | 156 | 0.2 | 3.605 | 1.611 | 3.8 | -0.057 | 2 | 6.082% | -3.86 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.058 | 240 | 150 | 16 | 73.1 | 150.9 | 154 | 3.1 | 0.21 | 2.935 | 1.6 | 1.834 | 7.493% | 154.6 | 0.3 | 3.397 | 1.591 | 3.7 | -0.057 | 2 | 6.17% | -3.93 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.058 | 255 | 150 | 16 | 88.2 | 150.8 | 154.9 | 4.1 | -0.07 | 4.185 | 1.631 | 2 | 6.019% | 154.7 | -0.1 | 4.028 | 1.622 | 3.9 | -0.057 | 2 | 6.219% | -3.73 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.058 | 257 | 110 | 16 | 130.8 | 110.2 | 113.7 | 3.5 | 0.21 | 3.248 | 1.693 | 1.919 | 7.106% | 114 | 0.3 | 3.493 | 1.684 | 3.8 | -0.057 | 2 | 6.432% | -2.8 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.058 | 208 | 40 | 0 | 157.2 | 50.8 | 54 | 3.2 | -3.95 | 7.207 | 1.96 | 2 | 6.292% | 57.1 | -5.5 | 11.846 | 1.949 | 6.3 | -0.057 | 2 | 3.141% | -0.77 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | LIG | FOSS | -0.058 | 815 | 280 | 0 | 62.5 | 752.5 | 757.2 | 4.7 | -0.27 | 5.008 | 7.966 | 0.629 | 16.77% | 755.2 | -0.4 | 3.058 | 7.924 | 2.7 | -0.057 | 0.386 | 28.69% | -26.93 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.058 | 650 | 189.5 | 0 | 457.4 | 192.6 | 200.6 | 8 | 0.12 | 7.937 | 3.599 | 2 | 7.858% | 198.6 | 0.2 | 5.922 | 3.58 | 6 | -0.057 | 1.654 | 10.3% | -3.1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.058 | 650 | 189.5 | 0 | 457.4 | 192.6 | 200.6 | 8 | 0.12 | 7.937 | 3.599 | 2 | 7.858% | 198.6 | 0.2 | 5.922 | 3.58 | 6 | -0.057 | 1.654 | 10.3% | -3.1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.058 | 650 | 189.5 | 0 | 457.4 | 192.6 | 200.6 | 8 | 0.12 | 7.937 | 3.599 | 2 | 7.858% | 198.6 | 0.2 | 5.922 | 3.58 | 6 | -0.057 | 1.654 | 10.3% | -3.1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.058 | 650 | 189.5 | 0 | 457.4 | 192.6 | 200.6 | 8 | 0.12 | 7.937 | 3.599 | 2 | 7.858% | 198.6 | 0.2 | 5.922 | 3.58 | 6 | -0.057 | 1.654 | 10.3% | -3.1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.058 | 650 | 189.5 | 0 | 457.4 | 192.6 | 200.6 | 8 | 0.12 | 7.937 | 3.599 | 2 | 7.858% | 198.6 | 0.2 | 5.922 | 3.58 | 6 | -0.057 | 1.654 | 10.3% | -3.1 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.058 | 732.7 | 477.2 | 90 | 53.3 | 589.4 | 597.1 | 7.7 | 3.25 | 4.39 | 4.611 | 0.952 | 9.202% | 596.4 | 4.5 | 2.463 | 4.585 | 7 | -0.057 | 0.537 | 9.948% | -8.14 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.058 | 737 | 456 | 43.7 | 212.4 | 480.9 | 488 | 7.1 | -7.79 | 14.845 | 4.974 | 2 | 10.04% | 497.5 | -10.8 | 27.416 | 4.946 | 16.6 | -0.057 | 2 | 4.219% | -2.8 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.058 | 736.7 | 453.7 | 46.1 | 203.7 | 486.9 | 496 | 9.1 | -2.07 | 11.162 | 4.955 | 2 | 7.829% | 506 | -2.9 | 21.973 | 4.927 | 19.1 | -0.057 | 2 | 3.666% | -2.46 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.058 | 174 | 0 | 0 | 172.2 | 1.8 | 1.9 | 0.1 | -0.12 | 0.218 | 1.701 | 0.128 | 168.5% | 2 | -0.2 | 0.43 | 1.692 | 0.2 | -0.057 | 0.254 | 82.79% | -0.73 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | FOSS | -0.058 | 50.1 | 24 | 0 | 23.4 | 26.7 | 30.2 | 3.5 | -0.56 | 4.085 | 0.426 | 2 | 1.392% | 32.5 | -0.8 | 6.553 | 0.424 | 5.8 | -0.057 | 2 | 0.8255% | -0.44 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.058 | 493.6 | 240 | 18.8 | 193.2 | 281.6 | 283.3 | 1.7 | -6.08 | 7.755 | 3.407 | 2 | 28.08% | 294.5 | -8.5 | 21.378 | 3.387 | 12.9 | -0.057 | 2 | 3.637% | -2.11 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.058 | 504 | 343 | 10 | 140.6 | 353.4 | 356.4 | 3 | -0.18 | 3.18 | 3.544 | 0.897 | 16.25% | 357 | -0.2 | 3.846 | 3.524 | 3.6 | -0.057 | 1.091 | 13.31% | -9.48 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.058 | 55.9 | 22.5 | 0 | 29.3 | 26.6 | 27.8 | 1.2 | -1.22 | 2.383 | 0.475 | 2 | 4.527% | 32.7 | -1.7 | 7.803 | 0.472 | 6.1 | -0.057 | 2 | 0.8752% | -0.42 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.058 | 55.9 | 22.5 | 0 | 28.8 | 27.1 | 28.2 | 1.1 | -1.02 | 2.146 | 0.476 | 2 | 4.938% | 33.6 | -1.4 | 7.984 | 0.473 | 6.5 | -0.057 | 2 | 0.8214% | -0.4 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.058 | 465 | 275 | 0 | 163.1 | 301.9 | 317.9 | 16 | -1.16 | 17.128 | 3.336 | 2 | 2.811% | 316.3 | -1.6 | 15.965 | 3.317 | 14.4 | -0.057 | 2 | 3.07% | -2.02 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.058 | 932.2 | 374.9 | 0 | 550.5 | 381.7 | 394.5 | 12.8 | -0.1 | 12.933 | 4.179 | 2 | 7.042% | 395.4 | -0.1 | 13.8 | 4.156 | 13.7 | -0.057 | 2 | 6.466% | -2.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.058 | 932.2 | 374.9 | 0 | 550.5 | 381.7 | 394.5 | 12.8 | -0.1 | 12.933 | 4.179 | 2 | 7.042% | 395.4 | -0.1 | 13.8 | 4.156 | 13.7 | -0.057 | 2 | 6.466% | -2.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.058 | 932.2 | 374.9 | 0 | 550.5 | 381.7 | 394.5 | 12.8 | -0.1 | 12.933 | 4.179 | 2 | 7.042% | 395.4 | -0.1 | 13.8 | 4.156 | 13.7 | -0.057 | 2 | 6.466% | -2.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.058 | 932.2 | 374.9 | 0 | 550.5 | 381.7 | 394.5 | 12.8 | -0.1 | 12.933 | 4.179 | 2 | 7.042% | 395.4 | -0.1 | 13.8 | 4.156 | 13.7 | -0.057 | 2 | 6.466% | -2.69 | 0.017 | 0.05 | 6.284% | 5.784%
Solar | SUN | PVGR | -0.058 | 98.6 | 0 | 0 | 40.1 | 58.5 | 59.7 | 1.2 | 0 | 1.2 | 0.964 | 1.245 | 7.966% | 59.7 | 0 | 1.2 | 0.959 | 1.2 | -0.057 | 1.252 | 7.829% | -4.69 | 0.017 | 0.05 | 6.014% | 6.718%
Thermal | NG | COGN | -0.058 | 80 | 58 | 0 | 21.7 | 58.3 | 60 | 1.7 | 0.01 | 1.637 | 0.68 | 2 | 4.566% | 59.9 | 0 | 1.567 | 0.676 | 1.6 | -0.057 | 2 | 4.768% | -3.5 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.058 | 80 | 62 | 0 | 17.5 | 62.5 | 63.9 | 1.4 | -0.03 | 1.406 | 0.68 | 2 | 5.544% | 63.7 | 0 | 1.241 | 0.676 | 1.2 | -0.057 | 1.836 | 6.357% | -5.01 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.058 | 120.1 | 65 | 0 | 18.9 | 101.2 | 102.8 | 1.6 | 0.08 | 1.524 | 0.862 | 1.769 | 7.274% | 103 | 0.1 | 1.692 | 0.857 | 1.8 | -0.057 | 1.975 | 6.354% | -5.42 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.058 | 162.4 | 0 | 0 | 29 | 133.4 | 134.7 | 1.3 | 0.05 | 1.159 | 1.587 | 0.73 | 12.1% | 134.5 | 0.1 | 0.982 | 1.579 | 1.1 | -0.057 | 0.622 | 14.05% | -11.7 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | BIT | FOSS | -0.058 | 663 | 156 | 0 | 256.1 | 406.9 | 417.2 | 10.3 | 5.98 | 4.302 | 5.477 | 0.786 | 6.225% | 418.3 | 8.3 | 3.11 | 5.448 | 11.4 | -0.057 | 0.571 | 5.527% | -3.45 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.058 | 610 | 303 | 0 | 139.3 | 470.7 | 481.7 | 11 | 5.78 | 5.155 | 4.733 | 1.089 | 5.363% | 483 | 8 | 4.187 | 4.708 | 12.3 | -0.057 | 0.889 | 4.714% | -3.7 | 0.017 | 0.05 | 6.284% | 5.784%
Wind | WND | WIND | -0.058 | 108 | 0 | 0 | 105.4 | 2.6 | 2.7 | 0.1 | -0.01 | 0.161 | 1.055 | 0.152 | 104.7% | 3 | 0 | 0.449 | 1.05 | 0.4 | -0.057 | 0.428 | 25.72% | -0.56 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.096 | 531.7 | 275 | 12 | 199.1 | 320.6 | 322.6 | 2 | -9.38 | 11.372 | 9.515 | 1.195 | 42.55% | 325.1 | -13.1 | 17.552 | 9.294 | 4.5 | -0.094 | 1.889 | 18.52% | -11.39 | 0.017 | 0.0578 | 5.933% | 5.163%
Hydro | NA | HYDR | -0.096 | 30 | 0 | 0 | 28.5 | 1.5 | 29.9 | 28.4 | -5.13 | 33.484 | 0.72 | 2 | 0.17% | 29.9 | -7.1 | 35.526 | 0.704 | 28.4 | -0.094 | 2 | 0.1665% | -0.01 | 0.017 | 0.05 | 0.2285% | 0.2528%
Thermal | SUB | FOSS | -0.096 | 420 | 125 | 0 | 35.8 | 384.2 | 391.7 | 7.5 | -0.29 | 7.73 | 7.968 | 0.97 | 8.964% | 387.5 | -0.4 | 3.704 | 7.787 | 3.3 | -0.094 | 0.476 | 19.95% | -18.62 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.096 | 417 | 125 | 0 | 54.2 | 362.8 | 370.5 | 7.7 | 0.3 | 7.411 | 7.821 | 0.948 | 8.669% | 368.6 | 0.4 | 5.39 | 7.643 | 5.8 | -0.094 | 0.705 | 11.27% | -10 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.096 | 45 | 0 | 0 | 10 | 35 | 36.7 | 1.7 | 0.02 | 1.669 | 0.97 | 1.72 | 4.252% | 36.7 | 0 | 1.685 | 0.946 | 1.7 | -0.094 | 1.782 | 4.164% | -3.28 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | FOSS | -0.096 | 749 | 309 | 0 | 292.2 | 456.8 | 471.1 | 14.3 | 0.93 | 13.419 | 12.123 | 1.107 | 8.384% | 477.2 | 1.3 | 19.09 | 11.763 | 20.4 | -0.094 | 1.623 | 5.755% | -3.58 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.096 | 464 | 348 | 46 | 51.8 | 366.2 | 379.7 | 13.5 | 0.62 | 12.836 | 7.653 | 1.677 | 5.501% | 381.3 | 0.9 | 14.181 | 7.475 | 15.1 | -0.094 | 1.897 | 4.816% | -3.88 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.096 | 320 | 50 | 0 | 51.6 | 268.4 | 282.4 | 14 | -0.03 | 14.116 | 6.14 | 2 | 3.659% | 282.8 | 0 | 14.442 | 6.001 | 14.4 | -0.094 | 2 | 3.483% | -2.98 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.096 | 45 | 7 | 0 | 18.1 | 26.9 | 33.6 | 6.7 | 0.1 | 6.574 | 0.824 | 2 | 1.079% | 34.4 | 0.1 | 7.422 | 0.805 | 7.5 | -0.094 | 2 | 0.9438% | -0.57 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.096 | 212 | 130 | 0 | 39.1 | 172.9 | 180.7 | 7.8 | -0.15 | 7.899 | 3.881 | 2 | 4.352% | 180.8 | -0.2 | 8.065 | 3.791 | 7.9 | -0.094 | 2 | 4.208% | -3.5 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.096 | 599.2 | 155.3 | 0 | 54.2 | 545 | 560.5 | 15.5 | -0.21 | 15.706 | 10.151 | 1.547 | 6.187% | 557.6 | -0.3 | 12.941 | 9.921 | 12.6 | -0.094 | 1.304 | 7.453% | -6.92 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.096 | 599.2 | 155.3 | 0 | 54.2 | 545 | 560.5 | 15.5 | -0.21 | 15.706 | 10.151 | 1.547 | 6.187% | 557.6 | -0.3 | 12.941 | 9.921 | 12.6 | -0.094 | 1.304 | 7.453% | -6.92 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | STM | -0.096 | 319 | 56 | 0 | 110.4 | 208.6 | 221 | 12.4 | 2.41 | 9.99 | 7.389 | 1.352 | 4.118% | 225.8 | 3.4 | 13.827 | 7.221 | 17.2 | -0.094 | 1.915 | 2.907% | -1.94 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | COGN | -0.096 | 235 | 150 | 16 | 10 | 209 | 210 | 1 | 0.11 | 0.946 | 4.918 | 0.192 | 37.63% | 210 | 0.2 | 0.811 | 4.807 | 1 | -0.094 | 0.169 | 36.84% | -33.41 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.096 | 236 | 150 | 16 | 9.4 | 210.6 | 215.7 | 5.1 | 0.52 | 4.536 | 4.967 | 0.913 | 7.409% | 216 | 0.7 | 4.588 | 4.854 | 5.4 | -0.094 | 0.945 | 6.852% | -6.23 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.096 | 239 | 150 | 16 | 10 | 213 | 215.2 | 2.2 | 0.12 | 2.117 | 5.072 | 0.417 | 17.39% | 215.5 | 0.2 | 2.345 | 4.957 | 2.5 | -0.094 | 0.473 | 14.99% | -13.62 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | GT | -0.096 | 95 | 35 | 0 | 19.1 | 75.9 | 79.8 | 3.9 | 0.1 | 3.808 | 2.049 | 1.859 | 3.905% | 79.5 | 0.1 | 3.43 | 1.997 | 3.6 | -0.094 | 1.718 | 4.142% | -3.37 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.096 | 91 | 35 | 0 | 17.2 | 73.8 | 77.8 | 4 | 0.09 | 3.859 | 1.962 | 1.967 | 3.647% | 77.5 | 0.1 | 3.497 | 1.913 | 3.7 | -0.094 | 1.828 | 3.861% | -3.18 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | COGN | -0.096 | 101 | 73 | 0 | 21.7 | 79.3 | 85.2 | 5.9 | 0.23 | 5.667 | 2.178 | 2 | 2.744% | 85.5 | 0.3 | 5.811 | 2.123 | 6.2 | -0.094 | 2 | 2.557% | -2.04 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.096 | 520 | 337 | 0 | 13.2 | 506.8 | 511.2 | 4.4 | 0.12 | 4.316 | 9.521 | 0.453 | 18.92% | 511.5 | 0.2 | 4.536 | 9.299 | 4.7 | -0.094 | 0.488 | 17.34% | -17.25 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.096 | 239 | 150 | 16 | 11.1 | 211.9 | 217.5 | 5.6 | 0.07 | 5.547 | 4.31 | 1.287 | 6.834% | 217.9 | 0.1 | 5.871 | 4.213 | 6 | -0.094 | 1.394 | 6.245% | -5.65 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.096 | 237 | 150 | 16 | 10.3 | 210.7 | 211.9 | 1.2 | 0.11 | 1.002 | 4.275 | 0.234 | 31.62% | 212.1 | 0.2 | 1.228 | 4.178 | 1.4 | -0.094 | 0.294 | 26.54% | -24.06 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.096 | 233 | 150 | 16 | 9.9 | 207.1 | 212.2 | 5.1 | 0.11 | 5.005 | 4.146 | 1.207 | 7.315% | 213.1 | 0.1 | 5.855 | 4.052 | 6 | -0.094 | 1.445 | 6.089% | -5.52 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.096 | 239 | 150 | 16 | 10.1 | 212.9 | 217.4 | 4.5 | 0.28 | 4.304 | 4.324 | 0.995 | 8.504% | 217.7 | 0.4 | 4.456 | 4.226 | 4.8 | -0.094 | 1.054 | 7.807% | -7.09 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.096 | 246 | 150 | 16 | 10.5 | 219.5 | 225.9 | 6.4 | 0.23 | 6.162 | 4.37 | 1.41 | 6.154% | 225.6 | 0.3 | 5.767 | 4.271 | 6.1 | -0.094 | 1.35 | 6.323% | -5.75 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.096 | 248 | 110 | 16 | 9.9 | 222.1 | 228.6 | 6.5 | 0.41 | 6.082 | 4.434 | 1.372 | 6.109% | 228.7 | 0.6 | 5.98 | 4.334 | 6.6 | -0.094 | 1.38 | 5.891% | -5.38 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.096 | 108 | 35 | 0 | 66.3 | 41.7 | 43.3 | 1.6 | -2.58 | 4.175 | 2.329 | 1.792 | 10.82% | 47.6 | -3.6 | 9.51 | 2.27 | 5.9 | -0.094 | 2 | 2.873% | -1.13 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | LIG | FOSS | -0.096 | 730 | 220 | 0 | 38.2 | 691.8 | 717.5 | 25.7 | -1.88 | 27.529 | 17.528 | 1.571 | 4.546% | 713.6 | -2.6 | 24.368 | 17.131 | 21.8 | -0.094 | 1.422 | 5.247% | -5.08 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.096 | 327 | 203 | 24 | 7.7 | 295.3 | 300.8 | 5.5 | -0.12 | 5.644 | 5.548 | 1.017 | 9.518% | 302.5 | -0.2 | 7.35 | 5.419 | 7.2 | -0.094 | 1.356 | 7.119% | -6.56 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.096 | 728 | 452 | 23.2 | 100.4 | 604.4 | 628.4 | 24 | 0.71 | 23.383 | 12.904 | 1.812 | 4.855% | 634.3 | 1 | 28.965 | 12.604 | 29.9 | -0.094 | 2 | 3.815% | -3.23 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.096 | 67 | 41 | 0 | 25.3 | 41.7 | 45.1 | 3.4 | 0.14 | 3.292 | 1.445 | 2 | 3.161% | 45.1 | 0.2 | 3.236 | 1.408 | 3.4 | -0.094 | 2 | 3.096% | -1.95 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.096 | 49.8 | 24 | 0 | 16.8 | 33 | 37 | 4 | 0.14 | 3.929 | 1.074 | 2 | 1.999% | 40.4 | 0.2 | 7.255 | 1.047 | 7.4 | -0.094 | 2 | 1.058% | -0.71 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.096 | 49.8 | 24 | 0 | 16.6 | 33.2 | 37 | 3.8 | 0.29 | 3.543 | 1.074 | 2 | 2.104% | 41.1 | 0.4 | 7.508 | 1.047 | 7.9 | -0.094 | 2 | 0.9912% | -0.67 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.096 | 478.3 | 240 | 4.6 | 150.8 | 322.9 | 342.4 | 19.5 | 0.59 | 18.988 | 8.673 | 2 | 3.926% | 357.6 | 0.8 | 33.929 | 8.471 | 34.7 | -0.094 | 2 | 2.16% | -1.49 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.096 | 279.2 | 118 | 65 | 38.9 | 175.3 | 177.4 | 2.1 | -2.02 | 4.108 | 3.922 | 1.047 | 21.29% | 181.5 | -2.8 | 8.987 | 3.83 | 6.2 | -0.094 | 2 | 7.06% | -4.52 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.096 | 264 | 165 | 35 | 62.8 | 166.2 | 175.7 | 9.5 | -0.01 | 9.55 | 4.193 | 2 | 4.449% | 177.9 | 0 | 11.737 | 4.095 | 11.7 | -0.094 | 2 | 3.537% | -2.27 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.096 | 669 | 156 | 0 | 56 | 613 | 630.7 | 17.7 | -0.04 | 17.744 | 12.264 | 1.447 | 6.049% | 630.5 | -0.1 | 17.59 | 11.986 | 17.5 | -0.094 | 1.467 | 5.991% | -5.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.096 | 663 | 156 | 0 | 54.2 | 608.8 | 624.8 | 16 | 0.21 | 15.844 | 12.228 | 1.296 | 6.632% | 624.2 | 0.3 | 15.112 | 11.951 | 15.4 | -0.094 | 1.265 | 6.747% | -6.32 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.096 | 545 | 303 | 0 | 19.7 | 525.3 | 536 | 10.7 | 0.24 | 10.395 | 10.084 | 1.031 | 8.152% | 537.1 | 0.3 | 11.475 | 9.856 | 11.8 | -0.094 | 1.164 | 7.238% | -7.12 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.096 | 1075 | 379 | 152 | 247.5 | 675.5 | 705.5 | 30 | -1.58 | 31.638 | 16.899 | 1.872 | 5.734% | 712.1 | -2.2 | 38.867 | 16.506 | 36.6 | -0.094 | 2 | 4.602% | -2.95 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.096 | 46 | 13 | 0 | 32.9 | 13.1 | 15 | 1.9 | 0 | 1.856 | 0.992 | 1.871 | 3.889% | 14.7 | 0 | 1.6 | 0.967 | 1.6 | -0.094 | 1.655 | 4.522% | -1.29 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.082 | 478 | 300 | 0 | 73.1 | 404.9 | 414 | 9.1 | 0.89 | 8.256 | 8.309 | 0.994 | 7.182% | 412.8 | 1.2 | 6.661 | 7.545 | 7.9 | -0.076 | 0.883 | 7.668% | -7 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.082 | 560 | 135 | 0 | 63.7 | 496.3 | 507 | 10.7 | 0.34 | 10.396 | 12.491 | 0.832 | 7.155% | 514.3 | 0.5 | 17.52 | 11.373 | 18 | -0.076 | 1.54 | 3.942% | -3.77 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 420 | 125 | 0 | 65.2 | 354.8 | 364.4 | 9.6 | 0.06 | 9.46 | 7.447 | 1.27 | 5.982% | 362.5 | 0.1 | 7.59 | 6.781 | 7.7 | -0.076 | 1.119 | 6.913% | -6.29 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 417 | 125 | 0 | 64.6 | 352.4 | 361.4 | 9 | 0.18 | 8.764 | 7.387 | 1.186 | 6.335% | 360.8 | 0.2 | 8.086 | 6.726 | 8.4 | -0.076 | 1.202 | 6.291% | -5.73 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 650 | 300 | 0 | 37.5 | 612.5 | 626.7 | 14.2 | 7.66 | 6.495 | 12.578 | 0.516 | 6.258% | 630.7 | 10.7 | 7.535 | 11.452 | 18.2 | -0.076 | 0.658 | 4.525% | -4.6 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 633 | 498 | 27 | 60 | 546 | 563.6 | 17.6 | 0.5 | 17.116 | 10.534 | 1.625 | 4.917% | 564.1 | 0.7 | 17.439 | 9.566 | 18.1 | -0.076 | 1.823 | 4.431% | -4.12 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.082 | 320 | 50 | 0 | 52.8 | 267.2 | 276.6 | 9.4 | 1.62 | 7.822 | 5.842 | 1.339 | 4.655% | 277.6 | 2.3 | 8.186 | 5.319 | 10.4 | -0.076 | 1.539 | 3.9% | -3.51 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 580.7 | 244.9 | 0 | 61.8 | 518.9 | 539.2 | 20.3 | 1.69 | 18.549 | 9.42 | 1.969 | 3.911% | 538.6 | 2.4 | 17.267 | 8.577 | 19.7 | -0.076 | 2 | 3.735% | -3.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 580.7 | 244.9 | 0 | 61.8 | 518.9 | 539.2 | 20.3 | 1.69 | 18.549 | 9.42 | 1.969 | 3.911% | 538.6 | 2.4 | 17.267 | 8.577 | 19.7 | -0.076 | 2 | 3.735% | -3.6 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 623 | 322 | 111 | 172.6 | 339.4 | 347 | 7.6 | -3.23 | 10.795 | 8.9 | 1.213 | 11.21% | 355.1 | -4.5 | 20.149 | 8.082 | 15.7 | -0.076 | 2 | 5.028% | -2.95 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.082 | 99 | 73 | 0 | 21.2 | 77.8 | 83.3 | 5.5 | -0.23 | 5.723 | 2.027 | 2 | 2.465% | 83.5 | -0.3 | 6.012 | 1.825 | 5.7 | -0.076 | 2 | 2.205% | -1.86 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 529 | 344 | 0 | 79.6 | 449.4 | 460.4 | 11 | -1.53 | 12.487 | 9.196 | 1.358 | 6.575% | 462.1 | -2.1 | 14.806 | 8.35 | 12.7 | -0.076 | 1.773 | 5.278% | -4.83 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | STM | -0.082 | 205 | 40 | 0 | 159.3 | 45.7 | 51.9 | 6.2 | -0.46 | 6.627 | 4.518 | 1.467 | 4.523% | 54.2 | -0.6 | 9.103 | 4.113 | 8.5 | -0.076 | 2 | 3.058% | -0.73 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.082 | 314.5 | 134 | 55.1 | 14.7 | 244.7 | 249.5 | 4.8 | 2.03 | 2.774 | 4.509 | 0.615 | 8.96% | 250.1 | 2.8 | 2.623 | 4.094 | 5.4 | -0.076 | 0.641 | 7.382% | -6.19 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 717 | 459.2 | 57.4 | 181.4 | 478.2 | 487.9 | 9.7 | -1.36 | 11.131 | 11.466 | 0.971 | 10.1% | 494.2 | -1.9 | 17.931 | 10.412 | 16 | -0.076 | 1.722 | 5.678% | -4.08 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 709 | 447 | 25.8 | 93 | 590.2 | 611.5 | 21.3 | -0.35 | 21.633 | 11.876 | 1.822 | 4.55% | 616.5 | -0.5 | 26.778 | 10.784 | 26.3 | -0.076 | 2 | 3.416% | -3.07 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 722.4 | 444 | 38 | 154.8 | 529.6 | 547.6 | 18 | -1.89 | 19.833 | 11.897 | 1.667 | 5.486% | 558.1 | -2.6 | 31.084 | 10.803 | 28.5 | -0.076 | 2 | 3.212% | -2.54 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 491.4 | 240 | 5.9 | 166.1 | 319.4 | 334.2 | 14.8 | -0.53 | 15.238 | 8.439 | 1.806 | 4.54% | 347.8 | -0.7 | 29.096 | 7.664 | 28.4 | -0.076 | 2 | 2.193% | -1.54 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 460 | 275 | 0 | 82.5 | 377.5 | 394.8 | 17.3 | -0.25 | 17.553 | 7.996 | 2 | 3.636% | 398.5 | -0.4 | 21.311 | 7.261 | 21 | -0.076 | 2 | 2.776% | -2.46 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.082 | 289.5 | 118 | 65 | 33.5 | 191 | 195.9 | 4.9 | 0.51 | 4.387 | 3.902 | 1.124 | 8.08% | 195.8 | 0.7 | 4.09 | 3.543 | 4.8 | -0.076 | 1.154 | 7.645% | -5.43 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.082 | 932.2 | 360 | 0 | 48.6 | 883.6 | 906.9 | 23.3 | -1.06 | 24.378 | 15.196 | 1.604 | 5.469% | 911 | -1.5 | 28.852 | 13.835 | 27.4 | -0.076 | 2 | 4.31% | -4.41 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 932.2 | 360 | 0 | 48.6 | 883.6 | 906.9 | 23.3 | -1.06 | 24.378 | 15.196 | 1.604 | 5.469% | 911 | -1.5 | 28.852 | 13.835 | 27.4 | -0.076 | 2 | 4.31% | -4.41 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 932.2 | 360 | 0 | 48.6 | 883.6 | 906.9 | 23.3 | -1.06 | 24.378 | 15.196 | 1.604 | 5.469% | 911 | -1.5 | 28.852 | 13.835 | 27.4 | -0.076 | 2 | 4.31% | -4.41 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.082 | 932.2 | 360 | 0 | 48.6 | 883.6 | 906.9 | 23.3 | -1.06 | 24.378 | 15.196 | 1.604 | 5.469% | 911 | -1.5 | 28.852 | 13.835 | 27.4 | -0.076 | 2 | 4.31% | -4.41 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.082 | 1093 | 379 | 152 | 195.3 | 745.7 | 771.8 | 26.1 | 0.42 | 25.646 | 16.357 | 1.568 | 5.724% | 780.8 | 0.6 | 34.492 | 14.854 | 35.1 | -0.076 | 2 | 3.945% | -2.9 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.102 | 194.7 | 85 | 0 | 37.6 | 157.1 | 165.9 | 8.8 | 0.19 | 8.645 | 3.996 | 2 | 3.764% | 172 | 0.3 | 14.677 | 4.057 | 14.9 | -0.103 | 2 | 2.245% | -1.79 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.102 | 194.7 | 85 | 0 | 22.5 | 172.2 | 180.9 | 8.7 | 0.15 | 8.572 | 3.996 | 2 | 3.808% | 185.7 | 0.2 | 13.284 | 4.057 | 13.5 | -0.103 | 2 | 2.478% | -2.17 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.102 | 511.8 | 275 | 12 | 48.6 | 451.2 | 463 | 11.8 | 1.53 | 10.171 | 8.712 | 1.168 | 7.376% | 468.2 | 2.1 | 14.809 | 8.834 | 17 | -0.103 | 1.676 | 5.17% | -4.51 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.102 | 412 | 70 | 0 | 90.3 | 321.7 | 332.8 | 11.1 | 0.05 | 11.069 | 5.431 | 2 | 6.315% | 335.5 | 0.1 | 13.709 | 5.535 | 13.8 | -0.103 | 2 | 5.129% | -3.96 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.102 | 198.3 | 161.3 | 0 | 33.7 | 164.6 | 171.2 | 6.6 | 0.23 | 6.423 | 3.456 | 1.858 | 5.112% | 171.8 | 0.3 | 6.921 | 3.505 | 7.2 | -0.103 | 1.975 | 4.732% | -3.88 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.102 | 420 | 70 | 0 | 45.2 | 374.8 | 382.7 | 7.9 | 0.52 | 7.449 | 8.299 | 0.898 | 9.042% | 385.9 | 0.7 | 10.372 | 8.414 | 11.1 | -0.103 | 1.233 | 6.498% | -5.74 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.102 | 749 | 310 | 0 | 52.7 | 696.3 | 708.6 | 12.3 | 1.1 | 11.251 | 10.132 | 1.11 | 10.36% | 717.4 | 1.5 | 19.548 | 10.326 | 21.1 | -0.103 | 1.893 | 6.096% | -5.61 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.102 | 624 | 456 | 35 | 83.5 | 505.5 | 522.9 | 17.4 | -1.28 | 18.65 | 10.266 | 1.817 | 6.098% | 524.7 | -1.8 | 20.976 | 10.411 | 19.2 | -0.103 | 2 | 5.581% | -4.47 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.102 | 315 | 50 | 0 | 51.4 | 263.6 | 278.1 | 14.5 | -0.18 | 14.737 | 5.681 | 2 | 3.695% | 279.9 | -0.3 | 16.611 | 5.76 | 16.3 | -0.103 | 2 | 3.319% | -2.75 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.102 | 420 | 50 | 0 | 116.4 | 303.6 | 319.8 | 16.2 | 0.11 | 16.073 | 8.108 | 1.982 | 4.409% | 320.8 | 0.2 | 17.044 | 8.22 | 17.2 | -0.103 | 2 | 4.194% | -3 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.102 | 150 | 80 | 0 | 24 | 126 | 132.4 | 6.4 | 0.01 | 6.428 | 3.079 | 2 | 3.989% | 132.3 | 0 | 6.285 | 3.126 | 6.3 | -0.103 | 2 | 4.092% | -3.4 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.102 | 150 | 80 | 0 | 11 | 139 | 145.3 | 6.3 | 0 | 6.384 | 3.079 | 2 | 4.052% | 145.4 | 0 | 6.489 | 3.126 | 6.4 | -0.103 | 2 | 4.028% | -3.69 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.102 | 212 | 130 | 0.2 | 26.8 | 185 | 190.8 | 5.8 | 1.12 | 4.691 | 3.692 | 1.271 | 6.219% | 191.5 | 1.6 | 4.942 | 3.744 | 6.5 | -0.103 | 1.32 | 5.603% | -4.83 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | STM | -0.102 | 304.9 | 54.5 | 0 | 45.5 | 259.4 | 267.3 | 7.9 | -0.49 | 8.411 | 6.658 | 1.263 | 6.565% | 266.8 | -0.7 | 8.096 | 6.75 | 7.4 | -0.103 | 1.199 | 7.077% | -5.96 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | FOSS | -0.102 | 234 | 47 | 0 | 185.1 | 48.9 | 57 | 8.1 | 0.7 | 7.344 | 3.685 | 1.993 | 4.918% | 55.4 | 1 | 5.531 | 3.755 | 6.5 | -0.103 | 1.473 | 6.189% | -1.27 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.102 | 382 | 40 | 0 | 337.8 | 44.2 | 56 | 11.8 | 0.23 | 11.585 | 5.691 | 2 | 5.508% | 55.5 | 0.3 | 10.97 | 5.8 | 11.3 | -0.103 | 1.891 | 5.808% | -0.66 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.102 | 215 | 150 | 0 | 7.3 | 207.7 | 212.4 | 4.7 | 0.58 | 4.086 | 4.569 | 0.894 | 7.783% | 212.8 | 0.8 | 4.306 | 4.632 | 5.1 | -0.103 | 0.93 | 7.242% | -6.92 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.102 | 215 | 150 | 0 | 7.3 | 207.7 | 212.1 | 4.4 | 0.36 | 4.003 | 4.57 | 0.876 | 8.313% | 212.8 | 0.5 | 4.574 | 4.633 | 5.1 | -0.103 | 0.987 | 7.242% | -6.92 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.102 | 216 | 150 | 0 | 6.5 | 209.5 | 213.3 | 3.8 | -0.17 | 3.958 | 4.617 | 0.857 | 9.671% | 214.5 | -0.2 | 5.247 | 4.68 | 5 | -0.103 | 1.121 | 7.422% | -7.12 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.102 | 223 | 150 | 0 | 7.2 | 215.8 | 219.2 | 3.4 | 0.64 | 2.791 | 4.863 | 0.574 | 11.16% | 220.7 | 0.9 | 4.004 | 4.93 | 4.9 | -0.103 | 0.812 | 7.818% | -7.48 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.102 | 96 | 59 | 0 | 20.6 | 75.4 | 80.5 | 5.1 | 0 | 5.13 | 1.97 | 2 | 3.206% | 80.8 | 0 | 5.4 | 2 | 5.4 | -0.103 | 2 | 3.057% | -2.37 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.102 | 523 | 45 | 0 | 408.2 | 114.8 | 116.8 | 2 | -0.79 | 2.811 | 9.585 | 0.293 | 44.47% | 118.6 | -1.1 | 4.952 | 9.717 | 3.8 | -0.103 | 0.51 | 23.63% | -5.13 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.102 | 515.9 | 303 | 12.8 | 31.4 | 471.7 | 484.5 | 12.8 | -0.87 | 13.585 | 8.769 | 1.549 | 6.854% | 490.9 | -1.2 | 20.352 | 8.892 | 19.2 | -0.103 | 2 | 4.614% | -4.18 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.102 | 519.4 | 305.5 | 19.7 | 13.2 | 486.5 | 496.7 | 10.2 | -0.31 | 10.567 | 8.709 | 1.213 | 8.659% | 496.8 | -0.4 | 10.787 | 8.831 | 10.3 | -0.103 | 1.221 | 8.659% | -8.03 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | STM | -0.102 | 203 | 40 | 0 | 70.3 | 132.7 | 139 | 6.3 | -0.57 | 6.843 | 4.203 | 1.628 | 5.482% | 140.4 | -0.8 | 8.515 | 4.26 | 7.7 | -0.103 | 1.999 | 4.529% | -2.93 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | GT | -0.102 | 104 | 35 | 0 | 51.7 | 52.3 | 57.6 | 5.3 | 0 | 5.284 | 2.135 | 2 | 3.341% | 60.4 | 0 | 8.107 | 2.167 | 8.1 | -0.103 | 2 | 2.208% | -1.09 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.102 | 104 | 35 | 0 | 36.1 | 67.9 | 72 | 4.1 | 0 | 4.109 | 2.135 | 1.925 | 4.319% | 76 | 0 | 8.125 | 2.167 | 8.1 | -0.103 | 2 | 2.208% | -1.42 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.102 | 657.6 | 250 | 75.9 | 11.1 | 570.6 | 587.6 | 17 | -0.5 | 17.531 | 10.14 | 1.729 | 6.578% | 589.8 | -0.7 | 19.96 | 10.283 | 19.2 | -0.103 | 1.941 | 5.881% | -5.05 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.102 | 49.7 | 24 | 0 | 16.5 | 33.2 | 34.6 | 1.4 | 0.01 | 1.445 | 1.021 | 1.416 | 6.055% | 39.6 | 0 | 6.424 | 1.036 | 6.4 | -0.103 | 2 | 1.338% | -0.88 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.102 | 49.7 | 24 | 0 | 16.8 | 32.9 | 34.2 | 1.3 | -0.07 | 1.366 | 1.021 | 1.338 | 6.521% | 37.9 | -0.1 | 5.12 | 1.037 | 5 | -0.103 | 2 | 1.712% | -1.11 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.102 | 472.6 | 240 | 27 | 153.4 | 292.2 | 307.2 | 15 | -0.53 | 15.519 | 7.767 | 1.998 | 5.358% | 323 | -0.7 | 31.496 | 7.876 | 30.8 | -0.103 | 2 | 2.635% | -1.61 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.102 | 171 | 70 | 0 | 28.7 | 142.3 | 152.5 | 10.2 | -0.27 | 10.453 | 2.981 | 2 | 2.853% | 154.6 | -0.4 | 12.587 | 3.023 | 12.3 | -0.103 | 2 | 2.389% | -1.96 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.102 | 55.8 | 22.5 | 0 | 10.2 | 45.6 | 47.4 | 1.8 | -0.03 | 1.765 | 1.146 | 1.541 | 5.286% | 47.7 | 0 | 2.068 | 1.163 | 2.1 | -0.103 | 1.778 | 4.575% | -3.68 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.102 | 55.9 | 22.5 | 0 | 9.9 | 46 | 47.6 | 1.6 | -0.02 | 1.61 | 1.146 | 1.404 | 5.957% | 47.5 | 0 | 1.57 | 1.164 | 1.5 | -0.103 | 1.349 | 6.416% | -5.19 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.102 | 502 | 35 | 0 | 462.4 | 39.6 | 42.5 | 2.9 | 0.09 | 2.763 | 7.398 | 0.373 | 29.45% | 40.5 | 0.1 | 0.738 | 7.539 | 0.9 | -0.103 | 0.098 | 95.81% | -7.42 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.102 | 25.7 | 8 | 0 | 17.1 | 8.6 | 8.6 | 0 | -0.01 | 0.021 | 0.527 | 0.039 | 0% | 8.6 | 0 | 0.016 | 0.536 | 0 | -0.103 | 0.031 | 0% |  | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.102 | 228.8 | 130 | 0 | 38.2 | 190.6 | 192.8 | 2.2 | 0.05 | 2.16 | 3.988 | 0.542 | 17.69% | 195.7 | 0.1 | 5.077 | 4.044 | 5.1 | -0.103 | 1.255 | 7.707% | -6.35 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.102 | 166 | 27 | 0 | 30.9 | 135.1 | 144.3 | 9.2 | -1.18 | 10.449 | 2.57 | 2 | 3.074% | 144 | -1.6 | 10.621 | 2.619 | 8.9 | -0.103 | 2 | 3.208% | -2.57 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.102 | 163 | 27 | 0 | 61.3 | 101.7 | 104.1 | 2.4 | 1.13 | 1.264 | 2.227 | 0.568 | 11.57% | 104.4 | 1.6 | 1.045 | 2.269 | 2.7 | -0.103 | 0.461 | 10.38% | -6.38 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.102 | 232 | 54 | 0 | 54.9 | 177.1 | 185 | 7.9 | 0.74 | 7.161 | 3.584 | 1.998 | 5% | 188 | 1 | 9.854 | 3.653 | 10.9 | -0.103 | 2 | 3.659% | -2.76 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.102 | 45 | 13 | 0 | 31.9 | 13.1 | 14.9 | 1.8 | 0 | 1.825 | 0.924 | 1.976 | 4.266% | 15 | 0 | 1.9 | 0.938 | 1.9 | -0.103 | 2 | 4.081% | -1.16 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | FOSS | -0.052 | 53.3 | 30 | 0 | 7.4 | 45.9 | 49.1 | 3.2 | 0.12 | 3.077 | 0.811 | 2 | 1.452% | 52.3 | 0.2 | 6.255 | 0.824 | 6.4 | -0.052 | 2 | 0.7262% | -0.62 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.052 | 53.3 | 30 | 0 | 7.5 | 45.8 | 48.8 | 3 | 0.05 | 2.928 | 0.811 | 2 | 1.549% | 51.3 | 0.1 | 5.42 | 0.824 | 5.5 | -0.052 | 2 | 0.845% | -0.72 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.052 | 53.3 | 30 | 0 | 9.7 | 43.6 | 45.1 | 1.5 | 0.24 | 1.238 | 0.811 | 1.526 | 3.098% | 48.9 | 0.3 | 4.951 | 0.824 | 5.3 | -0.052 | 2 | 0.8769% | -0.71 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.052 | 195 | 85 | 0 | 8.4 | 186.6 | 191.8 | 5.2 | -0.01 | 5.292 | 2.968 | 1.783 | 3.255% | 192.6 | 0 | 6.037 | 3.013 | 6 | -0.052 | 2 | 2.821% | -2.69 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.052 | 195 | 85 | 0 | 8.1 | 186.9 | 193.7 | 6.8 | -0.12 | 6.864 | 2.968 | 2 | 2.489% | 195.8 | -0.2 | 9.049 | 3.013 | 8.9 | -0.052 | 2 | 1.902% | -1.82 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.052 | 511.8 | 275 | 12 | 49.1 | 450.7 | 457.6 | 6.9 | 0.18 | 6.76 | 6.437 | 1.05 | 6.433% | 459.4 | 0.3 | 8.451 | 6.528 | 8.7 | -0.052 | 1.295 | 5.102% | -4.49 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.052 | 29.5 | 0 | 0 | 5.7 | 23.8 | 23.9 | 0.1 | -1.37 | 1.457 | 0.51 | 2 | 25.85% | 23.3 | -1.9 | 1.441 | 0.517 | -0.5 | -0.052 | 2 | -5.17% | 4.07 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | NG | FOSS | -0.052 | 217 | 62 | 0 | 24.8 | 192.2 | 194.4 | 2.2 | -0.04 | 2.198 | 2.949 | 0.745 | 8.574% | 196.4 | -0.1 | 4.293 | 3 | 4.2 | -0.052 | 1.431 | 4.491% | -3.95 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.052 | 230 | 60 | 0 | 26.1 | 203.9 | 206.9 | 3 | -0.22 | 3.184 | 2.695 | 1.181 | 6.663% | 206.9 | -0.3 | 3.324 | 2.741 | 3 | -0.052 | 1.213 | 6.663% | -5.87 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.052 | 412 | 70 | 0 | 45.3 | 366.7 | 373.6 | 6.9 | -0.17 | 7.017 | 4.453 | 1.576 | 5.183% | 377.6 | -0.2 | 11.145 | 4.529 | 10.9 | -0.052 | 2 | 3.281% | -2.91 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.052 | 560 | 135 | 0 | 65.9 | 494.1 | 500.8 | 6.7 | 0.55 | 6.079 | 9.417 | 0.645 | 7.248% | 501.5 | 0.8 | 6.651 | 9.543 | 7.4 | -0.052 | 0.697 | 6.562% | -5.78 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.052 | 785 | 300 | 0 | 76.3 | 708.7 | 724.4 | 15.7 | -0.75 | 16.423 | 12.71 | 1.292 | 4.335% | 725.2 | -1 | 17.592 | 12.88 | 16.5 | -0.052 | 1.366 | 4.125% | -3.72 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.052 | 400 | 125 | 0 | 30.9 | 369.1 | 372.7 | 3.6 | 0.02 | 3.561 | 5.429 | 0.656 | 9.638% | 373.4 | 0 | 4.214 | 5.501 | 4.3 | -0.052 | 0.766 | 8.069% | -7.43 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.052 | 400 | 125 | 0 | 30.3 | 369.7 | 376.2 | 6.5 | -0.1 | 6.608 | 5.421 | 1.219 | 5.338% | 374.9 | -0.1 | 5.382 | 5.493 | 5.2 | -0.052 | 0.98 | 6.672% | -6.16 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.052 | 420 | 70 | 0 | 51 | 369 | 374.4 | 5.4 | -0.49 | 5.848 | 6.304 | 0.928 | 6.746% | 376 | -0.7 | 7.645 | 6.388 | 7 | -0.052 | 1.197 | 5.204% | -4.56 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.052 | 410 | 70 | 0 | 44.9 | 365.1 | 371.2 | 6.1 | -0.35 | 6.43 | 6.754 | 0.952 | 5.83% | 367.8 | -0.5 | 3.132 | 6.844 | 2.7 | -0.052 | 0.458 | 13.17% | -11.71 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.052 | 624 | 456 | 1 | 31.2 | 591.8 | 604.4 | 12.6 | -0.39 | 12.994 | 8.024 | 1.619 | 4.294% | 606.1 | -0.5 | 14.885 | 8.137 | 14.3 | -0.052 | 1.829 | 3.784% | -3.58 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.052 | 103 | 12 | 0 | 18.9 | 84.1 | 85.8 | 1.7 | 0.71 | 0.958 | 1.677 | 0.571 | 5.268% | 85.6 | 1 | 0.506 | 1.7 | 1.5 | -0.052 | 0.297 | 5.97% | -4.84 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.052 | 315 | 50 | 0 | 41 | 274 | 285.7 | 11.7 | -0.07 | 11.813 | 4.409 | 2 | 2.336% | 286.5 | -0.1 | 12.618 | 4.467 | 12.5 | -0.052 | 2 | 2.186% | -1.9 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.052 | 420 | 50 | 0 | 43.5 | 376.5 | 390.5 | 14 | -0.36 | 14.357 | 6.192 | 2 | 2.602% | 390.1 | -0.5 | 14.089 | 6.275 | 13.6 | -0.052 | 2 | 2.679% | -2.4 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.052 | 212 | 130 | 0.1 | 39.2 | 172.7 | 179.8 | 7.1 | -0.09 | 7.226 | 2.729 | 2 | 2.592% | 179.7 | -0.1 | 7.211 | 2.767 | 7 | -0.052 | 2 | 2.629% | -2.13 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.052 | 95 | 0 | 0 | 9.4 | 85.6 | 96.6 | 11 | 1.49 | 9.462 | 1.224 | 2 | 0.7511% | 93.1 | 2.1 | 5.407 | 1.241 | 7.5 | -0.052 | 2 | 1.102% | -0.99 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.052 | 395 | 100 | 0 | 21.5 | 373.5 | 390.2 | 16.7 | -0.52 | 17.186 | 4.326 | 2 | 2.053% | 392.9 | -0.7 | 20.047 | 4.4 | 19.4 | -0.052 | 2 | 1.768% | -1.67 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.052 | 425 | 120 | 0 | 59.3 | 365.7 | 374.6 | 8.9 | -0.58 | 9.509 | 5.508 | 1.727 | 4.142% | 373.5 | -0.8 | 8.668 | 5.581 | 7.8 | -0.052 | 1.553 | 4.726% | -4.06 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.052 | 96 | 59 | 0 | 20.5 | 75.5 | 80.1 | 4.6 | 0 | 4.586 | 1.461 | 2 | 1.815% | 80 | 0 | 4.499 | 1.484 | 4.5 | -0.052 | 2 | 1.855% | -1.45 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.052 | 392 | 57 | 0 | 49.6 | 342.4 | 347.3 | 4.9 | 0.59 | 4.373 | 5.438 | 0.804 | 6.939% | 345.2 | 0.8 | 2.063 | 5.51 | 2.8 | -0.052 | 0.374 | 12.14% | -10.59 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | STM | -0.052 | 203 | 40 | 0 | 40.7 | 162.3 | 167.4 | 5.1 | 1.77 | 3.342 | 3.115 | 1.073 | 3.455% | 169.8 | 2.5 | 5.015 | 3.157 | 7.5 | -0.052 | 1.588 | 2.35% | -1.87 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | GT | -0.052 | 103 | 35 | 0 | 20.3 | 82.7 | 85.8 | 3.1 | -0.36 | 3.454 | 1.568 | 2 | 2.889% | 87.8 | -0.5 | 5.676 | 1.592 | 5.1 | -0.052 | 2 | 1.756% | -1.4 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | FOSS | -0.052 | 78 | 15 | 0 | 21.1 | 56.9 | 58.6 | 1.7 | 0.12 | 1.525 | 1.001 | 1.524 | 4.01% | 59.3 | 0.2 | 2.229 | 1.018 | 2.4 | -0.052 | 2 | 2.84% | -2.03 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.052 | 108 | 20 | 0 | 22.2 | 85.8 | 87.1 | 1.3 | 0 | 1.327 | 1.731 | 0.766 | 7.222% | 87.1 | 0 | 1.314 | 1.754 | 1.3 | -0.052 | 0.749 | 7.222% | -5.7 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.052 | 143 | 25 | 0 | 22 | 121 | 123.7 | 2.7 | -0.47 | 3.178 | 2.266 | 1.402 | 4.601% | 123 | -0.7 | 2.678 | 2.297 | 2 | -0.052 | 1.166 | 6.211% | -5.23 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.052 | 63 | 41 | 0 | 20.1 | 42.9 | 44.7 | 1.8 | 0.03 | 1.722 | 0.959 | 1.796 | 3.049% | 44.4 | 0 | 1.465 | 0.974 | 1.5 | -0.052 | 1.504 | 3.659% | -2.46 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.052 | 47.4 | 24 | 0 | 9 | 38.4 | 38.9 | 0.5 | 0.42 | 0.076 | 0.722 | 0.105 | 8.273% | 39.2 | 0.6 | 0.242 | 0.733 | 0.8 | -0.052 | 0.33 | 5.17% | -4.12 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.052 | 49.3 | 24 | 0 | 20.6 | 28.7 | 29.6 | 0.9 | -0.01 | 0.881 | 0.75 | 1.175 | 4.779% | 32 | 0 | 3.361 | 0.761 | 3.3 | -0.052 | 2 | 1.303% | -0.75 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.052 | 49 | 24 | 0 | 9.4 | 39.6 | 40.2 | 0.6 | -0.2 | 0.864 | 0.747 | 1.157 | 7.125% | 41.1 | -0.3 | 1.839 | 0.758 | 1.5 | -0.052 | 2 | 2.85% | -2.27 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.052 | 460 | 240 | 11.8 | 65.2 | 383 | 393.3 | 10.3 | 0 | 10.334 | 5.773 | 1.79 | 3.873% | 395.6 | 0 | 12.621 | 5.854 | 12.6 | -0.052 | 2 | 3.166% | -2.63 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.052 | 172 | 65 | 0 | 28.6 | 143.4 | 151.6 | 8.2 | -0.01 | 8.128 | 2.215 | 2 | 1.821% | 153.5 | 0 | 10.059 | 2.246 | 10.1 | -0.052 | 2 | 1.479% | -1.23 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.052 | 55.9 | 22.5 | 0 | 10 | 45.9 | 47.2 | 1.3 | 0.02 | 1.265 | 0.85 | 1.488 | 3.748% | 47.3 | 0 | 1.316 | 0.863 | 1.4 | -0.052 | 1.524 | 3.481% | -2.82 | 0.017 | 0.05 | 6.284% | 5.784%
Solar | SUN | PVGR | -0.052 | 71.8 | 0 | 0 | 65.4 | 6.4 | 6.4 | 0 | -0.03 | 0.089 | 1.24 | 0.072 | 0% | 6.6 | 0 | 0.218 | 1.257 | 0.2 | -0.052 | 0.174 | 31.25% | -2.63 | 0.017 | 0.05 | 6.014% | 6.718%
Solar | SUN | PVGR | -0.052 | 71.8 | 0 | 0 | 65.4 | 6.4 | 6.4 | 0 | 0.01 | 0.02 | 1.24 | 0.016 | 0% | 6.6 | 0 | 0.149 | 1.257 | 0.2 | -0.052 | 0.119 | 31.25% | -2.63 | 0.017 | 0.05 | 6.014% | 6.718%
Thermal | NG | FOSS | -0.052 | 57 | 15 | 0 | 11 | 46 | 47.1 | 1.1 | -0.12 | 1.271 | 0.94 | 1.352 | 4.517% | 46.6 | -0.2 | 0.786 | 0.953 | 0.6 | -0.052 | 0.825 | 8.281% | -6.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.052 | 61 | 15 | 0 | 14.7 | 46.3 | 46.9 | 0.6 | 0.06 | 0.526 | 1.006 | 0.523 | 8.858% | 46.6 | 0.1 | 0.246 | 1.02 | 0.3 | -0.052 | 0.242 | 17.72% | -13.28 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.052 | 229.5 | 130 | 0 | 36.3 | 193.2 | 195.7 | 2.5 | -0.03 | 2.506 | 2.956 | 0.848 | 7.967% | 198.1 | 0 | 4.886 | 2.997 | 4.9 | -0.052 | 1.63 | 4.065% | -3.41 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.052 | 45 | 13 | 0 | 31.8 | 13.2 | 14.2 | 1 | -0.24 | 1.237 | 0.685 | 1.806 | 3.928% | 15.1 | -0.3 | 2.236 | 0.695 | 1.9 | -0.052 | 2 | 2.068% | -0.59 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.052 | 45 | 13 | 0 | 31.2 | 13.8 | 14.9 | 1.1 | -0.24 | 1.303 | 0.685 | 1.901 | 3.571% | 15.4 | -0.3 | 1.936 | 0.695 | 1.6 | -0.052 | 2 | 2.455% | -0.73 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.083 | 515 | 275 | 12 | 152.3 | 350.7 | 364.5 | 13.8 | -0.59 | 14.404 | 9.148 | 1.575 | 5.164% | 369 | -0.8 | 19.149 | 8.336 | 18.3 | -0.077 | 2 | 3.613% | -2.65 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 512 | 337 | 60 | 97.8 | 354.2 | 361.7 | 7.5 | -1.3 | 8.838 | 8.22 | 1.075 | 9.447% | 363.5 | -1.8 | 11.149 | 7.491 | 9.3 | -0.077 | 1.488 | 7.068% | -5.27 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 564 | 256 | 89 | 216.8 | 258.2 | 281.9 | 23.7 | 0 | 23.651 | 8.638 | 2 | 3.293% | 286.3 | 0 | 28.086 | 7.872 | 28.1 | -0.077 | 2 | 2.577% | -1.27 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 164 | 105 | 6 | 52.7 | 105.3 | 108.4 | 3.1 | -0.24 | 3.42 | 2.873 | 1.19 | 7.327% | 108.2 | -0.3 | 3.278 | 2.618 | 2.9 | -0.077 | 1.252 | 7.267% | -5.01 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.083 | 560 | 135 | 0 | 309.2 | 250.8 | 261.9 | 11.1 | -0.81 | 11.916 | 10.019 | 1.189 | 6.982% | 262 | -1.1 | 12.276 | 9.152 | 11.2 | -0.077 | 1.341 | 6.419% | -3.1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 400 | 125 | 0 | 149.4 | 250.6 | 259.7 | 9.1 | -0.42 | 9.536 | 6.924 | 1.377 | 6.084% | 254.3 | -0.6 | 4.296 | 6.325 | 3.7 | -0.077 | 0.679 | 13.88% | -9.36 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 390 | 125 | 0 | 256.4 | 133.6 | 145.7 | 12.1 | 1.8 | 10.305 | 6.469 | 1.593 | 4.461% | 145.4 | 2.5 | 9.336 | 5.909 | 11.8 | -0.077 | 1.58 | 4.244% | -1.56 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.083 | 420 | 70 | 0 | 329.6 | 90.4 | 108.9 | 18.5 | -0.06 | 18.567 | 7.228 | 2 | 3.142% | 102 | -0.1 | 11.673 | 6.602 | 11.6 | -0.077 | 1.768 | 4.649% | -1.08 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.083 | 410 | 70 | 0 | 308.2 | 101.8 | 109.8 | 8 | 0.8 | 7.214 | 7.234 | 0.997 | 7.093% | 108.6 | 1.1 | 5.673 | 6.609 | 6.8 | -0.077 | 0.858 | 7.742% | -2.07 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.083 | 221 | 168 | 0 | 43.1 | 177.9 | 183.7 | 5.8 | 0.06 | 5.727 | 4.019 | 1.425 | 5.276% | 182.4 | 0.1 | 4.454 | 3.662 | 4.5 | -0.077 | 1.216 | 6.309% | -5.46 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 1110.5 | 430 | 140 | 171.3 | 799.2 | 837.9 | 38.7 | -0.28 | 38.911 | 17.649 | 2 | 3.97% | 833.4 | -0.4 | 34.512 | 16.083 | 34.2 | -0.077 | 2 | 4.168% | -3.23 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 592 | 376 | 95 | 90.9 | 406.1 | 412.1 | 6 | -0.11 | 6.079 | 9.038 | 0.673 | 13.65% | 412 | -0.2 | 6.017 | 8.236 | 5.9 | -0.077 | 0.731 | 12.88% | -9.52 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.083 | 650 | 275 | 0 | 308.8 | 341.2 | 357.5 | 16.3 | 0.6 | 15.697 | 13.649 | 1.15 | 5.518% | 354.9 | 0.8 | 12.816 | 12.468 | 13.7 | -0.077 | 1.028 | 6.091% | -3.44 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.083 | 625 | 456 | 20 | 126.9 | 478.1 | 498.5 | 20.4 | 0.03 | 20.343 | 11.002 | 1.849 | 4.24% | 498.5 | 0 | 20.344 | 10.026 | 20.4 | -0.077 | 2 | 3.933% | -3.24 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.083 | 420 | 50 | 0 | 369.9 | 50.1 | 71.7 | 21.6 | -0.43 | 22.037 | 6.5 | 2 | 2.691% | 74.1 | -0.6 | 24.593 | 5.937 | 24 | -0.077 | 2 | 2.247% | -0.29 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.083 | 35 | 4 | 0 | 29.3 | 5.7 | 15.5 | 9.8 | -1.09 | 10.891 | 0.637 | 2 | 0.4969% | 20.8 | -1.5 | 16.673 | 0.58 | 15.1 | -0.077 | 2 | 0.2993% | -0.05 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 465 | 315 | 12 | 10.7 | 442.3 | 452.6 | 10.3 | -0.65 | 10.953 | 8.238 | 1.33 | 6.248% | 453.2 | -0.9 | 11.76 | 7.507 | 10.9 | -0.077 | 1.567 | 5.477% | -5.61 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.083 | 581.2 | 155.4 | 0 | 24.9 | 556.3 | 571 | 14.7 | -0.21 | 14.908 | 9.743 | 1.53 | 5.471% | 569.9 | -0.3 | 13.866 | 8.9 | 13.6 | -0.077 | 1.558 | 5.486% | -5.66 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 581.2 | 155.4 | 0 | 24.9 | 556.3 | 571 | 14.7 | -0.21 | 14.908 | 9.743 | 1.53 | 5.471% | 569.9 | -0.3 | 13.866 | 8.9 | 13.6 | -0.077 | 1.558 | 5.486% | -5.66 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.083 | 534.1 | 220 | 128.9 | 93.7 | 311.5 | 316.8 | 5.3 | 0 | 5.35 | 7.367 | 0.726 | 13.95% | 322.6 | 0 | 11.142 | 6.714 | 11.1 | -0.077 | 1.66 | 6.178% | -3.88 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.083 | 470 | 180 | 0 | 289.2 | 180.8 | 195.5 | 14.7 | 0.01 | 14.716 | 5.429 | 2 | 4.427% | 190.3 | 0 | 9.464 | 4.812 | 9.5 | -0.077 | 1.967 | 6.355% | -2.63 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 470 | 180 | 0 | 289.2 | 180.8 | 195.5 | 14.7 | 0.01 | 14.716 | 5.429 | 2 | 4.427% | 190.3 | 0 | 9.464 | 4.812 | 9.5 | -0.077 | 1.967 | 6.355% | -2.63 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 470 | 180 | 0 | 289.2 | 180.8 | 195.5 | 14.7 | 0.01 | 14.716 | 5.429 | 2 | 4.427% | 190.3 | 0 | 9.464 | 4.812 | 9.5 | -0.077 | 1.967 | 6.355% | -2.63 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 470 | 180 | 0 | 289.2 | 180.8 | 195.5 | 14.7 | 0.01 | 14.716 | 5.429 | 2 | 4.427% | 190.3 | 0 | 9.464 | 4.812 | 9.5 | -0.077 | 1.967 | 6.355% | -2.63 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.083 | 489 | 348 | 48 | 92.2 | 348.8 | 364.9 | 16.1 | -0.3 | 16.48 | 8.02 | 2 | 4.203% | 363.1 | -0.4 | 14.719 | 7.308 | 14.3 | -0.077 | 2 | 4.39% | -3.37 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 489 | 348 | 43 | 80.3 | 365.7 | 383 | 17.3 | -2.47 | 19.744 | 8.111 | 2 | 3.912% | 381.4 | -3.4 | 19.094 | 7.391 | 15.7 | -0.077 | 2 | 3.999% | -3.22 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.083 | 220 | 150 | 8 | 29.4 | 182.6 | 184.3 | 1.7 | 0.03 | 1.684 | 4.374 | 0.385 | 17.92% | 182 | 0 | -0.664 | 3.995 | -0.6 | -0.077 | 0 | -47.1% | 42.05 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.083 | 220 | 150 | 8 | 35.7 | 176.3 | 176.6 | 0.3 | -0.04 | 0.365 | 4.288 | 0.085 | 101.5% | 175.8 | -0.1 | -0.406 | 3.918 | -0.5 | -0.077 | 0 | -56.52% | 48.72 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.083 | 228 | 150 | 8 | 30.8 | 189.2 | 191.1 | 1.9 | -0.68 | 2.572 | 4.629 | 0.556 | 16.61% | 190.8 | -0.9 | 2.558 | 4.229 | 1.6 | -0.077 | 0.605 | 18.31% | -16.34 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 161.9 | 0 | 40 | 78.4 | 43.5 | 55.1 | 11.6 | 0.51 | 11.117 | 2.217 | 2 | 1.933% | 61.2 | 0.7 | 16.947 | 2.02 | 17.7 | -0.077 | 2 | 1.175% | -0.34 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 595.3 | 260 | 113.6 | 104 | 377.7 | 383.7 | 6 | -0.63 | 6.57 | 8.759 | 0.75 | 13.73% | 388.2 | -0.9 | 11.349 | 7.982 | 10.5 | -0.077 | 1.422 | 7.279% | -4.97 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 601.5 | 260 | 115.2 | 108.5 | 377.8 | 384.6 | 6.8 | -0.3 | 7.101 | 8.843 | 0.803 | 12.24% | 389.4 | -0.4 | 11.992 | 8.058 | 11.6 | -0.077 | 1.488 | 6.657% | -4.5 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.083 | 804 | 260 | 0 | 435.8 | 368.2 | 390.3 | 22.1 | 0.9 | 21.227 | 13.037 | 1.628 | 5.034% | 392.5 | 1.3 | 23.065 | 11.909 | 24.3 | -0.077 | 1.937 | 4.247% | -2.09 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.083 | 836 | 258 | 0 | 459.1 | 376.9 | 393.4 | 16.5 | -2.5 | 18.975 | 14.085 | 1.347 | 7.011% | 393.8 | -3.5 | 20.336 | 12.867 | 16.9 | -0.077 | 1.581 | 6.35% | -3.08 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.083 | 785 | 280 | 0 | 18.4 | 766.6 | 774.9 | 8.3 | -1.3 | 9.673 | 18.725 | 0.517 | 13.09% | 772.6 | -1.8 | 7.879 | 17.105 | 6 | -0.077 | 0.461 | 16.79% | -17.67 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.083 | 825 | 310 | 0 | 63 | 762 | 772.5 | 10.5 | -6.31 | 16.797 | 19.679 | 0.854 | 10.87% | 772.2 | -8.8 | 18.897 | 17.977 | 10.2 | -0.077 | 1.051 | 10.38% | -10.33 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.083 | 674 | 434 | 50 | 76.9 | 547.1 | 558.6 | 11.5 | -1.18 | 12.748 | 11.348 | 1.123 | 8.11% | 565.6 | -1.6 | 20.163 | 10.341 | 18.5 | -0.077 | 1.95 | 4.677% | -4.09 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 312.1 | 134 | 73.2 | 12.6 | 226.3 | 234.9 | 8.6 | -0.16 | 8.848 | 4.343 | 2 | 5.024% | 235.7 | -0.2 | 9.707 | 3.958 | 9.4 | -0.077 | 2 | 4.264% | -3.33 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.083 | 650 | 189.5 | 0 | 276.2 | 373.8 | 388.9 | 15.1 | -0.68 | 15.736 | 9.379 | 1.678 | 5.957% | 386.4 | -1 | 13.507 | 8.567 | 12.6 | -0.077 | 1.577 | 6.623% | -4.1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 650 | 189.5 | 0 | 276.2 | 373.8 | 388.9 | 15.1 | -0.68 | 15.736 | 9.379 | 1.678 | 5.957% | 386.4 | -1 | 13.507 | 8.567 | 12.6 | -0.077 | 1.577 | 6.623% | -4.1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 650 | 189.5 | 0 | 276.2 | 373.8 | 388.9 | 15.1 | -0.68 | 15.736 | 9.379 | 1.678 | 5.957% | 386.4 | -1 | 13.507 | 8.567 | 12.6 | -0.077 | 1.577 | 6.623% | -4.1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 650 | 189.5 | 0 | 276.2 | 373.8 | 388.9 | 15.1 | -0.68 | 15.736 | 9.379 | 1.678 | 5.957% | 386.4 | -1 | 13.507 | 8.567 | 12.6 | -0.077 | 1.577 | 6.623% | -4.1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 650 | 189.5 | 0 | 276.2 | 373.8 | 388.9 | 15.1 | -0.68 | 15.736 | 9.379 | 1.678 | 5.957% | 386.4 | -1 | 13.507 | 8.567 | 12.6 | -0.077 | 1.577 | 6.623% | -4.1 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.083 | 715.8 | 408.8 | 90 | 117 | 508.8 | 522 | 13.2 | 0.47 | 12.712 | 11.381 | 1.117 | 7.504% | 522 | 0.7 | 12.515 | 10.371 | 13.2 | -0.077 | 1.207 | 6.961% | -5.33 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 712 | 441 | 46.7 | 205.5 | 459.8 | 487.2 | 27.4 | -0.12 | 27.543 | 12.1 | 2 | 3.596% | 497.8 | -0.2 | 38.214 | 11.026 | 38 | -0.077 | 2 | 2.405% | -1.67 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 713.8 | 440.9 | 64.2 | 208.4 | 441.2 | 461.5 | 20.3 | -0.35 | 20.702 | 11.814 | 1.752 | 4.866% | 468 | -0.5 | 27.328 | 10.765 | 26.8 | -0.077 | 2 | 3.419% | -2.28 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 484.3 | 235 | 12.9 | 233 | 238.4 | 254.7 | 16.3 | -0.41 | 16.623 | 8.573 | 1.939 | 4.112% | 256 | -0.6 | 18.132 | 7.812 | 17.6 | -0.077 | 2 | 3.533% | -1.87 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 495 | 365 | 15 | 98.1 | 381.9 | 392.1 | 10.2 | -1.59 | 11.772 | 8.729 | 1.349 | 6.716% | 394.4 | -2.2 | 14.745 | 7.955 | 12.5 | -0.077 | 1.854 | 5.084% | -4.22 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 687 | 420 | 0 | 200.6 | 486.4 | 510.7 | 24.3 | -0.47 | 24.776 | 12.494 | 1.983 | 3.912% | 509.2 | -0.7 | 23.512 | 11.385 | 22.8 | -0.077 | 2 | 3.868% | -2.95 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 274.9 | 118 | 60 | 41.7 | 173.2 | 179.4 | 6.2 | 0.23 | 5.922 | 3.908 | 1.515 | 6.138% | 179.3 | 0.3 | 5.699 | 3.562 | 6.1 | -0.077 | 1.6 | 5.788% | -3.92 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.083 | 932.6 | 360 | 0 | 33.4 | 899.2 | 913 | 13.8 | -0.04 | 13.82 | 15.913 | 0.868 | 9.351% | 916.9 | -0.1 | 17.738 | 14.536 | 17.7 | -0.077 | 1.22 | 6.763% | -7.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 932.6 | 360 | 0 | 33.4 | 899.2 | 913 | 13.8 | -0.04 | 13.82 | 15.913 | 0.868 | 9.351% | 916.9 | -0.1 | 17.738 | 14.536 | 17.7 | -0.077 | 1.22 | 6.763% | -7.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 932.6 | 360 | 0 | 33.4 | 899.2 | 913 | 13.8 | -0.04 | 13.82 | 15.913 | 0.868 | 9.351% | 916.9 | -0.1 | 17.738 | 14.536 | 17.7 | -0.077 | 1.22 | 6.763% | -7.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 932.6 | 360 | 0 | 33.4 | 899.2 | 913 | 13.8 | -0.04 | 13.82 | 15.913 | 0.868 | 9.351% | 916.9 | -0.1 | 17.738 | 14.536 | 17.7 | -0.077 | 1.22 | 6.763% | -7.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.083 | 79 | 58 | 0 | 19.4 | 59.6 | 61.9 | 2.3 | -0.15 | 2.462 | 1.692 | 1.455 | 4.764% | 61.7 | -0.2 | 2.289 | 1.529 | 2.1 | -0.077 | 1.497 | 4.841% | -3.91 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 832 | 465 | 123.6 | 211.3 | 497.1 | 518.1 | 21 | -0.93 | 21.996 | 12.883 | 1.707 | 5.482% | 520.4 | -1.3 | 24.677 | 11.74 | 23.3 | -0.077 | 2 | 4.584% | -2.95 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 78 | 60 | 3 | 12.4 | 62.6 | 64.7 | 2.1 | 0.06 | 2.026 | 1.364 | 1.485 | 5.152% | 65.2 | 0.1 | 2.496 | 1.243 | 2.6 | -0.077 | 2 | 3.861% | -3.32 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 276 | 165 | 35 | 75.4 | 165.6 | 176.9 | 11.3 | -0.33 | 11.659 | 4.383 | 2 | 3.381% | 178.3 | -0.5 | 13.226 | 3.994 | 12.7 | -0.077 | 2 | 2.791% | -1.8 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.083 | 667 | 156 | 0 | 196.1 | 470.9 | 490.5 | 19.6 | -0.88 | 20.498 | 12.984 | 1.579 | 4.709% | 489.5 | -1.2 | 19.784 | 11.861 | 18.6 | -0.077 | 1.668 | 4.604% | -3.5 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.083 | 663 | 156 | 0 | 219 | 444 | 459.5 | 15.5 | -0.73 | 16.243 | 13.118 | 1.238 | 5.919% | 459.8 | -1 | 16.91 | 11.983 | 15.8 | -0.077 | 1.411 | 5.387% | -3.89 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.083 | 574 | 159 | 0 | 126.6 | 447.4 | 458.4 | 11 | -1.51 | 12.511 | 10.989 | 1.138 | 7.221% | 459.1 | -2.1 | 13.789 | 10.039 | 11.7 | -0.077 | 1.374 | 6.298% | -5.29 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.083 | 610 | 303 | 0 | 122.8 | 487.2 | 497.8 | 10.6 | -0.36 | 10.886 | 11.451 | 0.951 | 7.963% | 496.1 | -0.5 | 9.403 | 10.461 | 8.9 | -0.077 | 0.899 | 8.799% | -7.57 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.083 | 643 | 300 | 0 | 312.9 | 330.1 | 347.6 | 17.5 | 0.86 | 16.666 | 11.694 | 1.425 | 5.084% | 353.8 | 1.2 | 22.554 | 10.656 | 23.7 | -0.077 | 2 | 3.483% | -1.93 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 1118 | 379 | 152 | 107.8 | 858.2 | 891.6 | 33.4 | -2.31 | 35.686 | 17.568 | 2 | 4.631% | 894.9 | -3.2 | 39.906 | 16.009 | 36.7 | -0.077 | 2 | 3.91% | -3.23 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.05 | 47 | 25 | 0 | 7 | 40 | 41.6 | 1.6 | -0.22 | 1.838 | 0.614 | 2 | 2.466% | 43.8 | -0.3 | 4.132 | 0.63 | 3.8 | -0.051 | 2 | 1.059% | -0.87 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.05 | 53.2 | 30 | 0 | 7.1 | 46.1 | 47.9 | 1.8 | -0.08 | 1.915 | 0.695 | 2 | 2.479% | 50.1 | -0.1 | 4.107 | 0.713 | 4 | -0.051 | 2 | 1.138% | -0.95 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.05 | 53.2 | 30 | 0 | 7.1 | 46.1 | 47.7 | 1.6 | -0.28 | 1.902 | 0.695 | 2 | 2.789% | 50.3 | -0.4 | 4.574 | 0.713 | 4.2 | -0.051 | 2 | 1.083% | -0.91 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.05 | 511.8 | 275 | 12 | 38.6 | 461.2 | 464.7 | 3.5 | -0.89 | 4.426 | 5.531 | 0.8 | 12.19% | 465.7 | -1.2 | 5.744 | 5.662 | 4.5 | -0.051 | 1.015 | 9.674% | -8.53 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.05 | 420 | 70 | 0 | 94.5 | 325.5 | 332.1 | 6.6 | -0.02 | 6.672 | 5.475 | 1.219 | 5.307% | 332.2 | 0 | 6.812 | 5.599 | 6.7 | -0.051 | 1.217 | 5.333% | -4.04 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.05 | 410 | 70 | 0 | 114 | 296 | 310.3 | 14.3 | 5.77 | 8.535 | 5.755 | 1.483 | 2.391% | 316.9 | 8 | 12.865 | 5.886 | 20.9 | -0.051 | 2 | 1.669% | -1.18 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.05 | 622 | 456 | 16 | 77 | 529 | 535.3 | 6.3 | -3.59 | 9.976 | 6.706 | 1.488 | 8.232% | 536.1 | -5 | 12.142 | 6.865 | 7.1 | -0.051 | 1.769 | 7.45% | -6.2 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.05 | 103 | 12 | 0 | 90.2 | 12.8 | 14.5 | 1.7 | 0.2 | 1.43 | 1.505 | 0.95 | 5.066% | 14.4 | 0.3 | 1.278 | 1.539 | 1.6 | -0.051 | 0.831 | 5.49% | -0.65 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.05 | 420 | 50 | 0 | 88.9 | 331.1 | 346.3 | 15.2 | 2.2 | 12.96 | 5.391 | 2 | 2.304% | 348.1 | 3.1 | 13.89 | 5.513 | 17 | -0.051 | 2 | 2.102% | -1.62 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.05 | 212 | 130 | 0.6 | 24.1 | 187.3 | 188.7 | 1.4 | -0.56 | 1.974 | 2.339 | 0.844 | 12.64% | 188.6 | -0.8 | 2.01 | 2.395 | 1.3 | -0.051 | 0.839 | 13.88% | -11.98 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.05 | 573.4 | 155.4 | 0 | 24.7 | 548.7 | 559.6 | 10.9 | -0.96 | 11.849 | 5.978 | 1.982 | 4.386% | 559.3 | -1.3 | 11.905 | 6.114 | 10.6 | -0.051 | 1.947 | 4.601% | -4.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.05 | 573.4 | 155.4 | 0 | 24.7 | 548.7 | 559.6 | 10.9 | -0.96 | 11.849 | 5.978 | 1.982 | 4.386% | 559.3 | -1.3 | 11.905 | 6.114 | 10.6 | -0.051 | 1.947 | 4.601% | -4.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.05 | 580.9 | 155.3 | 0 | 13.9 | 567 | 581.6 | 14.6 | -2.02 | 16.579 | 5.994 | 2 | 3.318% | 580.5 | -2.8 | 16.289 | 6.13 | 13.5 | -0.051 | 2 | 3.66% | -3.5 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.05 | 580.9 | 155.3 | 0 | 13.9 | 567 | 581.6 | 14.6 | -2.02 | 16.579 | 5.994 | 2 | 3.318% | 580.5 | -2.8 | 16.289 | 6.13 | 13.5 | -0.051 | 2 | 3.66% | -3.5 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | STM | -0.05 | 305.1 | 60 | 0 | 60.7 | 244.4 | 249.8 | 5.4 | 0.04 | 5.368 | 4.32 | 1.242 | 4.714% | 249.1 | 0.1 | 4.641 | 4.419 | 4.7 | -0.051 | 1.05 | 5.524% | -4.33 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | COGN | -0.05 | 214 | 150 | 0 | 16.9 | 197.1 | 203.6 | 6.5 | 2.09 | 4.451 | 2.85 | 1.562 | 2.748% | 203.2 | 2.9 | 3.169 | 2.915 | 6.1 | -0.051 | 1.087 | 2.987% | -2.69 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.05 | 435 | 120 | 0 | 207.6 | 227.4 | 233.6 | 6.2 | -2.47 | 8.637 | 5.417 | 1.594 | 5.851% | 234.7 | -3.4 | 10.75 | 5.54 | 7.3 | -0.051 | 1.94 | 5.069% | -2.59 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.05 | 435 | 120 | 0 | 314.6 | 120.4 | 128.5 | 8.1 | 0.44 | 7.64 | 5.867 | 1.302 | 4.479% | 128.9 | 0.6 | 7.816 | 6 | 8.5 | -0.051 | 1.303 | 4.353% | -1.18 | 0.017 | 0.05 | 6.284% | 5.784%
Solar | SUN | PVGR | -0.05 | 21.5 | 0 | 0 | 17.9 | 3.6 | 4.7 | 1.1 | -0.19 | 1.31 | 0.318 | 2 | 1.655% | 4.5 | -0.3 | 1.226 | 0.325 | 0.9 | -0.051 | 2 | 2.062% | -0.3 | 0.017 | 0.05 | 6.014% | 6.718%
CombinedCycle | CC | COGN | -0.05 | 603 | 305 | 122 | 72.4 | 408.6 | 414.5 | 5.9 | -0.66 | 6.556 | 5.323 | 1.232 | 8.522% | 415.1 | -0.9 | 7.432 | 5.449 | 6.5 | -0.051 | 1.364 | 7.89% | -5.23 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.05 | 615 | 305 | 129 | 72.1 | 413.9 | 417.8 | 3.9 | 0.36 | 3.528 | 5.378 | 0.656 | 13.15% | 418 | 0.5 | 3.685 | 5.506 | 4.1 | -0.051 | 0.669 | 12.76% | -8.41 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.05 | 95 | 59 | 0 | 20.4 | 74.6 | 77.7 | 3.1 | 0 | 3.124 | 1.241 | 2 | 2.563% | 77.6 | 0 | 3.039 | 1.273 | 3 | -0.051 | 2 | 2.701% | -2.06 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | STM | -0.05 | 67 | 20 | 0 | 42.2 | 24.8 | 25.9 | 1.1 | 0.77 | 0.27 | 0.964 | 0.28 | 5.102% | 26 | 1.1 | 0.082 | 0.986 | 1.2 | -0.051 | 0.083 | 4.769% | -1.7 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.05 | 115 | 38 | 0 | 32.7 | 82.3 | 84.5 | 2.2 | 0.89 | 1.309 | 1.643 | 0.797 | 4.369% | 84.1 | 1.2 | 0.557 | 1.68 | 1.8 | -0.051 | 0.331 | 5.446% | -3.79 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.05 | 205 | 40 | 0 | 52.1 | 152.9 | 158.6 | 5.7 | 3.1 | 2.548 | 2.704 | 0.942 | 3.002% | 161.8 | 4.3 | 4.596 | 2.766 | 8.9 | -0.051 | 1.662 | 1.961% | -1.43 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | GT | -0.05 | 103 | 35 | 0 | 36.2 | 66.8 | 74.9 | 8.1 | 3.09 | 4.97 | 1.346 | 2 | 1.063% | 79 | 4.3 | 7.87 | 1.38 | 12.2 | -0.051 | 2 | 0.7199% | -0.45 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.05 | 103 | 35 | 0 | 22.4 | 80.6 | 86.6 | 6 | 2.83 | 3.139 | 1.346 | 2 | 1.435% | 90.1 | 3.9 | 5.59 | 1.38 | 9.5 | -0.051 | 2 | 0.9246% | -0.7 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.05 | 700 | 432 | 6.6 | 32.9 | 660.5 | 672.1 | 11.6 | -0.59 | 12.165 | 7.674 | 1.585 | 5.031% | 671.8 | -0.8 | 12.142 | 7.855 | 11.3 | -0.051 | 1.546 | 5.268% | -4.87 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.05 | 697.7 | 431.8 | 43.3 | 172.9 | 481.5 | 491 | 9.5 | -3.6 | 13.125 | 7.242 | 1.812 | 6.123% | 495.1 | -5 | 18.615 | 7.413 | 13.6 | -0.051 | 2 | 4.363% | -2.95 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.05 | 49.6 | 24 | 0 | 13.7 | 35.9 | 39.1 | 3.2 | 1.25 | 2.021 | 0.649 | 2 | 1.301% | 43.3 | 1.7 | 5.64 | 0.665 | 7.4 | -0.051 | 2 | 0.5736% | -0.4 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.05 | 49.7 | 24 | 0 | 13.6 | 36.1 | 38.4 | 2.3 | 0.97 | 1.362 | 0.649 | 2 | 1.813% | 43.8 | 1.3 | 6.32 | 0.666 | 7.7 | -0.051 | 2 | 0.5523% | -0.39 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.05 | 474.6 | 235 | 12.2 | 95 | 367.4 | 380.6 | 13.2 | 1.12 | 12.093 | 5.117 | 2 | 2.998% | 384.2 | 1.6 | 15.226 | 5.238 | 16.8 | -0.051 | 2 | 2.403% | -1.82 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.05 | 169 | 60 | 0 | 39.4 | 129.6 | 140.6 | 11 | 1.77 | 9.221 | 1.87 | 2 | 1.283% | 140.8 | 2.5 | 8.707 | 1.915 | 11.2 | -0.051 | 2 | 1.285% | -0.96 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.05 | 55.6 | 22.5 | 0 | 9.9 | 45.7 | 47.1 | 1.4 | -0.14 | 1.484 | 0.727 | 2 | 3.33% | 48.4 | -0.2 | 2.864 | 0.745 | 2.7 | -0.051 | 2 | 1.761% | -1.4 | 0.017 | 0.05 | 6.284% | 5.784%
Solar | SUN | PVGR | -0.05 | 78.7 | 0 | 0 | 59.3 | 19.4 | 20.3 | 0.9 | -0.03 | 0.937 | 1.162 | 0.807 | 7.319% | 20.4 | 0 | 1.013 | 1.188 | 1 | -0.051 | 0.852 | 6.718% | -1.59 | 0.017 | 0.05 | 6.014% | 6.718%
Solar | SUN | PVGR | -0.05 | 78.7 | 0 | 0 | 59.3 | 19.4 | 20.3 | 0.9 | -0.07 | 0.957 | 1.162 | 0.824 | 7.319% | 20.4 | -0.1 | 1.05 | 1.188 | 1 | -0.051 | 0.884 | 6.718% | -1.59 | 0.017 | 0.05 | 6.014% | 6.718%
Solar | SUN | PVGR | -0.05 | 150 | 0 | 0 | 97.9 | 52.1 | 53 | 0.9 | -0.06 | 0.994 | 2.213 | 0.449 | 13.92% | 53 | -0.1 | 0.971 | 2.263 | 0.9 | -0.051 | 0.429 | 14.2% | -4.79 | 0.017 | 0.05 | 6.014% | 6.718%
CombinedCycle | CC | COGN | -0.05 | 683 | 420 | 0 | 71.3 | 611.7 | 628.1 | 16.4 | -0.81 | 17.165 | 7.558 | 2 | 3.472% | 629.3 | -1.1 | 18.681 | 7.737 | 17.6 | -0.051 | 2 | 3.3% | -2.89 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.05 | 270.7 | 118 | 60 | 42.7 | 168 | 171.1 | 3.1 | 0.46 | 2.677 | 2.331 | 1.148 | 7.286% | 170.4 | 0.6 | 1.738 | 2.387 | 2.4 | -0.051 | 0.728 | 9.599% | -5.82 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.05 | 47 | 15 | 0 | 12.9 | 34.1 | 41.7 | 7.6 | 5.99 | 1.565 | 0.614 | 2 | 0.5191% | 42 | 8.3 | -0.443 | 0.63 | 7.9 | -0.051 | 0 | 0.5093% | -0.36 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.05 | 228.8 | 130 | 0 | 31.5 | 197.3 | 199.5 | 2.2 | -0.42 | 2.679 | 2.532 | 1.058 | 8.68% | 200.5 | -0.6 | 3.826 | 2.592 | 3.2 | -0.051 | 1.476 | 6.086% | -5.13 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.05 | 166 | 142 | 0 | 11.4 | 154.6 | 160.4 | 5.8 | 0.1 | 5.726 | 1.403 | 2 | 2.395% | 160.6 | 0.1 | 5.852 | 1.455 | 6 | -0.051 | 2 | 2.361% | -2.14 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.05 | 163 | 27 | 0 | 55.2 | 107.8 | 110.7 | 2.9 | 0.95 | 1.906 | 1.285 | 1.483 | 4.703% | 111.1 | 1.3 | 1.977 | 1.332 | 3.3 | -0.051 | 1.484 | 4.216% | -2.71 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.05 | 630 | 300 | 0 | 72.1 | 557.9 | 565.9 | 8 | -2.59 | 10.554 | 6.972 | 1.514 | 6.566% | 563.4 | -3.6 | 9.051 | 7.137 | 5.5 | -0.051 | 1.268 | 9.742% | -8.45 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.041 | 265 | 60 | 0 | 168.8 | 96.2 | 96.2 | 0 | -0.06 | 0.116 | 1.15 | 0.101 | 0% | 96.4 | -0.1 | 0.273 | 1.197 | 0.2 | -0.042 | 0.228 | 93.03% | -32.58 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.041 | 195 | 161 | 0 | 32.1 | 162.9 | 167.2 | 4.3 | -0.28 | 4.599 | 1.76 | 2 | 3.105% | 167 | -0.4 | 4.582 | 1.8 | 4.1 | -0.042 | 2 | 3.336% | -2.71 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.041 | 390 | 125 | 0 | 39.7 | 350.3 | 347.7 | -2.6 | -4.63 | 2.1 | 3.696 | 0.568 | -10.26% | 344.8 | -6.4 | 0.956 | 3.776 | -5.5 | -0.042 | 0.253 | -4.969% | 4.35 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.041 | 420 | 70 | 0 | 322.3 | 97.7 | 94 | -3.7 | -5.68 | 1.988 | 3.699 | 0.537 | -7.764% | 97.3 | -7.9 | 7.447 | 3.779 | -0.4 | -0.042 | 1.971 | -73.57% | 16.62 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.041 | 410 | 70 | 0 | 315 | 95 | 91.9 | -3.1 | -4.8 | 1.748 | 3.691 | 0.474 | -9.047% | 90.3 | -6.7 | 2.008 | 3.77 | -4.7 | -0.042 | 0.532 | -6.112% | 1.38 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.041 | 737 | 310 | 0 | 400.5 | 336.5 | 352.6 | 16.1 | 4.55 | 11.494 | 4.343 | 2 | 3.132% | 354.4 | 6.3 | 11.534 | 4.519 | 17.9 | -0.042 | 2 | 2.885% | -1.28 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.041 | 650 | 275 | 0 | 25.8 | 624.2 | 630.8 | 6.6 | 0 | 6.568 | 6.708 | 0.979 | 6.734% | 631.6 | 0 | 7.359 | 6.853 | 7.4 | -0.042 | 1.074 | 6.152% | -5.76 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.041 | 624 | 456 | 6 | 91.3 | 526.7 | 537 | 10.3 | -0.73 | 11.024 | 5.578 | 1.976 | 4.143% | 538.1 | -1 | 12.496 | 5.705 | 11.4 | -0.042 | 2 | 3.834% | -3.15 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.041 | 103 | 12 | 0 | 89.9 | 13.1 | 13.7 | 0.6 | 0.28 | 0.347 | 1.239 | 0.28 | 11.78% | 13.6 | 0.4 | 0.177 | 1.266 | 0.5 | -0.042 | 0.14 | 14.48% | -1.73 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.041 | 314 | 50 | 0 | 236.8 | 77.2 | 84 | 6.8 | 1.86 | 4.947 | 2.688 | 1.84 | 3.16% | 83.6 | 2.6 | 3.778 | 2.746 | 6.4 | -0.042 | 1.376 | 3.439% | -0.82 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.041 | 420 | 50 | 0 | 366.5 | 53.5 | 62.9 | 9.4 | 0.39 | 8.953 | 3.32 | 2 | 3.056% | 64 | 0.5 | 9.952 | 3.391 | 10.5 | -0.042 | 2 | 2.803% | -0.35 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.041 | 514.9 | 337 | 0 | 58 | 456.9 | 465 | 8.1 | 1.22 | 6.851 | 4.648 | 1.474 | 4.347% | 465.6 | 1.7 | 6.945 | 4.753 | 8.7 | -0.042 | 1.461 | 4.146% | -3.59 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.041 | 581.7 | 155.4 | 0 | 28.4 | 553.3 | 563.7 | 10.4 | 0.64 | 9.769 | 4.985 | 1.96 | 3.825% | 564.5 | 0.9 | 10.312 | 5.092 | 11.2 | -0.042 | 2 | 3.638% | -3.37 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.041 | 581.7 | 155.4 | 0 | 28.4 | 553.3 | 563.7 | 10.4 | 0.64 | 9.769 | 4.985 | 1.96 | 3.825% | 564.5 | 0.9 | 10.312 | 5.092 | 11.2 | -0.042 | 2 | 3.638% | -3.37 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.041 | 583.3 | 155.3 | 0 | 12.5 | 570.8 | 582.1 | 11.3 | 1.49 | 9.886 | 4.954 | 1.995 | 3.53% | 582.1 | 2.1 | 9.284 | 5.061 | 11.3 | -0.042 | 1.834 | 3.616% | -3.45 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.041 | 583.3 | 155.3 | 0 | 12.5 | 570.8 | 582.1 | 11.3 | 1.49 | 9.886 | 4.954 | 1.995 | 3.53% | 582.1 | 2.1 | 9.284 | 5.061 | 11.3 | -0.042 | 1.834 | 3.616% | -3.45 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.041 | 470 | 180 | 0 | 15.4 | 454.6 | 454.7 | 0.1 | -0.15 | 0.251 | 2.333 | 0.108 | 321.7% | 454.7 | -0.2 | 0.315 | 2.428 | 0.1 | -0.042 | 0.13 | 329.6% | -310.08 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.041 | 470 | 180 | 0 | 15.4 | 454.6 | 454.7 | 0.1 | -0.15 | 0.251 | 2.333 | 0.108 | 321.7% | 454.7 | -0.2 | 0.315 | 2.428 | 0.1 | -0.042 | 0.13 | 329.6% | -310.08 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.041 | 470 | 180 | 0 | 15.4 | 454.6 | 454.7 | 0.1 | -0.15 | 0.251 | 2.333 | 0.108 | 321.7% | 454.7 | -0.2 | 0.315 | 2.428 | 0.1 | -0.042 | 0.13 | 329.6% | -310.08 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.041 | 470 | 180 | 0 | 15.4 | 454.6 | 454.7 | 0.1 | -0.15 | 0.251 | 2.333 | 0.108 | 321.7% | 454.7 | -0.2 | 0.315 | 2.428 | 0.1 | -0.042 | 0.13 | 329.6% | -310.08 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | STM | -0.041 | 304 | 60 | 0 | 6.7 | 297.3 | 302.6 | 5.3 | 0.38 | 4.94 | 3.512 | 1.406 | 3.925% | 302.5 | 0.5 | 4.728 | 3.588 | 5.2 | -0.042 | 1.318 | 4.098% | -3.9 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | COGN | -0.041 | 214 | 150 | 0 | 19.9 | 194.1 | 198.1 | 4 | -0.4 | 4.361 | 2.325 | 1.875 | 3.663% | 198.2 | -0.6 | 4.682 | 2.376 | 4.1 | -0.042 | 1.971 | 3.661% | -3.23 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.041 | 214 | 150 | 0 | 19.5 | 194.5 | 197.6 | 3.1 | -0.88 | 3.986 | 2.328 | 1.712 | 4.726% | 198.3 | -1.2 | 5.04 | 2.378 | 3.8 | -0.042 | 2 | 3.95% | -3.49 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.041 | 215 | 150 | 0 | 18.7 | 196.3 | 198.3 | 2 | -0.08 | 2.111 | 2.351 | 0.898 | 7.36% | 199.1 | -0.1 | 2.929 | 2.402 | 2.8 | -0.042 | 1.219 | 5.385% | -4.78 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.041 | 222 | 150 | 0 | 6.2 | 215.8 | 217.7 | 1.9 | 0 | 1.839 | 2.577 | 0.714 | 7.999% | 217.7 | 0 | 1.823 | 2.632 | 1.9 | -0.042 | 0.693 | 8.194% | -7.75 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.041 | 375 | 100 | 0 | 49.9 | 325.1 | 332.8 | 7.7 | -1.3 | 9.051 | 1.92 | 2 | 3.335% | 335.3 | -1.8 | 12.024 | 1.999 | 10.2 | -0.042 | 2 | 2.579% | -2.17 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.041 | 435 | 120 | 0 | 279.4 | 155.6 | 166.1 | 10.5 | 5.08 | 5.384 | 4.697 | 1.146 | 2.834% | 167.8 | 7.1 | 5.094 | 4.798 | 12.2 | -0.042 | 1.062 | 2.498% | -0.87 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.041 | 141 | 0 | 40 | 7.9 | 93.1 | 99.1 | 6 | 3.83 | 2.199 | 0.912 | 2 | 1.611% | 99.4 | 5.3 | 0.983 | 0.932 | 6.3 | -0.042 | 1.054 | 1.571% | -1.01 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.041 | 578 | 305 | 127 | 93.4 | 357.6 | 361.1 | 3.5 | -0.09 | 3.557 | 4.071 | 0.874 | 11.29% | 362.1 | -0.1 | 4.685 | 4.163 | 4.5 | -0.042 | 1.125 | 8.997% | -5.42 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.041 | 580 | 305 | 126 | 93.5 | 360.5 | 364.2 | 3.7 | -0.68 | 4.418 | 4.098 | 1.078 | 10.72% | 364.6 | -1 | 5.074 | 4.191 | 4.1 | -0.042 | 1.211 | 9.909% | -6 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.041 | 90 | 59 | 0 | 19.5 | 70.5 | 73.4 | 2.9 | 0 | 2.856 | 0.961 | 2 | 2.13% | 73.7 | 0 | 3.15 | 0.984 | 3.2 | -0.042 | 2 | 1.978% | -1.5 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | GT | -0.041 | 228 | 150 | 16 | 4.8 | 207.2 | 208 | 0.8 | -2.1 | 2.943 | 2.055 | 1.432 | 19.51% | 208 | -2.9 | 3.686 | 2.1 | 0.8 | -0.042 | 1.756 | 19.99% | -17.66 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.041 | 231 | 150 | 16 | 5.1 | 209.9 | 210.9 | 1 | -2.47 | 3.518 | 2.098 | 1.677 | 15.81% | 211 | -3.4 | 4.575 | 2.143 | 1.1 | -0.042 | 2 | 14.73% | -13.01 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.041 | 246 | 110 | 16 | 5 | 225 | 226.2 | 1.2 | -2.14 | 3.317 | 2.246 | 1.477 | 14.03% | 226 | -3 | 3.952 | 2.295 | 1 | -0.042 | 1.722 | 17.25% | -15.35 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.041 | 115 | 38 | 0 | 76.8 | 38.2 | 40 | 1.8 | -0.04 | 1.862 | 1.375 | 1.354 | 4.381% | 40.7 | -0.1 | 2.595 | 1.405 | 2.5 | -0.042 | 1.847 | 3.231% | -1.03 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | NG | STM | -0.041 | 205 | 40 | 0 | 162.4 | 42.6 | 46.2 | 3.6 | -1.25 | 4.852 | 2.412 | 2 | 3.899% | 48.7 | -1.7 | 7.785 | 2.464 | 6.1 | -0.042 | 2 | 2.357% | -0.47 | 0.017 | 0.05 | 5.146% | 4.85%
CombinedCycle | CC | COGN | -0.041 | 669 | 426 | 26 | 45.3 | 597.7 | 608.1 | 10.4 | 7.49 | 2.874 | 5.804 | 0.495 | 4.398% | 612.9 | 10.4 | 4.738 | 5.936 | 15.2 | -0.042 | 0.798 | 3.083% | -2.69 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.041 | 647.9 | 250 | 78.8 | 19.7 | 549.4 | 562 | 12.6 | 0.41 | 12.207 | 5.137 | 2 | 3.516% | 562.9 | 0.6 | 12.947 | 5.254 | 13.5 | -0.042 | 2 | 3.362% | -2.78 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.041 | 650 | 189.5 | 0 | 115.5 | 534.5 | 541.8 | 7.3 | 2.98 | 4.316 | 5.155 | 0.837 | 6.088% | 544.4 | 4.1 | 5.773 | 5.266 | 9.9 | -0.042 | 1.096 | 4.599% | -3.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.041 | 650 | 189.5 | 0 | 115.5 | 534.5 | 541.8 | 7.3 | 2.98 | 4.316 | 5.155 | 0.837 | 6.088% | 544.4 | 4.1 | 5.773 | 5.266 | 9.9 | -0.042 | 1.096 | 4.599% | -3.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.041 | 650 | 189.5 | 0 | 115.5 | 534.5 | 541.8 | 7.3 | 2.98 | 4.316 | 5.155 | 0.837 | 6.088% | 544.4 | 4.1 | 5.773 | 5.266 | 9.9 | -0.042 | 1.096 | 4.599% | -3.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.041 | 650 | 189.5 | 0 | 115.5 | 534.5 | 541.8 | 7.3 | 2.98 | 4.316 | 5.155 | 0.837 | 6.088% | 544.4 | 4.1 | 5.773 | 5.266 | 9.9 | -0.042 | 1.096 | 4.599% | -3.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.041 | 650 | 189.5 | 0 | 115.5 | 534.5 | 541.8 | 7.3 | 2.98 | 4.316 | 5.155 | 0.837 | 6.088% | 544.4 | 4.1 | 5.773 | 5.266 | 9.9 | -0.042 | 1.096 | 4.599% | -3.69 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.041 | 701 | 436 | 8.8 | 36.6 | 655.6 | 667.7 | 12.1 | -0.06 | 12.223 | 6.248 | 1.956 | 3.961% | 672.9 | -0.1 | 17.418 | 6.39 | 17.3 | -0.042 | 2 | 2.838% | -2.59 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.041 | 701.5 | 435.2 | 68 | 196.3 | 437.2 | 447.4 | 10.2 | 0.12 | 10.017 | 5.718 | 1.752 | 4.702% | 452.8 | 0.2 | 15.393 | 5.848 | 15.6 | -0.042 | 2 | 3.15% | -1.91 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.041 | 49.8 | 24 | 0 | 25 | 24.8 | 26.1 | 1.3 | 0.03 | 1.296 | 0.531 | 2 | 2.639% | 31.3 | 0 | 6.494 | 0.544 | 6.5 | -0.042 | 2 | 0.5407% | -0.26 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.041 | 49.9 | 24 | 0 | 25.2 | 24.7 | 26.9 | 2.2 | -0.12 | 2.347 | 0.532 | 2 | 1.563% | 31.4 | -0.2 | 6.86 | 0.545 | 6.7 | -0.042 | 2 | 0.5256% | -0.25 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.041 | 477.2 | 235 | 21.8 | 133.8 | 321.6 | 340.7 | 19.1 | 4.48 | 14.54 | 4.111 | 2 | 1.709% | 355.3 | 6.2 | 27.425 | 4.204 | 33.7 | -0.042 | 2 | 0.9921% | -0.65 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.041 | 168 | 70 | 0 | 44.5 | 123.5 | 124.3 | 0.8 | -1.69 | 2.426 | 1.516 | 1.6 | 14.39% | 125.2 | -2.3 | 4.044 | 1.551 | 1.7 | -0.042 | 2 | 6.934% | -4.95 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.041 | 55.8 | 22.5 | 0 | 13.7 | 42.1 | 46 | 3.9 | 1.09 | 2.798 | 0.596 | 2 | 0.985% | 48.5 | 1.5 | 4.875 | 0.611 | 6.4 | -0.042 | 2 | 0.6147% | -0.45 | 0.017 | 0.05 | 6.284% | 5.784%
Solar | SUN | PVGR | -0.041 | 78.8 | 0 | 0 | 63.7 | 15.1 | 16 | 0.9 | 0.01 | 0.851 | 0.956 | 0.89 | 6.014% | 16 | 0 | 0.904 | 0.977 | 0.9 | -0.042 | 0.925 | 6.16% | -1.11 | 0.017 | 0.05 | 6.014% | 6.718%
Solar | SUN | PVGR | -0.041 | 78.8 | 0 | 0 | 63.7 | 15.1 | 16 | 0.9 | 0.01 | 0.9 | 0.956 | 0.942 | 6.014% | 16.1 | 0 | 0.946 | 0.977 | 1 | -0.042 | 0.968 | 5.544% | -1 | 0.017 | 0.05 | 6.014% | 6.718%
Solar | SUN | PVGR | -0.041 | 150 | 0 | 0 | 7 | 143 | 145 | 2 | -0.06 | 2.028 | 1.821 | 1.114 | 5.139% | 145.1 | -0.1 | 2.193 | 1.861 | 2.1 | -0.042 | 1.179 | 5.013% | -4.64 | 0.017 | 0.05 | 6.014% | 6.718%
CombinedCycle | CC | COGN | -0.041 | 277.8 | 118 | 60 | 45.5 | 172.3 | 174.1 | 1.8 | -0.22 | 2.03 | 1.966 | 1.033 | 10.56% | 174 | -0.3 | 2.05 | 2.01 | 1.7 | -0.042 | 1.02 | 11.46% | -6.91 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.041 | 835 | 465 | 20.5 | 23.9 | 790.6 | 792.6 | 2 | 1.28 | 0.723 | 7.352 | 0.098 | 28.54% | 793.9 | 1.8 | 1.51 | 7.519 | 3.3 | -0.042 | 0.201 | 17.72% | -16.36 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.041 | 229.5 | 130 | 0 | 51.3 | 178.2 | 186.7 | 8.5 | 7.92 | 0.549 | 2.072 | 0.265 | 1.848% | 197 | 11 | 7.792 | 2.119 | 18.8 | -0.042 | 2 | 0.856% | -0.65 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.041 | 163 | 25 | 0 | 135.2 | 27.8 | 32.1 | 4.3 | 0.4 | 3.818 | 0.578 | 2 | 2.603% | 31.3 | 0.6 | 2.915 | 0.602 | 3.5 | -0.042 | 2 | 3.276% | -0.53 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.041 | 631 | 300 | 0 | 240.1 | 390.9 | 394.2 | 3.3 | -1.73 | 5.065 | 5.696 | 0.889 | 13.07% | 396.3 | -2.4 | 7.848 | 5.825 | 5.4 | -0.042 | 1.347 | 8.185% | -4.94 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.072 | 492 | 300 | 0 | 128.2 | 363.8 | 373.2 | 9.4 | -1.49 | 10.919 | 4.925 | 2 | 6.284% | 374.5 | -2.1 | 12.81 | 4.929 | 10.7 | -0.072 | 2 | 5.52% | -4.08 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.072 | 117.4 | 0 | 0 | 70.9 | 46.5 | 68.9 | 22.4 | 13.33 | 9.07 | 1.573 | 2 | 0.6302% | 80.7 | 18.6 | 15.631 | 1.574 | 34.2 | -0.072 | 2 | 0.4128% | -0.16 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.072 | 212 | 163 | 0 | 48.1 | 163.9 | 169.6 | 5.7 | 0.02 | 5.744 | 2.122 | 2 | 4.468% | 169.1 | 0 | 5.169 | 2.124 | 5.2 | -0.072 | 2 | 4.898% | -3.78 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.072 | 560 | 135 | 0 | 77.6 | 482.4 | 487.9 | 5.5 | 0.05 | 5.451 | 7.159 | 0.761 | 12.22% | 489.7 | 0.1 | 7.134 | 7.164 | 7.3 | -0.072 | 0.996 | 9.209% | -7.93 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.072 | 785 | 300 | 0 | 29.5 | 755.5 | 763.8 | 8.3 | 0 | 8.233 | 10.382 | 0.793 | 11.35% | 766.7 | 0 | 11.113 | 10.39 | 11.2 | -0.072 | 1.07 | 8.413% | -8.09 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.072 | 390 | 125 | 0 | 86.3 | 303.7 | 309.4 | 5.7 | -0.61 | 6.32 | 3.944 | 1.602 | 8.215% | 308.5 | -0.8 | 5.666 | 3.947 | 4.8 | -0.072 | 1.435 | 9.756% | -7.59 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.072 | 420 | 70 | 0 | 332.1 | 87.9 | 94.9 | 7 | 0.28 | 6.728 | 4.08 | 1.649 | 7.204% | 95.9 | 0.4 | 7.572 | 4.084 | 8 | -0.072 | 1.854 | 6.304% | -1.31 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.072 | 410 | 70 | 0 | 320.3 | 89.7 | 95.6 | 5.9 | -0.11 | 5.974 | 4.071 | 1.467 | 8.344% | 98.5 | -0.2 | 8.926 | 4.074 | 8.8 | -0.072 | 2 | 5.594% | -1.22 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.072 | 220.4 | 168 | 0 | 38.5 | 181.9 | 185.5 | 3.6 | -0.06 | 3.659 | 2.206 | 1.658 | 7.355% | 185 | -0.1 | 3.204 | 2.208 | 3.1 | -0.072 | 1.451 | 8.541% | -7.03 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.072 | 222.4 | 160 | 0 | 46.3 | 176.1 | 180.4 | 4.3 | 0 | 4.368 | 2.226 | 1.962 | 6.213% | 180 | 0 | 3.921 | 2.228 | 3.9 | -0.072 | 1.76 | 6.85% | -5.41 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.072 | 1104.5 | 490 | 140 | 164 | 800.5 | 818.5 | 18 | 0.23 | 17.761 | 9.654 | 1.84 | 7.365% | 826.7 | 0.3 | 25.886 | 9.662 | 26.2 | -0.072 | 2 | 5.06% | -3.67 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.072 | 737 | 93 | 0 | 643.8 | 93.2 | 99.3 | 6.1 | -0.36 | 6.454 | 4.148 | 1.556 | 14.51% | 98.9 | -0.5 | 6.208 | 4.154 | 5.7 | -0.072 | 1.495 | 15.53% | -1.95 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.072 | 650 | 275 | 0 | 74.1 | 575.9 | 583.3 | 7.4 | 0.6 | 6.786 | 7.435 | 0.913 | 10.54% | 581 | 0.8 | 4.285 | 7.44 | 5.1 | -0.072 | 0.576 | 15.3% | -13.55 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.072 | 622 | 456 | 3 | 58.9 | 560.1 | 568.6 | 8.5 | 0.56 | 7.967 | 6.196 | 1.286 | 8.785% | 569.1 | 0.8 | 8.206 | 6.201 | 9 | -0.072 | 1.323 | 8.296% | -7.46 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.072 | 420 | 50 | 0 | 368.6 | 51.4 | 62.8 | 11.4 | 0.02 | 11.337 | 3.663 | 2 | 4.424% | 62.8 | 0 | 11.346 | 3.666 | 11.4 | -0.072 | 2 | 4.424% | -0.54 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.072 | 15 | 0 | 0 | 12 | 3 | 11.4 | 8.4 | 1.98 | 6.436 | 0.15 | 2 | 0.2177% | 13.3 | 2.8 | 7.549 | 0.15 | 10.3 | -0.072 | 2 | 0.1775% | -0.03 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.072 | 53.8 | 0.1 | 0 | 16.5 | 37.3 | 38.9 | 1.6 | 0.47 | 1.064 | 0.721 | 1.476 | 4.053% | 38.8 | 0.7 | 0.829 | 0.721 | 1.5 | -0.072 | 1.149 | 4.323% | -2.97 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.072 | 53.4 | 0.1 | 0 | 17.6 | 35.8 | 36.7 | 0.9 | 0.65 | 0.265 | 0.715 | 0.37 | 7.151% | 37.1 | 0.9 | 0.383 | 0.716 | 1.3 | -0.072 | 0.534 | 4.951% | -3.28 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | SUB | FOSS | -0.072 | 581.7 | 155.4 | 0 | 118.6 | 463.1 | 477 | 13.9 | 1.99 | 11.921 | 5.67 | 2 | 5.024% | 478.1 | 2.8 | 12.25 | 5.675 | 15 | -0.072 | 2 | 4.655% | -3.7 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.072 | 581.7 | 155.4 | 0 | 118.6 | 463.1 | 477 | 13.9 | 1.99 | 11.921 | 5.67 | 2 | 5.024% | 478.1 | 2.8 | 12.25 | 5.675 | 15 | -0.072 | 2 | 4.655% | -3.7 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.072 | 583.3 | 155.3 | 0 | 19.6 | 563.7 | 574.4 | 10.7 | -0.11 | 10.846 | 5.491 | 1.975 | 6.544% | 572.9 | -0.1 | 9.411 | 5.495 | 9.2 | -0.072 | 1.713 | 7.611% | -7.35 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.072 | 583.3 | 155.3 | 0 | 19.6 | 563.7 | 574.4 | 10.7 | -0.11 | 10.846 | 5.491 | 1.975 | 6.544% | 572.9 | -0.1 | 9.411 | 5.495 | 9.2 | -0.072 | 1.713 | 7.611% | -7.35 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.072 | 889.3 | 461 | 141 | 28.5 | 719.8 | 739.2 | 19.4 | 1.11 | 18.347 | 7.49 | 2 | 5.502% | 743.7 | 1.5 | 22.354 | 7.496 | 23.9 | -0.072 | 2 | 4.466% | -3.61 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.072 | 889 | 461 | 140.2 | 39.3 | 709.5 | 728.7 | 19.2 | 1.65 | 17.506 | 7.496 | 2 | 5.558% | 733.2 | 2.3 | 21.444 | 7.502 | 23.7 | -0.072 | 2 | 4.502% | -3.59 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.072 | 470 | 180 | 0 | 289.1 | 180.9 | 188.7 | 7.8 | 0.22 | 7.542 | 2.311 | 2 | 7.238% | 185.9 | 0.3 | 4.731 | 2.314 | 5 | -0.072 | 2 | 11.29% | -4.33 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.072 | 470 | 180 | 0 | 289.1 | 180.9 | 188.7 | 7.8 | 0.22 | 7.542 | 2.311 | 2 | 7.238% | 185.9 | 0.3 | 4.731 | 2.314 | 5 | -0.072 | 2 | 11.29% | -4.33 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.072 | 470 | 180 | 0 | 289.1 | 180.9 | 188.7 | 7.8 | 0.22 | 7.542 | 2.311 | 2 | 7.238% | 185.9 | 0.3 | 4.731 | 2.314 | 5 | -0.072 | 2 | 11.29% | -4.33 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.072 | 470 | 180 | 0 | 289.1 | 180.9 | 188.7 | 7.8 | 0.22 | 7.542 | 2.311 | 2 | 7.238% | 185.9 | 0.3 | 4.731 | 2.314 | 5 | -0.072 | 2 | 11.29% | -4.33 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.072 | 235 | 170 | 26 | 18.8 | 190.2 | 195.7 | 5.5 | 0.03 | 5.454 | 2.092 | 2 | 5.132% | 195.8 | 0 | 5.596 | 2.094 | 5.6 | -0.072 | 2 | 5.041% | -4.07 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.072 | 219 | 150 | 0 | 20.2 | 198.8 | 202.4 | 3.6 | 0.11 | 3.475 | 2.662 | 1.305 | 7.308% | 202.8 | 0.2 | 3.821 | 2.664 | 4 | -0.072 | 1.434 | 6.577% | -5.96 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.072 | 219 | 150 | 0 | 19.9 | 199.1 | 201.5 | 2.4 | -0.13 | 2.446 | 2.665 | 0.918 | 10.96% | 202.4 | -0.2 | 3.427 | 2.667 | 3.3 | -0.072 | 1.285 | 7.972% | -7.23 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.072 | 221 | 150 | 0 | 20.1 | 200.9 | 203.4 | 2.5 | -0.18 | 2.638 | 2.703 | 0.976 | 10.62% | 204.4 | -0.3 | 3.761 | 2.705 | 3.5 | -0.072 | 1.39 | 7.585% | -6.88 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.072 | 227 | 150 | 0 | 20.4 | 206.6 | 208.9 | 2.3 | -0.7 | 2.998 | 2.823 | 1.062 | 11.86% | 210.2 | -1 | 4.609 | 2.825 | 3.6 | -0.072 | 1.632 | 7.575% | -6.88 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.072 | 145 | 0 | 40 | 32.6 | 72.4 | 76.7 | 4.3 | 0.41 | 3.888 | 1.051 | 2 | 4.053% | 74.9 | 0.6 | 1.97 | 1.052 | 2.5 | -0.072 | 1.873 | 6.971% | -3.46 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.072 | 586.2 | 260 | 113.2 | 69.4 | 403.6 | 403.8 | 0.2 | -2.18 | 2.313 | 4.735 | 0.489 | 351.9% | 407.5 | -3 | 6.946 | 4.739 | 3.9 | -0.072 | 1.466 | 18.04% | -12.41 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.072 | 90 | 59 | 0 | 19.9 | 70.1 | 72.8 | 2.7 | 0 | 2.722 | 1.064 | 2 | 4.01% | 73.3 | 0 | 3.156 | 1.065 | 3.2 | -0.072 | 2 | 3.384% | -2.62 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.072 | 522.6 | 305.5 | 34.1 | 13.9 | 474.6 | 484.3 | 9.7 | -0.47 | 10.239 | 4.889 | 2 | 6.468% | 483.6 | -0.7 | 9.717 | 4.893 | 9 | -0.072 | 1.986 | 6.971% | -6.32 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.072 | 770 | 280 | 0 | 19.1 | 750.9 | 748.3 | -2.6 | -8.52 | 5.874 | 10.317 | 0.569 | -35.55% | 745.1 | -11.9 | 6.082 | 10.325 | -5.8 | -0.072 | 0.589 | -15.94% | 15.53 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.072 | 644.7 | 250 | 145.5 | 204.6 | 294.6 | 306.1 | 11.5 | -4.42 | 15.909 | 4.997 | 2 | 6.73% | 306.8 | -6.2 | 18.376 | 5.001 | 12.2 | -0.072 | 2 | 6.344% | -2.9 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.072 | 440 | 385 | 0 | 11.5 | 428.5 | 437.6 | 9.1 | -0.24 | 9.408 | 5.895 | 1.596 | 5.805% | 438 | -0.3 | 9.907 | 5.9 | 9.5 | -0.072 | 1.679 | 5.561% | -5.41 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.072 | 650 | 189.5 | 0 | 303.1 | 346.9 | 354.3 | 7.4 | 0.19 | 7.268 | 5.202 | 1.397 | 10.54% | 355.4 | 0.3 | 8.223 | 5.206 | 8.5 | -0.072 | 1.579 | 9.18% | -4.89 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.072 | 650 | 189.5 | 0 | 303.1 | 346.9 | 354.3 | 7.4 | 0.19 | 7.268 | 5.202 | 1.397 | 10.54% | 355.4 | 0.3 | 8.223 | 5.206 | 8.5 | -0.072 | 1.579 | 9.18% | -4.89 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.072 | 650 | 189.5 | 0 | 303.1 | 346.9 | 354.3 | 7.4 | 0.19 | 7.268 | 5.202 | 1.397 | 10.54% | 355.4 | 0.3 | 8.223 | 5.206 | 8.5 | -0.072 | 1.579 | 9.18% | -4.89 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.072 | 650 | 189.5 | 0 | 303.1 | 346.9 | 354.3 | 7.4 | 0.19 | 7.268 | 5.202 | 1.397 | 10.54% | 355.4 | 0.3 | 8.223 | 5.206 | 8.5 | -0.072 | 1.579 | 9.18% | -4.89 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.072 | 650 | 189.5 | 0 | 303.1 | 346.9 | 354.3 | 7.4 | 0.19 | 7.268 | 5.202 | 1.397 | 10.54% | 355.4 | 0.3 | 8.223 | 5.206 | 8.5 | -0.072 | 1.579 | 9.18% | -4.89 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.072 | 706.7 | 405.5 | 59.9 | 144 | 502.8 | 510.3 | 7.5 | 1.36 | 6.16 | 6.474 | 0.952 | 11.31% | 511.6 | 1.9 | 6.926 | 6.479 | 8.8 | -0.072 | 1.069 | 9.64% | -6.85 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.072 | 704.1 | 437.2 | 68 | 197.9 | 438.2 | 449.5 | 11.3 | -0.06 | 11.313 | 6.367 | 1.777 | 7.48% | 454.8 | -0.1 | 16.661 | 6.372 | 16.6 | -0.072 | 2 | 5.092% | -3.17 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.072 | 486.3 | 235 | 19.8 | 230.6 | 235.9 | 244.5 | 8.6 | -0.12 | 8.759 | 4.669 | 1.876 | 6.789% | 246.3 | -0.2 | 10.593 | 4.673 | 10.4 | -0.072 | 2 | 5.614% | -2.72 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.072 | 685 | 420 | 0 | 92 | 593 | 607.6 | 14.6 | 1.14 | 13.443 | 6.856 | 1.961 | 5.632% | 608.8 | 1.6 | 14.236 | 6.862 | 15.8 | -0.072 | 2 | 5.204% | -4.5 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.072 | 273.1 | 118 | 60 | 43.5 | 169.6 | 173.6 | 4 | 0.04 | 3.932 | 2.133 | 1.843 | 8.2% | 173.5 | 0.1 | 3.891 | 2.135 | 3.9 | -0.072 | 1.823 | 8.41% | -5.21 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.072 | 79 | 58 | 0 | 20.5 | 58.5 | 60.1 | 1.6 | 0.08 | 1.566 | 0.934 | 1.676 | 5.943% | 60 | 0.1 | 1.419 | 0.935 | 1.5 | -0.072 | 1.517 | 6.339% | -4.66 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.072 | 830 | 465 | 123.8 | 170.4 | 535.8 | 544 | 8.2 | 3.58 | 4.551 | 7.068 | 0.644 | 12.15% | 545.1 | 5 | 4.283 | 7.074 | 9.3 | -0.072 | 0.605 | 10.71% | -6.91 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.072 | 276 | 165 | 35 | 75.5 | 165.5 | 172.1 | 6.6 | 0.1 | 6.492 | 2.412 | 2 | 5.022% | 172.7 | 0.1 | 7.092 | 2.414 | 7.2 | -0.072 | 2 | 4.604% | -2.75 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.072 | 663 | 156 | 0 | 62.6 | 600.4 | 611 | 10.6 | 2.48 | 8.182 | 6.848 | 1.195 | 7.508% | 610.3 | 3.5 | 6.446 | 6.853 | 9.9 | -0.072 | 0.941 | 8.039% | -7.27 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.072 | 662 | 156 | 0 | 152 | 510 | 517.8 | 7.8 | -0.08 | 7.923 | 7.165 | 1.106 | 10.19% | 517.8 | -0.1 | 7.929 | 7.171 | 7.8 | -0.072 | 1.106 | 10.19% | -7.84 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.072 | 608 | 303 | 0 | 31.4 | 576.6 | 584 | 7.4 | 0.07 | 7.34 | 6.11 | 1.201 | 9.863% | 585.3 | 0.1 | 8.607 | 6.115 | 8.7 | -0.072 | 1.408 | 8.389% | -7.95 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.072 | 314 | 125 | 0 | 171.1 | 142.9 | 147 | 4.1 | 0 | 4.121 | 3.143 | 1.311 | 9.197% | 145.8 | 0 | 2.93 | 3.145 | 2.9 | -0.072 | 0.932 | 13% | -5.9 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.072 | 1107 | 379 | 152 | 105.1 | 849.9 | 870.8 | 20.9 | -1.67 | 22.613 | 9.559 | 2 | 6.357% | 879.5 | -2.3 | 31.962 | 9.567 | 29.6 | -0.072 | 2 | 4.489% | -3.44 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 515.3 | 275 | 12 | 57.2 | 446.1 | 466.8 | 20.7 | 6.19 | 14.494 | 6.716 | 2 | 3.445% | 471.1 | 8.6 | 16.405 | 7.021 | 25 | -0.085 | 2 | 2.921% | -2.47 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 492 | 300 | 0 | 106.9 | 385.1 | 397.3 | 12.2 | 5.72 | 6.457 | 6.565 | 0.984 | 5.581% | 396.7 | 8 | 3.675 | 6.863 | 11.6 | -0.085 | 0.535 | 6.011% | -4.59 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.083 | 560 | 135 | 0 | 54.7 | 505.3 | 514.4 | 9.1 | -0.45 | 9.457 | 9.814 | 0.964 | 8.516% | 519.2 | -0.6 | 14.502 | 10.245 | 13.9 | -0.085 | 1.416 | 5.709% | -5.03 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 400 | 125 | 0 | 24.8 | 375.2 | 382.9 | 7.7 | -0.06 | 7.689 | 5.555 | 1.384 | 7.19% | 380.1 | -0.1 | 4.985 | 5.799 | 4.9 | -0.085 | 0.86 | 11.57% | -10.59 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 390 | 125 | 0 | 66 | 324 | 331.3 | 7.3 | 2.5 | 4.728 | 5.262 | 0.898 | 7.394% | 332.8 | 3.5 | 5.265 | 5.493 | 8.8 | -0.085 | 0.959 | 6.282% | -5.09 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.083 | 410 | 70 | 0 | 328.6 | 81.4 | 87.6 | 6.2 | -2.5 | 8.752 | 5.372 | 1.629 | 9.152% | 85.6 | -3.5 | 7.647 | 5.607 | 4.2 | -0.085 | 1.364 | 13.84% | -2.67 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.083 | 214.2 | 168 | 0 | 40.1 | 174.1 | 177 | 2.9 | -0.12 | 2.992 | 2.858 | 1.047 | 10.23% | 176.5 | -0.2 | 2.557 | 2.988 | 2.4 | -0.085 | 0.856 | 12.66% | -10.02 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 216.2 | 160 | 0 | 49.8 | 166.4 | 169.2 | 2.8 | 0.12 | 2.682 | 2.885 | 0.93 | 10.69% | 168.4 | 0.2 | 1.836 | 3.016 | 2 | -0.085 | 0.609 | 15.33% | -11.5 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 1104.5 | 490 | 140 | 313.8 | 650.7 | 684 | 33.3 | 7.84 | 25.522 | 12.87 | 1.983 | 4.589% | 686.1 | 10.9 | 24.573 | 13.455 | 35.4 | -0.085 | 1.826 | 4.421% | -2.54 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.083 | 737 | 93 | 0 | 642.9 | 94.1 | 103.6 | 9.5 | -0.85 | 10.373 | 6.459 | 1.606 | 10.74% | 104.5 | -1.2 | 11.611 | 6.877 | 10.4 | -0.085 | 1.688 | 10.04% | -1.25 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 650 | 275 | 0 | 209.3 | 440.7 | 457.5 | 16.8 | 1.11 | 15.744 | 10.093 | 1.56 | 5.354% | 456.4 | 1.5 | 14.178 | 10.535 | 15.7 | -0.085 | 1.346 | 5.867% | -3.88 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.083 | 617 | 456 | 3 | 85.6 | 528.4 | 542.4 | 14 | 0.2 | 13.754 | 8.193 | 1.679 | 6.099% | 544.7 | 0.3 | 16.015 | 8.565 | 16.3 | -0.085 | 1.87 | 5.364% | -4.48 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 1161 | 612 | 230 | 60.2 | 870.8 | 896.6 | 25.8 | 13.51 | 12.229 | 12.423 | 0.984 | 6.226% | 900.8 | 18.8 | 11.171 | 12.987 | 30 | -0.085 | 0.86 | 5.483% | -4.01 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.083 | 314 | 50 | 0 | 257.3 | 56.7 | 58 | 1.3 | -0.15 | 1.411 | 3.977 | 0.355 | 33.43% | 56.9 | -0.2 | 0.354 | 4.151 | 0.2 | -0.085 | 0.085 | 222.6% | -39.08 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.083 | 420 | 50 | 0 | 366.9 | 53.1 | 66.8 | 13.7 | -0.09 | 13.795 | 4.822 | 2 | 4.243% | 68 | -0.1 | 14.992 | 5.033 | 14.9 | -0.085 | 2 | 3.995% | -0.49 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 581.7 | 155.4 | 0 | 34.4 | 547.3 | 560.9 | 13.6 | 2.02 | 11.55 | 7.252 | 1.593 | 5.919% | 560.3 | 2.8 | 10.223 | 7.57 | 13 | -0.085 | 1.35 | 6.341% | -5.82 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.083 | 581.7 | 155.4 | 0 | 34.4 | 547.3 | 560.9 | 13.6 | 2.02 | 11.55 | 7.252 | 1.593 | 5.919% | 560.3 | 2.8 | 10.223 | 7.57 | 13 | -0.085 | 1.35 | 6.341% | -5.82 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.083 | 883.9 | 461 | 140.4 | 24.7 | 718.8 | 735.8 | 17 | -0.24 | 17.256 | 9.922 | 1.739 | 7.194% | 736.5 | -0.3 | 18.017 | 10.373 | 17.7 | -0.085 | 1.737 | 7.076% | -5.62 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 534.1 | 310 | 128.9 | 94.2 | 311 | 314.4 | 3.4 | 1.2 | 2.223 | 5.406 | 0.411 | 21.74% | 317.6 | 1.7 | 4.921 | 5.651 | 6.6 | -0.085 | 0.871 | 11.47% | -6.51 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.083 | 217 | 150 | 0 | 24.1 | 192.9 | 199.1 | 6.2 | 1.73 | 4.453 | 3.418 | 1.303 | 4.846% | 200.3 | 2.4 | 4.969 | 3.568 | 7.4 | -0.085 | 1.393 | 4.158% | -3.6 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.083 | 217 | 150 | 0 | 17.1 | 199.9 | 198.2 | -1.7 | -3.66 | 1.971 | 3.489 | 0.565 | -17.67% | 199.3 | -5.1 | 4.452 | 3.642 | -0.6 | -0.085 | 1.223 | -51.28% | 46.04 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 143.5 | 0 | 40 | 26.6 | 76.9 | 85.4 | 8.5 | 0.41 | 8.13 | 1.381 | 2 | 2.339% | 83.3 | 0.6 | 5.803 | 1.444 | 6.4 | -0.085 | 2 | 3.181% | -1.66 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 581 | 305 | 127 | 65.2 | 388.8 | 393.5 | 4.7 | -2.07 | 6.74 | 6.058 | 1.113 | 17.11% | 402.1 | -2.9 | 16.182 | 6.333 | 13.3 | -0.085 | 2 | 6.191% | -4.04 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 583 | 305 | 126 | 80 | 377 | 383.1 | 6.1 | 1.55 | 4.572 | 6.098 | 0.75 | 13.23% | 383.6 | 2.2 | 4.398 | 6.375 | 6.6 | -0.085 | 0.69 | 12.52% | -7.9 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 589.2 | 260 | 114.7 | 15.5 | 459 | 460.1 | 1.1 | 0.09 | 0.96 | 6.331 | 0.152 | 74.12% | 460.7 | 0.1 | 1.568 | 6.619 | 1.7 | -0.085 | 0.237 | 49.12% | -37.33 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.083 | 90 | 59 | 0 | 19.6 | 70.4 | 74.3 | 3.9 | 0 | 3.856 | 1.417 | 2 | 3.2% | 74.5 | 0 | 4.053 | 1.486 | 4.1 | -0.085 | 2 | 3.117% | -2.37 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 494 | 316 | 0 | 49.3 | 444.7 | 451.9 | 7.2 | -2.12 | 9.349 | 6.592 | 1.418 | 9.495% | 455.9 | -3 | 14.134 | 6.891 | 11.2 | -0.085 | 2 | 6.251% | -5.49 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.083 | 770 | 280 | 0 | 22 | 748 | 755.9 | 7.9 | 0 | 7.942 | 13.6 | 0.584 | 13.49% | 756.2 | 0 | 8.238 | 14.197 | 8.2 | -0.085 | 0.58 | 13.31% | -12.62 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.083 | 644.4 | 250 | 145.4 | 33.1 | 465.9 | 472.7 | 6.8 | 2.2 | 4.569 | 6.659 | 0.686 | 13.11% | 473.8 | 3.1 | 4.774 | 6.961 | 7.9 | -0.085 | 0.686 | 11.56% | -8.15 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 704.4 | 403.9 | 51.9 | 61.9 | 590.6 | 607.6 | 17 | 6.49 | 10.578 | 8.707 | 1.215 | 5.734% | 612.9 | 9 | 13.29 | 9.102 | 22.3 | -0.085 | 1.46 | 4.476% | -3.66 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 701 | 436 | 65.1 | 198.3 | 437.6 | 459.7 | 22.1 | 0.47 | 21.642 | 8.485 | 2 | 4.389% | 462.2 | 0.7 | 23.979 | 8.87 | 24.6 | -0.085 | 2 | 4.038% | -2.46 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 702.2 | 435.5 | 67.9 | 193.2 | 441.1 | 455.5 | 14.4 | 0.12 | 14.239 | 8.464 | 1.682 | 6.748% | 464.4 | 0.2 | 23.093 | 8.848 | 23.3 | -0.085 | 2 | 4.271% | -2.62 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 479.2 | 235 | 4.5 | 175.5 | 299.2 | 313.7 | 14.5 | -0.18 | 14.644 | 6.334 | 2 | 4.574% | 329.5 | -0.2 | 30.503 | 6.622 | 30.3 | -0.085 | 2 | 2.241% | -1.37 | 0.017 | 0.0578 | 5.933% | 5.163%
Solar | SUN | PVGR | -0.083 | 78.8 | 0 | 0 | 75.8 | 3 | 4.1 | 1.1 | -0.15 | 1.3 | 1.391 | 0.935 | 9.935% | 4.6 | -0.2 | 1.851 | 1.452 | 1.6 | -0.085 | 1.275 | 6.995% | -0.24 | 0.017 | 0.05 | 6.014% | 6.718%
Solar | SUN | PVGR | -0.083 | 78.8 | 0 | 0 | 75.8 | 3 | 4.4 | 1.4 | -0.14 | 1.542 | 1.391 | 1.109 | 7.806% | 4.6 | -0.2 | 1.787 | 1.452 | 1.6 | -0.085 | 1.231 | 6.995% | -0.24 | 0.017 | 0.05 | 6.014% | 6.718%
Solar | SUN | PVGR | -0.083 | 150 | 0 | 0 | 11.7 | 138.3 | 140.5 | 2.2 | -0.34 | 2.606 | 2.649 | 0.984 | 9.445% | 140.4 | -0.5 | 2.639 | 2.766 | 2.1 | -0.085 | 0.954 | 10.13% | -9.1 | 0.017 | 0.05 | 6.014% | 6.718%
CombinedCycle | CC | COGN | -0.083 | 685 | 420 | 0 | 83.2 | 601.8 | 614.4 | 12.6 | 0.41 | 12.215 | 9.141 | 1.336 | 7.523% | 616.3 | 0.6 | 13.919 | 9.556 | 14.5 | -0.085 | 1.457 | 6.694% | -5.74 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 272.6 | 118 | 60 | 46.5 | 166.1 | 170.7 | 4.6 | -0.59 | 5.226 | 2.836 | 1.842 | 8.204% | 172.3 | -0.8 | 7.066 | 2.965 | 6.2 | -0.085 | 2 | 6.233% | -3.7 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.083 | 79 | 58 | 0 | 20.4 | 58.6 | 60.4 | 1.8 | 0.15 | 1.647 | 1.243 | 1.325 | 6.087% | 60 | 0.2 | 1.2 | 1.305 | 1.4 | -0.085 | 0.92 | 8.014% | -5.77 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 830 | 465 | 124.1 | 36.7 | 669.2 | 684.8 | 15.6 | 2.96 | 12.669 | 9.42 | 1.345 | 7.362% | 684.5 | 4.1 | 11.209 | 9.848 | 15.3 | -0.085 | 1.138 | 7.687% | -6.05 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.083 | 273 | 165 | 35 | 72.7 | 165.3 | 173.7 | 8.4 | -0.12 | 8.509 | 3.176 | 2 | 4.499% | 175.2 | -0.2 | 10.036 | 3.32 | 9.9 | -0.085 | 2 | 3.909% | -2.31 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.083 | 662 | 156 | 0 | 44.9 | 617.1 | 636.3 | 19.2 | 5.6 | 13.597 | 8.931 | 1.522 | 4.771% | 639.9 | 7.8 | 15.012 | 9.323 | 22.8 | -0.085 | 1.61 | 4.115% | -3.74 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.083 | 1108 | 379 | 152 | 130.7 | 825.3 | 848.2 | 22.9 | -3.1 | 25.958 | 12.757 | 2 | 6.694% | 862.5 | -4.3 | 41.476 | 13.336 | 37.2 | -0.085 | 2 | 4.22% | -3.07 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.103 | 190 | 115 | 0 | 18.7 | 171.3 | 180.8 | 9.5 | -0.4 | 9.848 | 4.096 | 2 | 3.436% | 186 | -0.6 | 15.226 | 3.994 | 14.7 | -0.101 | 2 | 2.178% | -2 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.103 | 212.6 | 170.6 | 0 | 25 | 187.6 | 194.5 | 6.9 | 0.17 | 6.678 | 3.891 | 1.716 | 5.293% | 195.3 | 0.2 | 7.4 | 3.802 | 7.7 | -0.101 | 1.946 | 4.651% | -4.18 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.103 | 560 | 135 | 0 | 50 | 510 | 519.9 | 9.9 | 0.84 | 9.06 | 13.44 | 0.674 | 9.713% | 519.9 | 1.2 | 8.727 | 13.141 | 9.9 | -0.101 | 0.664 | 9.525% | -8.84 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.103 | 400 | 125 | 0 | 50 | 350 | 361.3 | 11.3 | 0.12 | 11.195 | 7.429 | 1.507 | 6.079% | 360.9 | 0.2 | 10.781 | 7.264 | 10.9 | -0.101 | 1.484 | 6.18% | -5.51 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.103 | 390 | 125 | 0 | 48.7 | 341.3 | 351 | 9.7 | -0.3 | 10.049 | 7.214 | 1.393 | 6.905% | 347.4 | -0.4 | 6.545 | 7.053 | 6.1 | -0.101 | 0.928 | 10.77% | -9.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.103 | 410 | 70 | 0 | 336.8 | 73.2 | 83.4 | 10.2 | -0.31 | 10.477 | 7.303 | 1.435 | 6.903% | 86.1 | -0.4 | 13.311 | 7.141 | 12.9 | -0.101 | 1.864 | 5.352% | -0.97 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.103 | 750 | 95 | 0 | 556.7 | 193.3 | 210.1 | 16.8 | -2.53 | 19.338 | 13.059 | 1.481 | 7.667% | 206.4 | -3.5 | 16.623 | 12.678 | 13.1 | -0.101 | 1.311 | 9.642% | -2.53 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.103 | 490 | 342 | 0 | 61.5 | 428.5 | 440.8 | 12.3 | 2 | 10.284 | 8.967 | 1.147 | 6.841% | 442.5 | 2.8 | 11.252 | 8.763 | 14 | -0.101 | 1.284 | 5.894% | -5.25 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.103 | 625 | 456 | 17 | 80.1 | 527.9 | 547.4 | 19.5 | 0.9 | 18.626 | 11.127 | 1.674 | 5.504% | 548.8 | 1.3 | 19.624 | 10.873 | 20.9 | -0.101 | 1.805 | 5.035% | -4.33 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.103 | 103 | 12 | 0 | 90.8 | 12.2 | 15.2 | 3 | 0.26 | 2.691 | 2.447 | 1.1 | 5.903% | 15 | 0.4 | 2.458 | 2.393 | 2.8 | -0.101 | 1.027 | 6.202% | -0.74 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.103 | 420 | 50 | 0 | 366.5 | 53.5 | 74.7 | 21.2 | 0.64 | 20.537 | 6.532 | 2 | 3.402% | 76.4 | 0.9 | 22.002 | 6.387 | 22.9 | -0.101 | 2 | 3.089% | -0.4 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.103 | 34 | 0 | 0 | 28.9 | 5.1 | 7.5 | 2.4 | 1.49 | 0.915 | 0.622 | 1.47 | 2.444% | 8.1 | 2.1 | 0.847 | 0.608 | 3 | -0.101 | 1.393 | 1.917% | -0.28 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.103 | 513.4 | 336.8 | 0 | 11.5 | 501.9 | 505.8 | 3.9 | 1.25 | 2.595 | 9.396 | 0.276 | 22.61% | 506.7 | 1.7 | 3.01 | 9.182 | 4.8 | -0.101 | 0.328 | 18.01% | -17.94 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.103 | 581.7 | 155.4 | 0 | 27.6 | 554.1 | 570.8 | 16.7 | -0.74 | 17.349 | 9.805 | 1.769 | 5.981% | 569.2 | -1 | 16.045 | 9.587 | 15.1 | -0.101 | 1.674 | 6.487% | -6.3 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.103 | 581.7 | 155.4 | 0 | 27.6 | 554.1 | 570.8 | 16.7 | -0.74 | 17.349 | 9.805 | 1.769 | 5.981% | 569.2 | -1 | 16.045 | 9.587 | 15.1 | -0.101 | 1.674 | 6.487% | -6.3 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.103 | 584.3 | 155.3 | 0 | 17.8 | 566.5 | 581.3 | 14.8 | -0.21 | 15.03 | 9.811 | 1.532 | 6.779% | 580.3 | -0.3 | 14.098 | 9.593 | 13.8 | -0.101 | 1.47 | 7.129% | -7.04 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.103 | 584.3 | 155.3 | 0 | 17.8 | 566.5 | 581.3 | 14.8 | -0.21 | 15.03 | 9.811 | 1.532 | 6.779% | 580.3 | -0.3 | 14.098 | 9.593 | 13.8 | -0.101 | 1.47 | 7.129% | -7.04 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.103 | 880.2 | 461 | 92.9 | 44.6 | 742.7 | 770.7 | 28 | -0.35 | 28.353 | 14.408 | 1.968 | 5.397% | 777.4 | -0.5 | 35.147 | 14.079 | 34.7 | -0.101 | 2 | 4.271% | -3.67 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.103 | 466.1 | 180 | 0 | 16.2 | 449.9 | 456.1 | 6.2 | 1.78 | 4.497 | 6.534 | 0.688 | 12.91% | 456.6 | 2.5 | 4.281 | 6.343 | 6.7 | -0.101 | 0.675 | 11.72% | -11.52 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.103 | 466.1 | 180 | 0 | 16.2 | 449.9 | 456.1 | 6.2 | 1.78 | 4.497 | 6.534 | 0.688 | 12.91% | 456.6 | 2.5 | 4.281 | 6.343 | 6.7 | -0.101 | 0.675 | 11.72% | -11.52 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.103 | 466.1 | 180 | 0 | 16.2 | 449.9 | 456.1 | 6.2 | 1.78 | 4.497 | 6.534 | 0.688 | 12.91% | 456.6 | 2.5 | 4.281 | 6.343 | 6.7 | -0.101 | 0.675 | 11.72% | -11.52 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.103 | 466.1 | 180 | 0 | 16.2 | 449.9 | 456.1 | 6.2 | 1.78 | 4.497 | 6.534 | 0.688 | 12.91% | 456.6 | 2.5 | 4.281 | 6.343 | 6.7 | -0.101 | 0.675 | 11.72% | -11.52 | 0.034 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.103 | 163.9 | 0 | 24 | 24.7 | 115.2 | 129.1 | 13.9 | -0.52 | 14.355 | 2.559 | 2 | 2.026% | 134.4 | -0.7 | 19.92 | 2.501 | 19.2 | -0.101 | 2 | 1.438% | -1.03 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.103 | 586.7 | 260 | 10.5 | 19.8 | 556.4 | 557.4 | 1 | 0.8 | 0.23 | 10.544 | 0.022 | 100.7% | 557.4 | 1.1 | -0.133 | 10.304 | 1 | -0.101 | 0 | 98.79% | -95.49 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.103 | 90 | 59 | 0 | 19.5 | 70.5 | 75.9 | 5.4 | 0.23 | 5.18 | 1.94 | 2 | 2.866% | 76 | 0.3 | 5.186 | 1.892 | 5.5 | -0.101 | 2 | 2.76% | -2.2 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.103 | 495 | 317 | 0 | 55 | 440 | 455.3 | 15.3 | 0.12 | 15.143 | 9.059 | 1.672 | 5.556% | 458 | 0.2 | 17.8 | 8.852 | 18 | -0.101 | 2 | 4.631% | -4.19 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.103 | 513 | 303 | 14.5 | 10.6 | 487.9 | 496.9 | 9 | 0.4 | 8.605 | 9.122 | 0.943 | 9.788% | 497.5 | 0.6 | 9.03 | 8.914 | 9.6 | -0.101 | 1.013 | 8.998% | -8.72 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.103 | 520.6 | 305.5 | 7.8 | 24.3 | 488.5 | 503 | 14.5 | 0.61 | 13.938 | 9.384 | 1.485 | 6.165% | 500.8 | 0.9 | 11.472 | 9.17 | 12.3 | -0.101 | 1.251 | 7.127% | -6.82 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.103 | 232 | 150 | 16 | 10 | 206 | 211.4 | 5.4 | -0.4 | 5.796 | 4.114 | 1.409 | 7.381% | 211.2 | -0.6 | 5.698 | 4.022 | 5.2 | -0.101 | 1.417 | 7.516% | -6.8 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.103 | 237 | 150 | 16 | 10.5 | 210.5 | 216.5 | 6 | -0.25 | 6.225 | 4.254 | 1.463 | 6.786% | 216.2 | -0.3 | 6.015 | 4.16 | 5.7 | -0.101 | 1.446 | 7.004% | -6.33 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.103 | 249 | 150 | 16 | 10.3 | 222.7 | 228.5 | 5.8 | -0.17 | 5.927 | 4.46 | 1.329 | 7.375% | 228.3 | -0.2 | 5.861 | 4.361 | 5.6 | -0.101 | 1.344 | 7.49% | -6.82 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.103 | 251 | 110 | 16 | 9.6 | 225.4 | 231.7 | 6.3 | -0.21 | 6.429 | 4.525 | 1.421 | 6.844% | 231.4 | -0.3 | 6.236 | 4.424 | 6 | -0.101 | 1.41 | 7.047% | -6.44 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.103 | 642.3 | 250 | 135.4 | 33.7 | 473.2 | 492.9 | 19.7 | -0.05 | 19.685 | 9.276 | 2 | 5.598% | 494.7 | -0.1 | 21.509 | 9.065 | 21.5 | -0.101 | 2 | 5.03% | -3.78 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.103 | 707 | 437 | 21 | 80.4 | 605.6 | 626.2 | 20.6 | -2.66 | 23.268 | 12.555 | 1.853 | 5.893% | 631.1 | -3.7 | 29.195 | 12.268 | 25.5 | -0.101 | 2 | 4.668% | -4.08 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.103 | 701.8 | 437 | 67.9 | 194.9 | 439 | 459.3 | 20.3 | -0.12 | 20.414 | 11.601 | 1.76 | 5.936% | 464.7 | -0.2 | 25.907 | 11.336 | 25.7 | -0.101 | 2 | 4.598% | -2.93 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.103 | 481.2 | 235 | 7.4 | 123.1 | 350.7 | 368.5 | 17.8 | -0.53 | 18.304 | 8.671 | 2 | 4.642% | 381.7 | -0.7 | 31.725 | 8.473 | 31 | -0.101 | 2 | 2.614% | -1.94 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.103 | 55.9 | 22.5 | 0 | 32.7 | 23.2 | 26.1 | 2.9 | -0.27 | 3.232 | 1.204 | 2 | 3.319% | 31.2 | -0.4 | 8.435 | 1.175 | 8 | -0.101 | 2 | 1.18% | -0.49 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.103 | 692 | 420 | 0 | 74.2 | 617.8 | 645.8 | 28 | -0.65 | 28.64 | 12.664 | 2 | 4.244% | 646.3 | -0.9 | 29.329 | 12.375 | 28.5 | -0.101 | 2 | 4.088% | -3.72 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.103 | 276.2 | 118 | 60 | 44 | 172.2 | 178.2 | 6 | -0.27 | 6.305 | 3.956 | 1.594 | 7.907% | 178.5 | -0.4 | 6.7 | 3.866 | 6.3 | -0.101 | 1.733 | 7.384% | -4.69 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.103 | 932.6 | 360 | 0 | 19.6 | 913 | 919 | 6 | -0.28 | 6.376 | 15.972 | 0.399 | 26.69% | 924.3 | -0.4 | 11.79 | 15.617 | 11.3 | -0.101 | 0.755 | 13.9% | -13.87 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.103 | 932.6 | 360 | 0 | 19.6 | 913 | 919 | 6 | -0.28 | 6.376 | 15.972 | 0.399 | 26.69% | 924.3 | -0.4 | 11.79 | 15.617 | 11.3 | -0.101 | 0.755 | 13.9% | -13.87 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.103 | 932.6 | 360 | 0 | 19.6 | 913 | 919 | 6 | -0.28 | 6.376 | 15.972 | 0.399 | 26.69% | 924.3 | -0.4 | 11.79 | 15.617 | 11.3 | -0.101 | 0.755 | 13.9% | -13.87 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.103 | 932.6 | 360 | 0 | 19.6 | 913 | 919 | 6 | -0.28 | 6.376 | 15.972 | 0.399 | 26.69% | 924.3 | -0.4 | 11.79 | 15.617 | 11.3 | -0.101 | 0.755 | 13.9% | -13.87 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.103 | 79 | 58 | 0 | 20.4 | 58.6 | 61 | 2.4 | -0.07 | 2.443 | 1.703 | 1.435 | 5.663% | 60.5 | -0.1 | 1.997 | 1.661 | 1.9 | -0.101 | 1.203 | 7.014% | -5.28 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.103 | 833 | 460 | 124 | 29.4 | 679.6 | 693.6 | 14 | -0.54 | 14.484 | 12.976 | 1.116 | 10.22% | 696.2 | -0.8 | 17.304 | 12.68 | 16.6 | -0.101 | 1.365 | 8.449% | -7.03 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.103 | 275 | 165 | 35 | 8 | 232 | 235.9 | 3.9 | 0.2 | 3.703 | 4.392 | 0.843 | 12.11% | 235.9 | 0.3 | 3.66 | 4.292 | 3.9 | -0.101 | 0.853 | 11.88% | -10.2 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.103 | 638 | 300 | 0 | 336.4 | 301.6 | 319.6 | 18 | 0.86 | 17.065 | 11.676 | 1.462 | 6.086% | 318.7 | 1.2 | 15.856 | 11.41 | 17.1 | -0.101 | 1.39 | 6.282% | -3.03 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.103 | 1114 | 379 | 152 | 119.1 | 842.9 | 877 | 34.1 | -1.49 | 35.657 | 17.605 | 2 | 5.609% | 884.1 | -2.1 | 43.31 | 17.204 | 41.2 | -0.101 | 2 | 4.552% | -3.51 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 646 | 258 | 122.5 | 24.5 | 499 | 516.5 | 17.5 | -0.18 | 17.646 | 6.021 | 2 | 4.677% | 520 | -0.2 | 21.242 | 6.754 | 21 | -0.082 | 2 | 4.205% | -3.01 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 549.1 | 275 | 12 | 95.3 | 441.8 | 456.1 | 14.3 | 1.06 | 13.243 | 6.177 | 2 | 4.866% | 457.8 | 1.5 | 14.471 | 6.93 | 16 | -0.082 | 2 | 4.692% | -3.5 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 492 | 300 | 0 | 51.3 | 440.7 | 448.8 | 8.1 | -0.44 | 8.535 | 5.658 | 1.508 | 7.697% | 449.2 | -0.6 | 9.048 | 6.348 | 8.5 | -0.082 | 1.425 | 7.914% | -6.56 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 683 | 338 | 3.9 | 98.6 | 580.5 | 582.6 | 2.1 | -0.53 | 2.678 | 7.81 | 0.343 | 41.21% | 583.2 | -0.7 | 3.467 | 8.762 | 2.7 | -0.082 | 0.396 | 34.58% | -27.22 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 190 | 117 | 14 | 13.5 | 162.5 | 164.5 | 2 | -0.12 | 2.06 | 2.024 | 1.018 | 12.05% | 164.4 | -0.2 | 2.05 | 2.271 | 1.9 | -0.082 | 0.903 | 13.68% | -10.82 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.076 | 560 | 135 | 0 | 12.8 | 547.2 | 555.6 | 8.4 | -0.92 | 9.397 | 8.571 | 1.096 | 8.448% | 556.9 | -1.3 | 11.012 | 9.574 | 9.7 | -0.082 | 1.15 | 7.893% | -7.14 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 400 | 125 | 0 | 44.9 | 355.1 | 362 | 6.9 | 0 | 6.886 | 4.764 | 1.445 | 7.347% | 362.2 | 0 | 7.124 | 5.322 | 7.1 | -0.082 | 1.339 | 7.704% | -6.33 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 390 | 125 | 0 | 51.1 | 338.9 | 343.2 | 4.3 | 0 | 4.246 | 4.609 | 0.921 | 11.49% | 344.5 | 0 | 5.609 | 5.149 | 5.6 | -0.082 | 1.089 | 9.523% | -7.66 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 462 | 312 | 55 | 11 | 396 | 396.6 | 0.6 | 0.47 | 0.155 | 4.681 | 0.033 | 97.58% | 396.4 | 0.7 | -0.23 | 5.251 | 0.4 | -0.082 | 0 | 157.9% | -125.33 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 470 | 365 | 39 | 32.9 | 398.1 | 406.4 | 8.3 | -0.28 | 8.574 | 4.957 | 1.73 | 7.176% | 407 | -0.4 | 9.307 | 5.561 | 8.9 | -0.082 | 1.674 | 7.22% | -5.66 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.076 | 103 | 12 | 0 | 90.9 | 12.1 | 14.1 | 2 | 0.28 | 1.683 | 1.562 | 1.078 | 6.538% | 14.1 | 0.4 | 1.609 | 1.744 | 2 | -0.082 | 0.922 | 7.053% | -0.75 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.076 | 320 | 50 | 0 | 122.6 | 197.4 | 203 | 5.6 | -2.52 | 8.157 | 3.288 | 2 | 7.243% | 202 | -3.5 | 8.074 | 3.673 | 4.6 | -0.082 | 2 | 9.513% | -5.43 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 212 | 130 | 0.1 | 40.4 | 171.5 | 177.9 | 6.4 | 0.81 | 5.547 | 2.438 | 2 | 4.2% | 179 | 1.1 | 6.312 | 2.735 | 7.5 | -0.082 | 2 | 3.867% | -2.89 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.076 | 580.2 | 155.4 | 0 | 46.6 | 533.6 | 543.3 | 9.7 | 0.42 | 9.267 | 6.322 | 1.466 | 7.579% | 543.8 | 0.6 | 9.579 | 7.062 | 10.2 | -0.082 | 1.356 | 7.777% | -6.62 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.076 | 580.2 | 155.4 | 0 | 46.6 | 533.6 | 543.3 | 9.7 | 0.42 | 9.267 | 6.322 | 1.466 | 7.579% | 543.8 | 0.6 | 9.579 | 7.062 | 10.2 | -0.082 | 1.356 | 7.777% | -6.62 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 525 | 354 | 48 | 109.9 | 367.1 | 377.3 | 10.2 | 1.26 | 8.933 | 5.486 | 1.628 | 6.522% | 381.3 | 1.7 | 12.459 | 6.154 | 14.2 | -0.082 | 2 | 5.055% | -3.27 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 521 | 354 | 44 | 75.6 | 401.4 | 411.5 | 10.1 | 1.22 | 8.886 | 5.486 | 1.62 | 6.537% | 414.9 | 1.7 | 11.764 | 6.154 | 13.5 | -0.082 | 1.912 | 5.276% | -3.76 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.076 | 230 | 150 | 0 | 8 | 222 | 226.8 | 4.8 | -0.11 | 4.977 | 3.425 | 1.453 | 6.075% | 227 | -0.2 | 5.143 | 3.826 | 5 | -0.082 | 1.344 | 6.292% | -5.62 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.076 | 230 | 150 | 0 | 8.2 | 221.8 | 226.8 | 5 | -0.12 | 5.091 | 3.423 | 1.487 | 5.832% | 227.1 | -0.2 | 5.471 | 3.824 | 5.3 | -0.082 | 1.431 | 5.936% | -5.3 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.076 | 375 | 100 | 0 | 142.8 | 232.2 | 247.2 | 15 | 0.65 | 14.31 | 2.697 | 2 | 3.17% | 241.2 | 0.9 | 8.109 | 3.2 | 9 | -0.082 | 2 | 5.701% | -3.26 | 0.034 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.076 | 101 | 60 | 0 | 21.8 | 79.2 | 83.2 | 4 | 0 | 3.932 | 1.371 | 2 | 3.205% | 83.1 | 0 | 3.883 | 1.552 | 3.9 | -0.082 | 2 | 3.547% | -2.57 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 552 | 356 | 0 | 110.1 | 441.9 | 451 | 9.1 | -0.94 | 10.057 | 6.348 | 1.584 | 7.687% | 453.4 | -1.3 | 12.814 | 7.122 | 11.5 | -0.082 | 1.799 | 6.562% | -4.86 | 0.017 | 0.0578 | 5.933% | 5.163%
Hydro | WAT | HYDR | -0.076 | 34.2 | 0 | 0 | 9.4 | 24.8 | 25.7 | 0.9 | 0.22 | 0.606 | 0.33 | 1.834 | 4.876% | 24.9 | 0.3 | -0.194 | 0.392 | 0.1 | -0.082 | 0 | 47.31% | -30.85 | 0.034 | 0.05 | 0.2285% | 0.2528%
Hydro | WAT | HYDR | -0.076 | 35 | 0 | 0 | 10.1 | 24.9 | 26.2 | 1.3 | -0.05 | 1.356 | 0.536 | 2 | 3.432% | 26.2 | -0.1 | 1.354 | 0.599 | 1.3 | -0.082 | 2 | 3.701% | -2.4 | 0.017 | 0.05 | 0.2285% | 0.2528%
Thermal | NG | GT | -0.076 | 254 | 130 | 16 | 10.3 | 227.7 | 232.1 | 4.4 | 0.22 | 4.179 | 3.029 | 1.38 | 7.319% | 232.1 | 0.3 | 4.176 | 3.384 | 4.4 | -0.082 | 1.234 | 7.896% | -6.55 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.076 | 253 | 130 | 16 | 10.4 | 226.6 | 230.9 | 4.3 | -0.11 | 4.422 | 3.012 | 1.468 | 7.459% | 231.1 | -0.2 | 4.585 | 3.364 | 4.5 | -0.082 | 1.363 | 7.69% | -6.37 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.076 | 251 | 130 | 16 | 10 | 225 | 228 | 3 | -0.22 | 3.177 | 2.982 | 1.066 | 10.61% | 229.6 | -0.3 | 4.858 | 3.331 | 4.6 | -0.082 | 1.459 | 7.463% | -6.19 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.076 | 255 | 130 | 16 | 10.4 | 228.6 | 232.8 | 4.2 | -0.22 | 4.431 | 3.047 | 1.454 | 7.697% | 233.1 | -0.3 | 4.788 | 3.403 | 4.5 | -0.082 | 1.407 | 7.751% | -6.43 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.076 | 274 | 130 | 16 | 9.8 | 248.2 | 252.7 | 4.5 | -0.07 | 4.546 | 3.313 | 1.372 | 7.719% | 252.9 | -0.1 | 4.834 | 3.701 | 4.7 | -0.082 | 1.306 | 7.973% | -6.68 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.076 | 276 | 130 | 16 | 10.2 | 249.8 | 254.5 | 4.7 | -0.25 | 4.977 | 3.334 | 1.493 | 7.444% | 255.1 | -0.3 | 5.591 | 3.725 | 5.3 | -0.082 | 1.501 | 7.122% | -5.96 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.076 | 119 | 35 | 0 | 64 | 55 | 50.8 | -4.2 | -4.61 | 0.377 | 1.616 | 0.233 | -3.596% | 49.9 | -6.4 | 1.247 | 1.829 | -5.1 | -0.082 | 0.682 | -3.194% | 1.36 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.076 | 119 | 35 | 0 | 63.3 | 55.7 | 51.4 | -4.3 | -4.9 | 0.584 | 1.616 | 0.362 | -3.512% | 50.8 | -6.8 | 1.942 | 1.829 | -4.9 | -0.082 | 1.062 | -3.325% | 1.43 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.076 | 662.8 | 250 | 149.3 | 13.9 | 499.6 | 508.1 | 8.5 | -0.14 | 8.647 | 5.906 | 1.464 | 9.88% | 508.5 | -0.2 | 9.059 | 6.625 | 8.9 | -0.082 | 1.367 | 10.18% | -7.11 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 749.6 | 481.8 | 57.3 | 209.6 | 482.7 | 497 | 14.3 | -0.47 | 14.76 | 7.962 | 1.854 | 6.642% | 504.8 | -0.7 | 22.757 | 8.932 | 22.1 | -0.082 | 2 | 4.637% | -2.77 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 506.2 | 235 | 0 | 117 | 389.2 | 388.9 | -0.3 | -15.05 | 14.696 | 5.822 | 2 | -213.8% | 398 | -20.9 | 29.693 | 6.531 | 8.8 | -0.082 | 2 | 7.865% | -5.6 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.076 | 56.1 | 22.5 | 0 | 33.5 | 22.6 | 23.9 | 1.3 | -0.02 | 1.339 | 0.762 | 1.757 | 5.488% | 25.6 | 0 | 3.043 | 0.863 | 3 | -0.082 | 2 | 2.565% | -0.94 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.076 | 733 | 420 | 0 | 282.5 | 450.5 | 471 | 20.5 | -0.49 | 21.006 | 8.43 | 2 | 4.53% | 473 | -0.7 | 23.167 | 9.457 | 22.5 | -0.082 | 2 | 4.454% | -2.53 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.076 | 47 | 12 | 0 | 8.9 | 38.1 | 40 | 1.9 | -0.03 | 1.891 | 0.638 | 2 | 3.148% | 41.2 | 0 | 3.095 | 0.722 | 3.1 | -0.082 | 2 | 2.081% | -1.55 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.076 | 47 | 12 | 0 | 9.5 | 37.5 | 39.7 | 2.2 | 0.03 | 2.2 | 0.638 | 2 | 2.719% | 40.2 | 0 | 2.714 | 0.722 | 2.7 | -0.082 | 2 | 2.39% | -1.75 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.076 | 47 | 12 | 0 | 9.5 | 37.5 | 39.7 | 2.2 | -0.03 | 2.325 | 0.638 | 2 | 2.719% | 40.2 | 0 | 2.8 | 0.722 | 2.7 | -0.082 | 2 | 2.39% | -1.75 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | COGN | -0.076 | 78 | 58 | 0 | 19.9 | 58.1 | 60.1 | 2 | 0.02 | 1.931 | 1.059 | 1.824 | 4.954% | 60 | 0 | 1.907 | 1.199 | 1.9 | -0.082 | 1.591 | 5.625% | -3.86 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 87 | 67 | 3 | 14.3 | 69.7 | 70.4 | 0.7 | -0.06 | 0.754 | 0.966 | 0.78 | 15.78% | 71.2 | -0.1 | 1.539 | 1.084 | 1.5 | -0.082 | 1.42 | 7.946% | -5.87 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.076 | 35.6 | 0 | 0 | 2.6 | 33 | 34.9 | 1.9 | -2 | 3.929 | 0.545 | 2 | 2.388% | 35.5 | -2.8 | 5.28 | 0.609 | 2.5 | -0.082 | 2 | 1.957% | -1.66 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.076 | 331 | 140 | 0 | 63.8 | 267.2 | 280.6 | 13.4 | 1.73 | 11.667 | 3.807 | 2 | 3.131% | 283.5 | 2.4 | 13.921 | 4.27 | 16.3 | -0.082 | 2 | 2.777% | -2.07 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.076 | 1129 | 379 | 152 | 26.1 | 950.9 | 972.8 | 21.9 | 0.01 | 21.88 | 11.236 | 1.947 | 6.531% | 973.8 | 0 | 22.811 | 12.605 | 22.9 | -0.082 | 1.81 | 6.739% | -5.26 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.087 | 53.2 | 30 | 0 | 13.6 | 39.6 | 42.1 | 2.5 | -0.19 | 2.673 | 1.118 | 2 | 3.097% | 46.2 | -0.3 | 6.783 | 1.085 | 6.6 | -0.085 | 2 | 1.146% | -0.87 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.087 | 538 | 275 | 12 | 90.5 | 435.5 | 450.4 | 14.9 | 1.89 | 12.967 | 9.385 | 1.382 | 5.237% | 454.1 | 2.6 | 15.953 | 9.13 | 18.6 | -0.085 | 1.747 | 4.099% | -3.39 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 492 | 300 | 0 | 54.7 | 437.3 | 448.2 | 10.9 | 0.41 | 10.571 | 8.778 | 1.204 | 6.548% | 447.5 | 0.6 | 9.701 | 8.54 | 10.2 | -0.085 | 1.136 | 6.836% | -6.21 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.087 | 400 | 125 | 0 | 51.3 | 348.7 | 370.1 | 21.4 | -0.24 | 21.589 | 7.198 | 2 | 2.712% | 368.5 | -0.3 | 20.068 | 7.008 | 19.8 | -0.085 | 2 | 2.863% | -2.55 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.087 | 390 | 125 | 0 | 51 | 339 | 347.3 | 8.3 | -0.3 | 8.567 | 7.034 | 1.218 | 6.817% | 347.4 | -0.4 | 8.762 | 6.849 | 8.4 | -0.085 | 1.279 | 6.581% | -5.85 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.087 | 44 | 32 | 0 | 11.9 | 32.1 | 33.8 | 1.7 | 0.09 | 1.617 | 0.925 | 1.748 | 3.77% | 33.7 | 0.1 | 1.513 | 0.898 | 1.6 | -0.085 | 1.686 | 3.914% | -2.89 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.087 | 44 | 32 | 0 | 11.8 | 32.2 | 33.9 | 1.7 | 0.12 | 1.586 | 0.925 | 1.716 | 3.77% | 33.8 | 0.2 | 1.398 | 0.898 | 1.6 | -0.085 | 1.557 | 3.914% | -2.9 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.087 | 453 | 365 | 35 | 33.1 | 384.9 | 397.4 | 12.5 | 0.36 | 12.12 | 7.458 | 1.625 | 5.257% | 397.9 | 0.5 | 12.489 | 7.256 | 13 | -0.085 | 1.721 | 4.939% | -4.29 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.087 | 56.5 | 11.3 | 0 | 31.9 | 24.6 | 27.6 | 3 | 1.76 | 1.251 | 1.187 | 1.053 | 2.74% | 29.1 | 2.4 | 2.014 | 1.153 | 4.5 | -0.085 | 1.748 | 1.785% | -0.79 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.087 | 56.5 | 11.3 | 0 | 31.7 | 24.8 | 27.5 | 2.7 | 1.75 | 0.994 | 1.187 | 0.837 | 3.045% | 30 | 2.4 | 2.843 | 1.153 | 5.2 | -0.085 | 2 | 1.545% | -0.69 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.087 | 56.5 | 11.3 | 0 | 31.8 | 24.7 | 27.6 | 2.9 | 2.11 | 0.733 | 1.187 | 0.618 | 2.835% | 28.9 | 2.9 | 1.224 | 1.153 | 4.2 | -0.085 | 1.062 | 1.912% | -0.85 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.087 | 56.5 | 11.3 | 0 | 31.6 | 24.9 | 27.4 | 2.5 | 2.25 | 0.231 | 1.187 | 0.194 | 3.288% | 29.1 | 3.1 | 1.092 | 1.153 | 4.2 | -0.085 | 0.947 | 1.912% | -0.85 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | FOSS | -0.087 | 320 | 50 | 0 | 30.7 | 289.3 | 306.1 | 16.8 | -0.36 | 17.17 | 6.081 | 2 | 2.764% | 303.1 | -0.5 | 14.287 | 5.921 | 13.8 | -0.085 | 2 | 3.287% | -3.04 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | GT | -0.087 | 166 | 80 | 0 | 26.5 | 139.5 | 145.9 | 6.4 | -0.06 | 6.404 | 3.489 | 1.836 | 3.765% | 146 | -0.1 | 6.513 | 3.386 | 6.5 | -0.085 | 1.924 | 3.622% | -3.11 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.087 | 540.5 | 337.1 | 0 | 56.6 | 483.9 | 498 | 14.1 | 0.09 | 14.059 | 9.644 | 1.458 | 5.56% | 499.3 | 0.1 | 15.245 | 9.382 | 15.4 | -0.085 | 1.625 | 4.974% | -4.55 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 212 | 130 | 0.7 | 40.2 | 171.1 | 179.8 | 8.7 | -0.84 | 9.574 | 3.77 | 2 | 3.537% | 180.4 | -1.2 | 10.535 | 3.668 | 9.3 | -0.085 | 2 | 3.232% | -2.66 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.087 | 580.2 | 155.4 | 0 | 22.7 | 557.5 | 573.3 | 15.8 | -0.32 | 16.064 | 9.535 | 1.685 | 5.326% | 572.4 | -0.4 | 15.3 | 9.283 | 14.9 | -0.085 | 1.648 | 5.518% | -5.42 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.087 | 580.2 | 155.4 | 0 | 22.7 | 557.5 | 573.3 | 15.8 | -0.32 | 16.064 | 9.535 | 1.685 | 5.326% | 572.4 | -0.4 | 15.3 | 9.283 | 14.9 | -0.085 | 1.648 | 5.518% | -5.42 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.087 | 239 | 150 | 16 | 7.3 | 215.7 | 220.1 | 4.4 | 0.03 | 4.433 | 4.989 | 0.889 | 7.883% | 221.3 | 0 | 5.602 | 4.857 | 5.6 | -0.085 | 1.153 | 6.051% | -5.58 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.087 | 239 | 150 | 16 | 7.3 | 215.7 | 220.2 | 4.5 | 0.21 | 4.307 | 4.989 | 0.863 | 7.707% | 221.1 | 0.3 | 5.14 | 4.857 | 5.4 | -0.085 | 1.058 | 6.275% | -5.79 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 210 | 10 | 40 | 23.3 | 146.7 | 147.8 | 1.1 | -0.09 | 1.262 | 3.033 | 0.416 | 27.71% | 147.6 | -0.1 | 1.034 | 2.951 | 0.9 | -0.085 | 0.35 | 33.09% | -23.6 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 603 | 305 | 127 | 49.8 | 426.2 | 436.2 | 10 | 0.04 | 9.964 | 8.493 | 1.173 | 8.746% | 436.9 | 0 | 10.626 | 8.263 | 10.7 | -0.085 | 1.286 | 7.986% | -5.77 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.087 | 93 | 58 | 0 | 19.7 | 73.3 | 79 | 5.7 | 0 | 5.686 | 1.955 | 2 | 2.371% | 79.2 | 0 | 5.909 | 1.897 | 5.9 | -0.085 | 2 | 2.238% | -1.8 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 531 | 341 | 0 | 98.8 | 432.2 | 447.6 | 15.4 | -0.47 | 15.863 | 9.474 | 1.674 | 5.002% | 449.2 | -0.7 | 17.685 | 9.217 | 17 | -0.085 | 1.919 | 4.427% | -3.68 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | GT | -0.087 | 250 | 130 | 16 | 9.4 | 224.6 | 229.5 | 4.9 | 0.41 | 4.454 | 4.533 | 0.983 | 7.404% | 229.5 | 0.6 | 4.267 | 4.413 | 4.9 | -0.085 | 0.967 | 7.234% | -6.64 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.087 | 266 | 130 | 16 | 8.9 | 241.1 | 246.5 | 5.4 | 0.46 | 4.892 | 4.865 | 1.006 | 7.148% | 246.5 | 0.6 | 4.75 | 4.736 | 5.4 | -0.085 | 1.003 | 6.984% | -6.47 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.087 | 268 | 130 | 16 | 9.1 | 242.9 | 248.6 | 5.7 | 0.41 | 5.25 | 4.921 | 1.067 | 6.823% | 248 | 0.6 | 4.516 | 4.791 | 5.1 | -0.085 | 0.943 | 7.45% | -6.9 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | STM | -0.087 | 208 | 40 | 0 | 167.9 | 40.1 | 49.2 | 9.1 | 0 | 9.021 | 4.71 | 1.915 | 3.317% | 50.3 | 0 | 10.157 | 4.586 | 10.2 | -0.085 | 2 | 2.892% | -0.57 | 0.017 | 0.05 | 5.146% | 4.85%
Thermal | LIG | FOSS | -0.087 | 770 | 400 | 0 | 150.7 | 619.3 | 632 | 12.7 | 0.14 | 12.576 | 18.029 | 0.698 | 8.794% | 632.4 | 0.2 | 12.933 | 17.553 | 13.1 | -0.085 | 0.737 | 8.329% | -6.85 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.087 | 765 | 280 | 0 | 149.9 | 615.1 | 632.2 | 17.1 | 0.24 | 16.893 | 17.912 | 0.943 | 6.488% | 630.4 | 0.3 | 14.952 | 17.439 | 15.3 | -0.085 | 0.857 | 7.085% | -5.83 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.087 | 50.2 | 24 | 0 | 23.9 | 26.3 | 28.5 | 2.2 | -0.04 | 2.233 | 1.055 | 2 | 3.322% | 32.9 | -0.1 | 6.716 | 1.024 | 6.6 | -0.085 | 2 | 1.082% | -0.57 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.087 | 50.2 | 24 | 0 | 23.8 | 26.4 | 28.4 | 2 | -0.04 | 2.094 | 1.054 | 1.987 | 3.654% | 32.6 | -0.1 | 6.278 | 1.023 | 6.2 | -0.085 | 2 | 1.152% | -0.61 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.087 | 502.8 | 235 | 23.4 | 116.5 | 362.9 | 380.7 | 17.8 | -1.53 | 19.356 | 8.553 | 2 | 4.097% | 396.5 | -2.1 | 35.763 | 8.322 | 33.6 | -0.085 | 2 | 2.121% | -1.57 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 112 | 45 | 0 | 60.3 | 51.7 | 58.3 | 6.6 | -0.83 | 7.386 | 1.998 | 2 | 2.465% | 59.6 | -1.2 | 9.048 | 1.944 | 7.9 | -0.085 | 2 | 2.012% | -0.95 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.087 | 55.8 | 22.5 | 0 | 16.3 | 39.5 | 41.7 | 2.2 | -0.92 | 3.138 | 1.172 | 2 | 3.691% | 45.2 | -1.3 | 6.927 | 1.137 | 5.7 | -0.085 | 2 | 1.392% | -1 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | FOSS | -0.087 | 56 | 22.5 | 0 | 16.4 | 39.6 | 40.8 | 1.2 | -0.8 | 2.02 | 1.177 | 1.717 | 6.79% | 40.5 | -1.1 | 2.044 | 1.142 | 0.9 | -0.085 | 1.79 | 8.846% | -6.35 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.087 | 709 | 420 | 0 | 121.6 | 587.4 | 614.9 | 27.5 | 0.17 | 27.363 | 12.65 | 2 | 3.739% | 614.1 | 0.2 | 26.522 | 12.307 | 26.7 | -0.085 | 2 | 3.763% | -3.19 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 288 | 118 | 60 | 40.8 | 187.2 | 193.3 | 6.1 | 0.21 | 5.945 | 4.068 | 1.461 | 6.851% | 192.9 | 0.3 | 5.408 | 3.958 | 5.7 | -0.085 | 1.366 | 7.163% | -4.76 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.087 | 380 | 220 | 0 | 41.1 | 338.9 | 350.2 | 11.3 | -0.06 | 11.39 | 8.61 | 1.323 | 4.879% | 350.4 | -0.1 | 11.582 | 8.383 | 11.5 | -0.085 | 1.382 | 4.684% | -4.27 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.087 | 79 | 65 | 3 | 9 | 67 | 68 | 1 | 0.24 | 0.835 | 1.356 | 0.616 | 11.48% | 68.9 | 0.3 | 1.614 | 1.319 | 1.9 | -0.085 | 1.224 | 5.905% | -5.1 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 332 | 140 | 0 | 73.3 | 258.7 | 274 | 15.3 | -0.86 | 16.144 | 5.923 | 2 | 3.148% | 273.3 | -1.2 | 15.75 | 5.763 | 14.6 | -0.085 | 2 | 3.223% | -2.57 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.087 | 1127 | 379 | 152 | 106.5 | 868.5 | 897.5 | 29 | -1.58 | 30.544 | 17.396 | 1.756 | 5.636% | 905.1 | -2.2 | 38.768 | 16.924 | 36.6 | -0.085 | 2 | 4.363% | -3.44 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 259 | 170 | 10 | 42.8 | 206.2 | 210.4 | 4.2 | 0.3 | 3.918 | 1.305 | 2 | 5.557% | 209.4 | 0.4 | 2.84 | 1.254 | 3.2 | -0.053 | 2 | 7.158% | -5.79 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 492 | 300 | 0 | 142 | 350 | 357.8 | 7.8 | -0.04 | 7.856 | 2.579 | 2 | 5.681% | 358.6 | -0.1 | 8.717 | 2.478 | 8.6 | -0.053 | 2 | 5.057% | -3.66 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 362 | 149 | 9.8 | 135.1 | 217.1 | 224.3 | 7.2 | -1.65 | 8.859 | 1.846 | 2 | 4.529% | 223.8 | -2.3 | 9.006 | 1.773 | 6.7 | -0.053 | 2 | 4.777% | -2.91 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 173 | 106 | 7 | 37.8 | 128.2 | 128.9 | 0.7 | -0.12 | 0.819 | 0.87 | 0.942 | 22.28% | 128.9 | -0.2 | 0.9 | 0.836 | 0.7 | -0.053 | 1.077 | 21.87% | -16.44 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.054 | 560 | 135 | 0 | 72.9 | 487.1 | 493.3 | 6.2 | 0.03 | 6.139 | 3.933 | 1.561 | 8.134% | 493 | 0 | 5.867 | 3.792 | 5.9 | -0.053 | 1.547 | 8.389% | -7.43 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.054 | 400 | 180 | 0 | 94 | 306 | 311.4 | 5.4 | 0.34 | 5.055 | 2.208 | 2 | 6.672% | 308.3 | 0.5 | 1.78 | 2.129 | 2.3 | -0.053 | 0.836 | 15.37% | -11.96 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.054 | 390 | 125 | 0 | 91.5 | 298.5 | 304.2 | 5.7 | -0.23 | 5.98 | 2.142 | 2 | 6.163% | 301.4 | -0.3 | 3.19 | 2.065 | 2.9 | -0.053 | 1.544 | 11.89% | -9.25 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.054 | 237.4 | 168 | 0 | 68.8 | 168.6 | 170.8 | 2.2 | 0 | 2.235 | 1.244 | 1.796 | 9.725% | 169.9 | 0 | 1.329 | 1.196 | 1.3 | -0.053 | 1.111 | 16.15% | -11.65 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 1160.5 | 430 | 140 | 440.8 | 579.7 | 598 | 18.3 | -1.31 | 19.646 | 5.349 | 2 | 5.709% | 595.3 | -1.8 | 17.379 | 5.139 | 15.6 | -0.053 | 2 | 6.573% | -3.34 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 667 | 482 | 27 | 31.7 | 608.3 | 616.5 | 8.2 | -0.76 | 8.911 | 3.354 | 2 | 7.324% | 614.9 | -1.1 | 7.688 | 3.223 | 6.6 | -0.053 | 2 | 8.931% | -8.29 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 212 | 130 | 0 | 40.3 | 171.7 | 175.5 | 3.8 | 0.44 | 3.329 | 1.111 | 2 | 5.029% | 174.9 | 0.6 | 2.561 | 1.068 | 3.2 | -0.053 | 2 | 5.861% | -4.82 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.054 | 68.4 | 0 | 0 | 19.9 | 48.5 | 49.2 | 0.7 | -0.12 | 0.781 | 0.499 | 1.565 | 8.835% | 48.9 | -0.2 | 0.571 | 0.481 | 0.4 | -0.053 | 1.187 | 15.18% | -10.84 | 0.017 | 0.05 | 5.986% | 5.139%
Wind | WND | WIND | -0.054 | 58.2 | 0 | 0 | 12.4 | 45.8 | 46.9 | 1.1 | -0.12 | 1.259 | 0.425 | 2 | 4.788% | 46.8 | -0.2 | 1.164 | 0.41 | 1 | -0.053 | 2 | 5.169% | -4.09 | 0.017 | 0.05 | 5.986% | 5.139%
Thermal | SUB | FOSS | -0.054 | 434.1 | 179 | 0 | 20.7 | 413.4 | 419.2 | 5.8 | -0.39 | 6.234 | 3.169 | 1.967 | 6.741% | 417.8 | -0.5 | 4.936 | 3.055 | 4.4 | -0.053 | 1.616 | 8.721% | -8.45 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.054 | 957.5 | 461 | 80.2 | 69.2 | 808.1 | 821.9 | 13.8 | 0.4 | 13.448 | 4.598 | 2 | 6.247% | 821.8 | 0.6 | 13.179 | 4.418 | 13.7 | -0.053 | 2 | 6.176% | -5.31 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 962.9 | 461 | 118.2 | 79 | 765.7 | 765.2 | -0.5 | -9.94 | 9.366 | 4.427 | 2 | -173.4% | 766.9 | -13.8 | 14.957 | 4.254 | 1.2 | -0.053 | 2 | 70.9% | -57.4 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 526 | 355 | 43 | 14.2 | 468.8 | 477.2 | 8.4 | 0.3 | 8.087 | 2.531 | 2 | 5.639% | 476.7 | 0.4 | 7.447 | 2.432 | 7.9 | -0.053 | 2 | 5.885% | -5.34 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.054 | 239 | 150 | 16 | 18.1 | 204.9 | 208.3 | 3.4 | -0.46 | 3.863 | 1.504 | 2 | 6.335% | 208.8 | -0.6 | 4.477 | 1.45 | 3.9 | -0.053 | 2 | 5.421% | -4.72 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.054 | 246 | 150 | 16 | 16.8 | 213.2 | 224 | 10.8 | 1.06 | 9.675 | 1.592 | 2 | 2.053% | 224.8 | 1.5 | 10.097 | 1.535 | 11.6 | -0.053 | 2 | 1.876% | -1.65 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 238.8 | 14.3 | 40 | 48.3 | 150.5 | 153 | 2.5 | -0.17 | 2.683 | 1.042 | 2 | 8.608% | 152.4 | -0.2 | 2.153 | 1.001 | 1.9 | -0.053 | 2 | 11.12% | -7.11 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 641 | 305 | 132 | 201.8 | 307.2 | 313.2 | 6 | -1.33 | 7.316 | 2.668 | 2 | 9.62% | 315 | -1.9 | 9.571 | 2.563 | 7.8 | -0.053 | 2 | 7.263% | -3.54 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 631.9 | 260 | 126 | 27.8 | 478.1 | 482.9 | 4.8 | -2.95 | 7.682 | 2.651 | 2 | 11.85% | 483 | -4.1 | 8.962 | 2.548 | 4.9 | -0.053 | 2 | 11.4% | -8.78 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 631.9 | 260 | 126 | 30.8 | 475.1 | 481.8 | 6.7 | -3.54 | 10.178 | 2.652 | 2 | 8.492% | 482 | -4.9 | 11.783 | 2.548 | 6.9 | -0.053 | 2 | 8.094% | -6.19 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | COGN | -0.054 | 101 | 73 | 0 | 21.5 | 79.5 | 82 | 2.5 | 0 | 2.558 | 0.629 | 2 | 3.647% | 81.5 | 0 | 2.054 | 0.603 | 2 | -0.053 | 2 | 4.475% | -3.56 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | GT | -0.054 | 257 | 130 | 16 | 100.8 | 140.2 | 141.6 | 1.4 | 0 | 1.395 | 1.299 | 1.074 | 16.54% | 141.9 | 0 | 1.755 | 1.252 | 1.7 | -0.053 | 1.402 | 13.37% | -7.41 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.054 | 255 | 130 | 16 | 79.1 | 159.9 | 162.3 | 2.4 | 1.52 | 0.899 | 1.268 | 0.709 | 9.574% | 162.6 | 2.1 | 0.637 | 1.222 | 2.7 | -0.053 | 0.521 | 8.353% | -5.32 | 0.017 | 0.05 | 6.335% | 5.367%
Thermal | NG | GT | -0.054 | 280 | 130 | 16 | 114.8 | 149.2 | 153.5 | 4.3 | 0.04 | 4.286 | 1.391 | 2 | 5.867% | 152.5 | 0.1 | 3.31 | 1.341 | 3.3 | -0.053 | 2 | 7.504% | -4.06 | 0.017 | 0.05 | 6.335% | 5.367%
CombinedCycle | CC | COGN | -0.054 | 354 | 229 | 11 | 70 | 273 | 278.6 | 5.6 | 3.01 | 2.538 | 1.798 | 1.412 | 5.694% | 280.5 | 4.2 | 3.291 | 1.727 | 7.5 | -0.053 | 1.906 | 4.173% | -3.27 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 669.7 | 250 | 113.9 | 63.4 | 492.4 | 502.7 | 10.3 | 0.31 | 9.957 | 2.913 | 2 | 5.854% | 499.7 | 0.4 | 6.851 | 2.799 | 7.3 | -0.053 | 2 | 8.108% | -6.07 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 525 | 329.8 | 44 | 50.7 | 430.3 | 439.1 | 8.8 | 0.06 | 8.77 | 2.521 | 2 | 5.373% | 449.3 | 0.1 | 18.886 | 2.422 | 19 | -0.053 | 2 | 2.442% | -2.04 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 520 | 349.1 | 15.7 | 58.3 | 446 | 453.7 | 7.7 | 0.26 | 7.493 | 2.643 | 2 | 6.082% | 462.3 | 0.4 | 15.972 | 2.54 | 16.3 | -0.053 | 2 | 2.82% | -2.46 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 751.3 | 513 | 47 | 173.1 | 531.2 | 536.4 | 5.2 | -3.6 | 8.837 | 3.691 | 2 | 13.01% | 536.6 | -5 | 10.408 | 3.547 | 5.4 | -0.053 | 2 | 12.3% | -8.85 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 536.3 | 235 | 0 | 297.3 | 239 | 246.4 | 7.4 | -1.06 | 8.44 | 2.811 | 2 | 6.526% | 247.8 | -1.5 | 10.299 | 2.701 | 8.8 | -0.053 | 2 | 5.387% | -2.44 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.054 | 380 | 222 | 0 | 41 | 339 | 344.6 | 5.6 | 0.06 | 5.516 | 2.685 | 2 | 6.112% | 343.4 | 0.1 | 4.339 | 2.589 | 4.4 | -0.053 | 1.676 | 7.635% | -6.93 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.054 | 932.6 | 360 | 0 | 113 | 819.6 | 842.7 | 23.1 | -0.29 | 23.321 | 4.925 | 2 | 3.635% | 840.3 | -0.4 | 21.017 | 4.748 | 20.7 | -0.053 | 2 | 3.981% | -3.56 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.054 | 932.6 | 360 | 0 | 113 | 819.6 | 842.7 | 23.1 | -0.29 | 23.321 | 4.925 | 2 | 3.635% | 840.3 | -0.4 | 21.017 | 4.748 | 20.7 | -0.053 | 2 | 3.981% | -3.56 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.054 | 932.6 | 360 | 0 | 113 | 819.6 | 842.7 | 23.1 | -0.29 | 23.321 | 4.925 | 2 | 3.635% | 840.3 | -0.4 | 21.017 | 4.748 | 20.7 | -0.053 | 2 | 3.981% | -3.56 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.054 | 932.6 | 360 | 0 | 113 | 819.6 | 842.7 | 23.1 | -0.29 | 23.321 | 4.925 | 2 | 3.635% | 840.3 | -0.4 | 21.017 | 4.748 | 20.7 | -0.053 | 2 | 3.981% | -3.56 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.054 | 880 | 465 | 122.4 | 71.2 | 686.4 | 700.4 | 14 | -6.92 | 20.904 | 3.97 | 2 | 5.659% | 704.4 | -9.6 | 27.663 | 3.815 | 18 | -0.053 | 2 | 4.32% | -3.43 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 92 | 71 | 3 | 16.7 | 72.3 | 73.4 | 1.1 | -0.06 | 1.1 | 0.466 | 2 | 7.553% | 73.5 | -0.1 | 1.261 | 0.448 | 1.2 | -0.053 | 2 | 6.796% | -5.4 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.054 | 1129 | 379 | 152 | 594.6 | 382.4 | 396.2 | 13.8 | 0.1 | 13.631 | 5.121 | 2 | 7.365% | 394.6 | 0.1 | 12.013 | 4.92 | 12.2 | -0.053 | 2 | 8.177% | -2.82 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.08 | 56 | 30 | 0 | 25.8 | 30.2 | 32.8 | 2.6 | -0.16 | 2.762 | 1.345 | 2 | 2.883% | 36.4 | -0.2 | 6.386 | 1.179 | 6.2 | -0.071 | 2 | 1.073% | -0.64 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 255 | 155 | 0 | 80.2 | 174.8 | 178.3 | 3.5 | -0.64 | 4.098 | 5.202 | 0.788 | 9.722% | 176.3 | -0.9 | 2.352 | 4.611 | 1.5 | -0.071 | 0.51 | 20.14% | -15.52 | 0.017 | 0.0578 | 5.933% | 5.163%
Hydro | NA | HYDR | -0.08 | 30 | 0 | 0 | 18.1 | 11.9 | 13.5 | 1.6 | 0 | 1.611 | 0.801 | 2 | 2.518% | 13.4 | 0 | 1.43 | 0.712 | 1.5 | -0.071 | 2 | 2.386% | -1.04 | 0.017 | 0.05 | 0.2285% | 0.2528%
CombinedCycle | CC | COGN | -0.08 | 492 | 300 | 0 | 15.6 | 476.4 | 488.3 | 11.9 | -1.88 | 13.715 | 10.038 | 1.366 | 5.515% | 489.8 | -2.6 | 16.039 | 8.897 | 13.4 | -0.071 | 1.803 | 4.347% | -4.74 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 338 | 99.1 | 7.4 | 230.8 | 99.8 | 117.2 | 17.4 | -0.47 | 17.876 | 6.744 | 2 | 2.592% | 120.2 | -0.7 | 21.085 | 5.978 | 20.4 | -0.071 | 2 | 1.962% | -0.65 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 237 | 154 | 0 | 82.6 | 154.4 | 167.3 | 12.9 | 0.12 | 12.812 | 4.835 | 2 | 2.452% | 169.2 | 0.2 | 14.684 | 4.286 | 14.8 | -0.071 | 2 | 1.897% | -1.39 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 149 | 122 | 5 | 20 | 124 | 127.1 | 3.1 | -0.12 | 3.244 | 2.938 | 1.104 | 6.418% | 127.7 | -0.2 | 3.871 | 2.604 | 3.7 | -0.071 | 1.487 | 4.773% | -4.46 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.08 | 560 | 135 | 0 | 180.7 | 379.3 | 396.6 | 17.3 | -0.26 | 17.484 | 11.782 | 1.484 | 4.318% | 393.8 | -0.4 | 14.851 | 10.474 | 14.5 | -0.071 | 1.418 | 4.572% | -3.49 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 400 | 125 | 0 | 90.1 | 309.9 | 323.2 | 13.3 | 1.6 | 11.765 | 8.056 | 1.46 | 4.012% | 321.5 | 2.2 | 9.359 | 7.161 | 11.6 | -0.071 | 1.307 | 4.083% | -3.56 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 390 | 125 | 0 | 168.5 | 221.5 | 232 | 10.5 | -0.46 | 10.92 | 7.378 | 1.48 | 4.955% | 241.9 | -0.6 | 21.034 | 6.559 | 20.4 | -0.071 | 2 | 2.264% | -1.45 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 1161.5 | 379 | 140 | 530 | 491.5 | 529 | 37.5 | 1.91 | 35.56 | 20.84 | 1.706 | 4.131% | 551.3 | 2.7 | 57.117 | 18.472 | 59.8 | -0.071 | 2 | 2.299% | -1.1 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 395 | 187 | 115 | 87.5 | 192.5 | 198.3 | 5.8 | -0.71 | 6.474 | 5.712 | 1.133 | 9.085% | 199.6 | -1 | 8.114 | 5.063 | 7.1 | -0.071 | 1.602 | 6.587% | -3.61 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.08 | 103 | 12 | 0 | 89.5 | 13.5 | 16.1 | 2.6 | 0.43 | 2.16 | 2.72 | 0.794 | 5.293% | 15.6 | 0.6 | 1.506 | 2.418 | 2.1 | -0.071 | 0.623 | 5.817% | -0.84 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 1045 | 518 | 303 | 50.6 | 691.4 | 693.9 | 2.5 | 1.71 | 0.815 | 15.138 | 0.054 | 55.74% | 696.2 | 2.4 | 2.426 | 13.418 | 4.8 | -0.071 | 0.181 | 25.77% | -19.2 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 567.4 | 337.1 | 0 | 125.3 | 442.1 | 462.9 | 20.8 | 2.61 | 18.223 | 11.576 | 1.574 | 3.639% | 471.2 | 3.6 | 25.469 | 10.261 | 29.1 | -0.071 | 2 | 2.308% | -2.02 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.08 | 592.6 | 155.4 | 0 | 33.5 | 559.1 | 576.9 | 17.8 | -1.17 | 18.946 | 11.079 | 1.71 | 4.441% | 573.1 | -1.6 | 15.646 | 9.849 | 14 | -0.071 | 1.589 | 5.011% | -5.32 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 592.6 | 155.4 | 0 | 33.5 | 559.1 | 576.9 | 17.8 | -1.17 | 18.946 | 11.079 | 1.71 | 4.441% | 573.1 | -1.6 | 15.646 | 9.849 | 14 | -0.071 | 1.589 | 5.011% | -5.32 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 597.2 | 155.3 | 0 | 33 | 564.2 | 569.7 | 5.5 | -0.32 | 5.751 | 11.241 | 0.512 | 14.48% | 566.6 | -0.4 | 2.835 | 9.992 | 2.4 | -0.071 | 0.284 | 29.46% | -31.33 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 597.2 | 155.3 | 0 | 33 | 564.2 | 569.7 | 5.5 | -0.32 | 5.751 | 11.241 | 0.512 | 14.48% | 566.6 | -0.4 | 2.835 | 9.992 | 2.4 | -0.071 | 0.284 | 29.46% | -31.33 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 499 | 305 | 10 | 158.5 | 330.5 | 347.9 | 17.4 | 2.24 | 15.141 | 9.976 | 1.518 | 3.825% | 347.8 | 3.1 | 14.144 | 8.843 | 17.3 | -0.071 | 1.6 | 3.415% | -2.55 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 493 | 320 | 10 | 124 | 359 | 378.3 | 19.3 | 4.01 | 15.302 | 9.854 | 1.553 | 3.407% | 381.5 | 5.6 | 16.882 | 8.734 | 22.5 | -0.071 | 1.933 | 2.594% | -2.13 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 953.2 | 461 | 141 | 33.2 | 779 | 806.6 | 27.6 | 0.17 | 27.469 | 16.571 | 1.658 | 4.606% | 814.8 | 0.2 | 35.562 | 14.688 | 35.8 | -0.071 | 2 | 3.151% | -2.9 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 956.3 | 461 | 141 | 66.6 | 748.7 | 779.4 | 30.7 | 7.13 | 23.547 | 16.633 | 1.416 | 4.154% | 789.2 | 9.9 | 30.554 | 14.743 | 40.5 | -0.071 | 2 | 2.795% | -2.46 | 0.017 | 0.0578 | 5.933% | 5.163%
Wind | WND | WIND | -0.08 | 143.6 | 0 | 0 | 7.1 | 136.5 | 141.2 | 4.7 | 1.24 | 3.392 | 3.833 | 0.885 | 4.08% | 142.4 | 1.7 | 4.126 | 3.408 | 5.9 | -0.071 | 1.211 | 2.885% | -3.08 | 0.017 | 0.05 | 5.986% | 5.139%
Hydro | NA | HYDR | -0.08 | 9.9 | 0 | 0 | 6 | 3.9 | 9.9 | 6 | 0 | 6.034 | 0.264 | 2 | 0.2247% | 9.9 | 0 | 6.034 | 0.235 | 6 | -0.071 | 2 | 0.2% | -0.08 | 0.017 | 0.05 | 0.2285% | 0.2528%
CombinedCycle | CC | COGN | -0.08 | 173.1 | 0 | 40 | 74.9 | 58.2 | 69.4 | 11.2 | -0.09 | 11.199 | 2.715 | 2 | 2.063% | 77.9 | -0.1 | 19.818 | 2.407 | 19.7 | -0.071 | 2 | 1.041% | -0.39 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 634 | 305 | 117 | 176 | 341 | 354.8 | 13.8 | -0.89 | 14.703 | 10.548 | 1.394 | 6.128% | 357.1 | -1.2 | 17.361 | 9.349 | 16.1 | -0.071 | 1.857 | 4.662% | -2.82 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 644 | 305 | 132 | 206.8 | 305.2 | 320.1 | 14.9 | -0.02 | 14.952 | 10.446 | 1.431 | 5.765% | 327.5 | 0 | 22.347 | 9.259 | 22.3 | -0.071 | 2 | 3.419% | -1.82 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 310.2 | 145 | 72 | 77.2 | 161 | 164 | 3 | -0.59 | 3.559 | 4.86 | 0.732 | 13.8% | 166 | -0.8 | 5.821 | 4.308 | 5 | -0.071 | 1.351 | 7.347% | -4.29 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 310.2 | 145 | 72 | 76.4 | 161.8 | 163.6 | 1.8 | 0 | 1.777 | 4.86 | 0.366 | 22.99% | 166 | 0 | 4.214 | 4.308 | 4.2 | -0.071 | 0.978 | 8.747% | -5.13 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.08 | 826 | 260 | 0 | 463.1 | 362.9 | 390.7 | 27.8 | -0.48 | 28.325 | 14.905 | 1.9 | 3.963% | 393.5 | -0.7 | 31.236 | 13.25 | 30.6 | -0.071 | 2 | 3.195% | -1.58 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.08 | 820 | 310 | 0 | 469.1 | 350.9 | 368 | 17.1 | -0.67 | 17.706 | 21.89 | 0.809 | 6.395% | 365.3 | -0.9 | 15.294 | 19.459 | 14.4 | -0.071 | 0.786 | 6.74% | -3.25 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.08 | 740 | 280 | 0 | 252.2 | 487.8 | 505.6 | 17.8 | -0.38 | 18.229 | 19.754 | 0.923 | 5.545% | 503.8 | -0.5 | 16.569 | 17.56 | 16 | -0.071 | 0.944 | 5.475% | -4.06 | 0.017 | 0.05 | 6.284% | 5.784%
Hydro | NA | HYDR | -0.08 | 34 | 0 | 0 | 28.7 | 5.3 | 13.2 | 7.9 | 0 | 7.906 | 0.908 | 2 | 0.5774% | 13.3 | 0 | 7.969 | 0.807 | 8 | -0.071 | 2 | 0.5065% | -0.08 | 0.017 | 0.05 | 0.2285% | 0.2528%
Thermal | SUB | FOSS | -0.08 | 650 | 189.6 | 0 | 316.3 | 333.7 | 346.5 | 12.8 | -0.82 | 13.606 | 10.238 | 1.329 | 6.773% | 349 | -1.1 | 16.463 | 9.101 | 15.3 | -0.071 | 1.809 | 5.029% | -2.91 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 650 | 189.6 | 0 | 316.3 | 333.7 | 346.5 | 12.8 | -0.82 | 13.606 | 10.238 | 1.329 | 6.773% | 349 | -1.1 | 16.463 | 9.101 | 15.3 | -0.071 | 1.809 | 5.029% | -2.91 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 650 | 189.6 | 0 | 316.3 | 333.7 | 346.5 | 12.8 | -0.82 | 13.606 | 10.238 | 1.329 | 6.773% | 349 | -1.1 | 16.463 | 9.101 | 15.3 | -0.071 | 1.809 | 5.029% | -2.91 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 650 | 189.6 | 0 | 316.3 | 333.7 | 346.5 | 12.8 | -0.82 | 13.606 | 10.238 | 1.329 | 6.773% | 349 | -1.1 | 16.463 | 9.101 | 15.3 | -0.071 | 1.809 | 5.029% | -2.91 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 650 | 189.6 | 0 | 316.3 | 333.7 | 346.5 | 12.8 | -0.82 | 13.606 | 10.238 | 1.329 | 6.773% | 349 | -1.1 | 16.463 | 9.101 | 15.3 | -0.071 | 1.809 | 5.029% | -2.91 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 756.5 | 464.1 | 90 | 201.7 | 464.8 | 479.1 | 14.3 | 0 | 14.321 | 13.598 | 1.053 | 7.056% | 479.4 | 0 | 14.621 | 12.053 | 14.6 | -0.071 | 1.213 | 6.133% | -4.24 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 498.8 | 235 | 0 | 260.8 | 238 | 259.3 | 21.3 | -0.71 | 22.008 | 10.176 | 2 | 3.124% | 274.2 | -1 | 37.214 | 9.02 | 36.2 | -0.071 | 2 | 1.631% | -0.88 | 0.017 | 0.0578 | 5.933% | 5.163%
Hydro | NA | HYDR | -0.08 | 9.9 | 0 | 0 | 5.9 | 4 | 9.9 | 5.9 | 0 | 5.944 | 0.264 | 2 | 0.2285% | 9.9 | 0 | 5.941 | 0.235 | 5.9 | -0.071 | 2 | 0.2034% | -0.09 | 0.017 | 0.05 | 0.2285% | 0.2528%
CombinedCycle | CC | COGN | -0.08 | 119.8 | 80 | 10 | 27 | 82.8 | 83.8 | 1 | 0.06 | 0.948 | 2.24 | 0.423 | 16% | 84.6 | 0.1 | 1.675 | 1.985 | 1.8 | -0.071 | 0.844 | 7.891% | -6.12 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 737 | 420 | 0 | 265.6 | 471.4 | 485.8 | 14.4 | 2.28 | 12.171 | 15.036 | 0.809 | 6.826% | 483.1 | 3.2 | 8.494 | 13.327 | 11.7 | -0.071 | 0.637 | 7.456% | -5.37 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 302.2 | 118 | 70 | 77.1 | 155.1 | 164.3 | 9.2 | 0.44 | 8.819 | 4.737 | 1.861 | 4.383% | 169.1 | 0.6 | 13.429 | 4.199 | 14 | -0.071 | 2 | 2.556% | -1.48 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.08 | 385 | 222 | 0 | 10.3 | 374.7 | 380.6 | 5.9 | -0.53 | 6.396 | 9.946 | 0.643 | 8.705% | 380.9 | -0.7 | 6.932 | 8.841 | 6.2 | -0.071 | 0.784 | 7.353% | -8.05 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 932.6 | 360 | 0 | 81.4 | 851.2 | 885.6 | 34.4 | -0.11 | 34.531 | 17.783 | 1.942 | 3.616% | 887.5 | -0.2 | 36.47 | 15.808 | 36.3 | -0.071 | 2 | 3.041% | -3.13 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 932.6 | 360 | 0 | 81.4 | 851.2 | 885.6 | 34.4 | -0.11 | 34.531 | 17.783 | 1.942 | 3.616% | 887.5 | -0.2 | 36.47 | 15.808 | 36.3 | -0.071 | 2 | 3.041% | -3.13 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 932.6 | 360 | 0 | 81.4 | 851.2 | 885.6 | 34.4 | -0.11 | 34.531 | 17.783 | 1.942 | 3.616% | 887.5 | -0.2 | 36.47 | 15.808 | 36.3 | -0.071 | 2 | 3.041% | -3.13 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.08 | 932.6 | 360 | 0 | 81.4 | 851.2 | 885.6 | 34.4 | -0.11 | 34.531 | 17.783 | 1.942 | 3.616% | 887.5 | -0.2 | 36.47 | 15.808 | 36.3 | -0.071 | 2 | 3.041% | -3.13 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.08 | 76 | 60 | 0 | 15.2 | 60.8 | 63.1 | 2.3 | -0.15 | 2.392 | 1.826 | 1.31 | 4.418% | 62.6 | -0.2 | 1.965 | 1.6 | 1.8 | -0.071 | 1.228 | 5.012% | -4.49 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | NG | COGN | -0.08 | 76 | 60 | 0 | 14 | 62 | 64.2 | 2.2 | 0.22 | 1.979 | 1.826 | 1.084 | 4.619% | 64.3 | 0.3 | 2.061 | 1.6 | 2.3 | -0.071 | 1.288 | 3.922% | -3.58 | 0.017 | 0.05 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 264 | 120 | 30 | 113.7 | 120.3 | 129.5 | 9.2 | -0.18 | 9.348 | 4.774 | 1.958 | 3.829% | 133.6 | -0.3 | 13.531 | 4.231 | 13.3 | -0.071 | 2 | 2.351% | -1.2 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.08 | 270 | 150 | 0 | 119 | 151 | 156.1 | 5.1 | -0.86 | 5.888 | 5.508 | 1.069 | 7.064% | 156.2 | -1.2 | 6.398 | 4.882 | 5.2 | -0.071 | 1.31 | 6.15% | -3.87 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.08 | 664 | 158 | 0 | 503.4 | 160.6 | 181.8 | 21.2 | -0.09 | 21.19 | 16.517 | 1.283 | 4.177% | 180.2 | -0.1 | 19.716 | 14.683 | 19.6 | -0.071 | 1.343 | 4.01% | -1.09 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.08 | 662 | 158 | 0 | 503.2 | 158.8 | 177.5 | 18.7 | -0.32 | 18.975 | 16.508 | 1.149 | 4.722% | 176.2 | -0.4 | 17.823 | 14.675 | 17.4 | -0.071 | 1.215 | 4.504% | -1.22 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.08 | 551 | 226 | 0 | 322.9 | 228.1 | 246.8 | 18.7 | -0.17 | 18.783 | 13.146 | 1.429 | 3.93% | 245.1 | -0.2 | 17.186 | 11.686 | 17 | -0.071 | 1.471 | 3.837% | -1.79 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.08 | 608 | 303 | 0 | 298.1 | 309.9 | 324.6 | 14.7 | -0.12 | 14.883 | 13.975 | 1.065 | 5.517% | 323.4 | -0.2 | 13.737 | 12.423 | 13.5 | -0.071 | 1.106 | 5.331% | -3.06 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.08 | 1129 | 379 | 152 | 70.6 | 906.4 | 937.3 | 30.9 | -1.45 | 32.289 | 19.932 | 1.62 | 4.873% | 931.8 | -2 | 27.395 | 17.667 | 25.4 | -0.071 | 1.551 | 5.261% | -4.76 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.042 | 240 | 140 | 0 | 68.1 | 171.9 | 173.8 | 1.9 | 0.26 | 1.663 | 2.541 | 0.654 | 8.857% | 172.2 | 0.4 | -0.109 | 2.437 | 0.3 | -0.041 | 0 | 54.76% | -40.02 | 0.017 | 0.0578 | 5.933% | 5.163%
Hydro | NA | HYDR | -0.042 | 30 | 0 | 0 | 18.1 | 11.9 | 26 | 14.1 | 0 | 14.119 | 0.425 | 2 | 0.1509% | 29.9 | 0 | 18.003 | 0.408 | 18 | -0.041 | 2 | 0.1155% | -0.04 | 0.017 | 0.05 | 0.2285% | 0.2528%
Wind | WND | WIND | -0.042 | 126.4 | 0 | 0 | 5 | 121.4 | 122.6 | 1.2 | -0.59 | 1.8 | 1.789 | 1.006 | 7.397% | 122.5 | -0.8 | 1.892 | 1.719 | 1.1 | -0.041 | 1.101 | 7.878% | -7.7 | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.042 | 492 | 300 | 0 | 159.3 | 332.7 | 343.5 | 10.8 | 7.24 | 3.525 | 5.21 | 0.677 | 3.192% | 354 | 10.1 | 11.238 | 4.996 | 21.3 | -0.041 | 2 | 1.58% | -1.09 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.042 | 324 | 89.7 | 6.3 | 226.5 | 91.2 | 105 | 13.8 | -3.36 | 17.14 | 3.364 | 2 | 1.646% | 109.3 | -4.7 | 22.794 | 3.226 | 18.1 | -0.041 | 2 | 1.225% | -0.35 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.042 | 233 | 154 | 0 | 78.3 | 154.7 | 161.5 | 6.8 | -0.2 | 6.931 | 2.467 | 2 | 2.403% | 162.9 | -0.3 | 8.391 | 2.366 | 8.2 | -0.041 | 2 | 1.945% | -1.32 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.042 | 148 | 118 | 5 | 24.9 | 118.1 | 120.4 | 2.3 | -0.12 | 2.427 | 1.514 | 1.603 | 4.517% | 120.7 | -0.2 | 2.736 | 1.452 | 2.6 | -0.041 | 1.884 | 3.901% | -3.17 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.042 | 560 | 135 | 0 | 420.5 | 139.5 | 150.8 | 11.3 | 0.29 | 10.962 | 5.945 | 1.844 | 3.472% | 155.6 | 0.4 | 15.635 | 5.712 | 16.1 | -0.041 | 2 | 2.379% | -0.6 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.042 | 400 | 125 | 0 | 268.9 | 131.1 | 140.5 | 9.4 | 1.67 | 7.716 | 3.948 | 1.954 | 2.982% | 139.6 | 2.3 | 6.126 | 3.793 | 8.5 | -0.041 | 1.615 | 3.219% | -1.08 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.042 | 390 | 125 | 0 | 256.9 | 133.1 | 139.9 | 6.8 | -0.37 | 7.17 | 3.851 | 1.862 | 4.019% | 137.4 | -0.5 | 4.828 | 3.7 | 4.3 | -0.041 | 1.305 | 6.204% | -2.16 | 0.017 | 0.05 | 6.284% | 5.784%
Wind | WND | WIND | -0.042 | 180.3 | 0 | 0 | 6.3 | 174 | 174.1 | 0.1 | -0.59 | 0.715 | 2.552 | 0.28 | 126.5% | 174 | -0.8 | 0.821 | 2.451 | 0 | -0.041 | 0.335 | 0% |  | 0.017 | 0.05 | 5.986% | 5.139%
CombinedCycle | CC | COGN | -0.042 | 1134.5 | 379 | 140 | 614.2 | 380.3 | 412.3 | 32 | 0.56 | 31.417 | 10.531 | 2 | 2.483% | 430.6 | 0.8 | 49.44 | 10.099 | 50.3 | -0.041 | 2 | 1.542% | -0.53 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.042 | 377 | 212 | 115 | 45.6 | 216.4 | 219.8 | 3.4 | -0.47 | 3.886 | 2.774 | 1.401 | 7.77% | 220.8 | -0.7 | 5.071 | 2.661 | 4.4 | -0.041 | 1.906 | 5.861% | -3.44 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.042 | 636 | 485 | 45 | 103.7 | 487.3 | 499.5 | 12.2 | -0.53 | 12.659 | 6.258 | 2 | 3.652% | 499 | -0.7 | 12.434 | 6.002 | 11.7 | -0.041 | 2 | 3.717% | -2.91 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | NG | FOSS | -0.042 | 103 | 12 | 0 | 90.1 | 12.9 | 14.2 | 1.3 | -0.27 | 1.557 | 1.444 | 1.078 | 5.568% | 14.1 | -0.4 | 1.651 | 1.388 | 1.2 | -0.041 | 1.19 | 5.889% | -0.73 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.042 | 269 | 163.2 | 0 | 104.8 | 164.2 | 171.5 | 7.3 | 0.15 | 7.222 | 2.849 | 2 | 2.583% | 173.5 | 0.2 | 9.13 | 2.732 | 9.3 | -0.041 | 2 | 1.98% | -1.23 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | SUB | FOSS | -0.042 | 592.6 | 155.4 | 0 | 342.2 | 250.4 | 257.9 | 7.5 | -1.4 | 8.867 | 6.173 | 1.436 | 5.535% | 256.9 | -1.9 | 8.37 | 5.931 | 6.5 | -0.041 | 1.411 | 6.234% | -2.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.042 | 592.6 | 155.4 | 0 | 342.2 | 250.4 | 257.9 | 7.5 | -1.4 | 8.867 | 6.173 | 1.436 | 5.535% | 256.9 | -1.9 | 8.37 | 5.931 | 6.5 | -0.041 | 1.411 | 6.234% | -2.69 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.042 | 597.2 | 155.3 | 0 | 296.7 | 300.5 | 303.5 | 3 | -0.71 | 3.717 | 6.477 | 0.574 | 13.94% | 303.1 | -1 | 3.592 | 6.223 | 2.6 | -0.041 | 0.577 | 15.71% | -8.08 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.042 | 597.2 | 155.3 | 0 | 296.7 | 300.5 | 303.5 | 3 | -0.71 | 3.717 | 6.477 | 0.574 | 13.94% | 303.1 | -1 | 3.592 | 6.223 | 2.6 | -0.041 | 0.577 | 15.71% | -8.08 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.042 | 436 | 179 | 0 | 188.6 | 247.4 | 256.5 | 9.1 | -2.82 | 11.929 | 5.545 | 2 | 3.357% | 256.1 | -3.9 | 12.608 | 5.327 | 8.7 | -0.041 | 2 | 3.428% | -1.99 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.042 | 238 | 150 | 10 | 54.3 | 173.7 | 178.2 | 4.5 | 2.54 | 1.964 | 2.414 | 0.813 | 3.709% | 178.7 | 3.5 | 1.427 | 2.315 | 5 | -0.041 | 0.616 | 3.258% | -2.43 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.042 | 235 | 150 | 10 | 51.2 | 173.8 | 178.7 | 4.9 | 2.18 | 2.734 | 2.383 | 1.147 | 3.363% | 179 | 3 | 2.148 | 2.285 | 5.2 | -0.041 | 0.94 | 3.094% | -2.33 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.042 | 928.7 | 461 | 141 | 183.5 | 604.2 | 624 | 19.8 | 2.67 | 17.151 | 8.342 | 2 | 3.285% | 625 | 3.7 | 17.072 | 7.999 | 20.8 | -0.041 | 2 | 3.052% | -2.03 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.042 | 921.8 | 461 | 141 | 205.4 | 575.4 | 596.2 | 20.8 | 2.08 | 18.655 | 8.269 | 2 | 3.104% | 595.9 | 2.9 | 17.562 | 7.93 | 20.5 | -0.041 | 2 | 3.074% | -1.96 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.042 | 292.9 | 150 | 39.9 | 77.3 | 175.7 | 176.3 | 0.6 | -0.6 | 1.167 | 2.679 | 0.436 | 34.22% | 178.8 | -0.8 | 3.87 | 2.569 | 3.1 | -0.041 | 1.506 | 6.466% | -3.96 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.042 | 509 | 327 | 48 | 133.5 | 327.5 | 337.8 | 10.3 | -0.06 | 10.279 | 4.882 | 2 | 3.462% | 335.5 | -0.1 | 8.039 | 4.682 | 8 | -0.041 | 1.717 | 4.351% | -2.86 | 0.017 | 0.0578 | 5.933% | 5.163%
Hydro | NA | HYDR | -0.042 | 9.9 | 0 | 0 | 5.9 | 4 | 9.9 | 5.9 | 0 | 5.941 | 0.14 | 2 | 0.1223% | 9.9 | 0 | 5.941 | 0.135 | 5.9 | -0.041 | 2 | 0.1195% | -0.04 | 0.017 | 0.05 | 0.2285% | 0.2528%
CombinedCycle | CC | COGN | -0.042 | 170.5 | 0 | 40 | 120.4 | 10.1 | 14.8 | 4.7 | 1.13 | 3.556 | 1.382 | 2 | 2.545% | 15 | 1.6 | 3.368 | 1.325 | 4.9 | -0.041 | 2 | 2.384% | -0.14 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.042 | 617.1 | 275 | 125 | 214.1 | 278 | 279.1 | 1.1 | -1.18 | 2.305 | 5.211 | 0.442 | 39.3% | 287 | -1.6 | 10.642 | 4.997 | 9 | -0.041 | 2 | 4.689% | -2.16 | 0.017 | 0.0578 | 5.933% | 5.163%
CombinedCycle | CC | COGN | -0.042 | 617.4 | 275 | 125 | 214.4 | 278 | 279.5 | 1.5 | -1.18 | 2.68 | 5.215 | 0.514 | 28.83% | 286 | -1.6 | 9.642 | 5.001 | 8 | -0.041 | 1.928 | 5.277% | -2.43 | 0.017 | 0.0578 | 5.933% | 5.163%
Thermal | LIG | FOSS | -0.042 | 826 | 259 | 0 | 513 | 313 | 331.7 | 18.7 | 0.5 | 18.154 | 7.735 | 2 | 3.093% | 332.5 | 0.7 | 18.792 | 7.431 | 19.5 | -0.041 | 2 | 2.896% | -1.12 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.042 | 450 | 220 | 0 | 133.4 | 316.6 | 326.7 | 10.1 | 0.03 | 10.131 | 6.37 | 1.59 | 3.122% | 325.3 | 0 | 8.704 | 6.12 | 8.7 | -0.041 | 1.422 | 3.538% | -2.54 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.042 | 820 | 310 | 0 | 394 | 426 | 434 | 8 | -0.87 | 8.845 | 11.608 | 0.762 | 7.179% | 432.7 | -1.2 | 7.911 | 11.152 | 6.7 | -0.041 | 0.709 | 8.367% | -4.45 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | LIG | FOSS | -0.042 | 450 | 230 | 0 | 122.3 | 327.7 | 337.2 | 9.5 | -0.02 | 9.52 | 6.37 | 1.495 | 3.319% | 335.3 | 0 | 7.628 | 6.12 | 7.6 | -0.041 | 1.246 | 4.05% | -3.01 | 0.017 | 0.05 | 6.284% | 5.784%
Hydro | NA | HYDR | -0.042 | 34 | 0 | 0 | 28.7 | 5.3 | 12.7 | 7.4 | -0.01 | 7.382 | 0.481 | 2 | 0.3255% | 13.3 | 0 | 8.005 | 0.462 | 8 | -0.041 | 2 | 0.294% | -0.04 | 0.017 | 0.05 | 0.2285% | 0.2528%
Thermal | SUB | FOSS | -0.042 | 650 | 189.6 | 0 | 459.7 | 190.3 | 203.5 | 13.2 | -0.96 | 14.134 | 5.204 | 2 | 3.449% | 202.7 | -1.3 | 13.645 | 5 | 12.4 | -0.041 | 2 | 3.584% | -1.07 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.042 | 650 | 189.6 | 0 | 459.7 | 190.3 | 203.5 | 13.2 | -0.96 | 14.134 | 5.204 | 2 | 3.449% | 202.7 | -1.3 | 13.645 | 5 | 12.4 | -0.041 | 2 | 3.584% | -1.07 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.042 | 650 | 189.6 | 0 | 459.7 | 190.3 | 203.5 | 13.2 | -0.96 | 14.134 | 5.204 | 2 | 3.449% | 202.7 | -1.3 | 13.645 | 5 | 12.4 | -0.041 | 2 | 3.584% | -1.07 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.042 | 650 | 189.6 | 0 | 459.7 | 190.3 | 203.5 | 13.2 | -0.96 | 14.134 | 5.204 | 2 | 3.449% | 202.7 | -1.3 | 13.645 | 5 | 12.4 | -0.041 | 2 | 3.584% | -1.07 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.042 | 650 | 189.6 | 0 | 459.7 | 190.3 | 203.5 | 13.2 | -0.96 | 14.134 | 5.204 | 2 | 3.449% | 202.7 | -1.3 | 13.645 | 5 | 12.4 | -0.041 | 2 | 3.584% | -1.07 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.042 | 484.5 | 235 | 0 | 244.7 | 239.8 | 271.2 | 31.4 | 0.77 | 30.618 | 5.131 | 2 | 1.081% | 289.5 | 1.1 | 48.661 | 4.92 | 49.7 | -0.041 | 2 | 0.6667% | -0.34 | 0.017 | 0.0578 | 5.933% | 5.163%
Hydro | NA | HYDR | -0.042 | 9.9 | 0 | 0 | 5.9 | 4 | 9.9 | 5.9 | 0 | 5.93 | 0.14 | 2 | 0.1223% | 9.9 | 0 | 5.93 | 0.135 | 5.9 | -0.041 | 2 | 0.1195% | -0.04 | 0.017 | 0.05 | 0.2285% | 0.2528%
Solar | SUN | PVGR | -0.042 | 98.1 | 0 | 0 | 76.9 | 21.2 | 20.6 | -0.6 | -1.16 | 0.535 | 1.389 | 0.385 | -11.49% | 20.5 | -1.6 | 0.895 | 1.334 | -0.7 | -0.041 | 0.671 | -9.617% | 2.08 | 0.017 | 0.05 | 6.014% | 6.718%
Thermal | SUB | FOSS | -0.042 | 932.6 | 360 | 0 | 528.8 | 403.8 | 417.8 | 14 | -1.54 | 15.585 | 6.341 | 2 | 4.665% | 415.6 | -2.1 | 13.931 | 6.093 | 11.8 | -0.041 | 2 | 5.403% | -2.39 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.042 | 932.6 | 360 | 0 | 528.8 | 403.8 | 417.8 | 14 | -1.54 | 15.585 | 6.341 | 2 | 4.665% | 415.6 | -2.1 | 13.931 | 6.093 | 11.8 | -0.041 | 2 | 5.403% | -2.39 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.042 | 932.6 | 360 | 0 | 528.8 | 403.8 | 417.8 | 14 | -1.54 | 15.585 | 6.341 | 2 | 4.665% | 415.6 | -2.1 | 13.931 | 6.093 | 11.8 | -0.041 | 2 | 5.403% | -2.39 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | SUB | FOSS | -0.042 | 932.6 | 360 | 0 | 528.8 | 403.8 | 417.8 | 14 | -1.54 | 15.585 | 6.341 | 2 | 4.665% | 415.6 | -2.1 | 13.931 | 6.093 | 11.8 | -0.041 | 2 | 5.403% | -2.39 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | NG | COGN | -0.042 | 76 | 60 | 0 | 15.2 | 60.8 | 62.3 | 1.5 | -0.21 | 1.762 | 0.951 | 1.853 | 3.566% | 62.1 | -0.3 | 1.668 | 0.908 | 1.3 | -0.041 | 1.836 | 4.017% | -3.25 | 0.017 | 0.05 | 5.933% | 5.163%
Thermal | BIT | FOSS | -0.042 | 664 | 158 | 0 | 505.4 | 158.6 | 171.1 | 12.5 | -0.75 | 13.255 | 8.796 | 1.507 | 3.721% | 171.1 | -1 | 13.535 | 8.451 | 12.5 | -0.041 | 1.602 | 3.632% | -0.89 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.042 | 551 | 226 | 0 | 322.6 | 228.4 | 238 | 9.6 | 0 | 9.608 | 7 | 1.373 | 4.021% | 236.5 | 0 | 8.091 | 6.726 | 8.1 | -0.041 | 1.203 | 4.652% | -1.97 | 0.017 | 0.05 | 6.284% | 5.784%
Thermal | BIT | FOSS | -0.042 | 608 | 303 | 0 | 304 | 304 | 311.5 | 7.5 | -0.33 | 7.873 | 7.459 | 1.056 | 5.678% | 313.3 | -0.5 | 9.823 | 7.167 | 9.3 | -0.041 | 1.371 | 4.47% | -2.29 | 0.017 | 0.05 | 6.284% | 5.784%
CombinedCycle | CC | COGN | -0.042 | 1129 | 379 | 152 | 557.2 | 419.8 | 441.3 | 21.5 | 1.7 | 19.805 | 10.346 | 1.914 | 3.677% | 441.5 | 2.4 | 19.312 | 9.922 | 21.7 | -0.041 | 1.947 | 3.557% | -1.35 | 0.017 | 0.0578 | 5.933% | 5.163%