## Slide 1
Southern Cross Transmission - Directive 9 - Discuss Frequency Overshoot Study and RRS impacts
ERCOT Staff

## Slide 2: Scenarios Used for Frequency Overshoot Study
Scenario Name | Inertia (GW·s) | Load (GW) | Wind (GW) | Synchronous Gen (GW)
CASE 0 | 130 | 34 | 15.5 | 19
CASE 1 | 130 | 34 | 10 | 24.5
CASE 2 | 130 | 32 | 5 | 27.5
CASE 3 | 130 | 32 | 3.5 | 29
CASE 4 | 120 | 29.9 | 3.5 | 26.9
CASE 5 | 110 | 27.2 | 3.5 | 24.2
Preliminary
Draft

## Slide 3: Frequency Response when Tripping SC DC Tie Export at 2,100 MW
 | Case 0 | Case 1 | Case 2 | Case 3 | Case 4 | Case 5
Highest Frequency Overshoot (Hz) DR=2.0 | 60.38 | 60.47 | 60.51 | 60.53 | 60.60 | 60.70
Highest Frequency Overshoot (Hz) DR=0.0 | 60.42 | 60.54 | 60.60 | 60.62 | 60.73 | 60.89
Preliminary
Draft

## Slide 4: Limit Imposed on SC DC Tie Export
 | 130 GW·s | 120 GW·s | 110 GW·s
Limit on SC DC tie export | 2,000 MW | 1,745 MW | 1,488 MW
Preliminary
Draft

## Slide 5: Simulated RRS Case Study
Case No. | Time | INERTIA (GW·s) | PFR (MW) | LR (MW) |  | LR/PFR Ratio |  | PFR (No LR) (MW) | 
 |  |  |  | w/o SCDCT | w/ SCDCT | w/o SCDCT | w/ SCDCT | w/o SCDCT | w/ SCDCT
*Case1 | 10-Feb-17 01:00:00 | 130 | 1150 | 1900 | 2650 | 2.39 | 2.94 | 5691 | 8941
Case2 | 31-Mar-14 02:00:00 | 140 | 1150 | 1800 | 3250 | 2.17 | 3.29 | 5056 | 11843
Case3 | 21-Mar-14 02:00:00 | 150 | 1150 | 1750 | 2900 | 1.85 | 2.59 | 4388 | 8661
Case4 | 23-Oct-16 00:00:00 | 160 | 1150 | 1700 | 2550 | 1.85 | 2.43 | 4295 | 7347
Case5 | 28-Oct-13 00:00:00 | 180 | 1150 | 1650 | 2375 | 1.71 | 1.98 | 3972 | 5853
Case6 | 24-Nov-16 15:00:00 | 200 | 1150 | 1450 | 2100 | 1.43 | 1.53 | 3224 | 4363
Case7 | 02-Apr-14 10:00:00 | 220 | 1150 | 1500 | 2150 | 1.55 | 1.68 | 3475 | 4762
Case8 | 05-Oct-13 18:00:00 | 260 | 1150 | 1450 | 2150 | 1.10 | 1.17 | 2745 | 3666
Case9 | 28-May-14 18:00:00 | 290 | 1150 | 1300 | 1950 | 1.00 | 1.06 | 2450 | 3217
Case10 | 03-Sep-13 18:00:00 | 359 | 1150 | 1150 | 1800 | 1.00 | 1.12 | 2300 | 3166
Case11 | 07-Aug-13 17:00:00 | 376 | 1150 | 1050 | 1700 | 1.00 | 0.95 | 2085 | 2765
*Case 1 : With RCC increased to 3,375 MW, ERCOT’s critical inertia goes up to around 130 GW*s. As a result, current RRS mix is insufficient to arrest system frequency above 59.4 Hz. Therefore, for the case with 130 GW*s inertia, LRs’ response time are shortened to 15 cycles to improve frequency nadir.
Preliminary
Draft

## Slide 6: Interpolated PFR (No LR) Quantities
*Note: With RCC increased to 3,375 MW, ERCOT’s critical inertia becomes 130 GW·s. As a result, current RRS mix is insufficient to arrest system frequency above 59.4 Hz. Therefore, for the case with 130 GW·s inertia, LRs’ response time are shortened to 15 cycles to improve frequency nadir. PFR quantity related to 130 GW·s is not included for interpolation.
Preliminary
Draft

## Slide 7: Interpolated LR/PFR Equivalency Ratio
*Note: With RCC increased to 3,375 MW, ERCOT’s critical inertia becomes 130 GW·s. As a result, current RRS mix is insufficient to arrest system frequency above 59.4 Hz. Therefore, for the case with 130 GW·s inertia, LRs’ response time are shortened to 15 cycles to improve frequency nadir. PFR quantity related to 130 GW·s is not included for interpolation.
Preliminary
Draft

## Slide 8: Interpolated RRS Quantities
*Note: With RCC increased to 3,375 MW, ERCOT’s critical inertia becomes 130 GW·s. As a result, current RRS mix is insufficient to arrest system frequency above 59.4 Hz. Therefore, for the case with 130 GW·s inertia, LRs’ response time are shortened to 15 cycles to improve frequency nadir. PFR quantity related to 130 GW·s is not included for interpolation.
Preliminary
Draft

## Slide 9: RRS Quantity Increase
2019 Total RRS (w/o SCDCT) | 2019 Total RRS (w/ SCDCT) | Delta
23,716,368 MWh | 28,986,904 MWh | 5,270,536 MWh
Preliminary
Draft

## Slide 10: Questions?