## Slide 1
Key Input Assumptions for 2019 RTP Economic Analysis
Sandeep Borkar

## Slide 2: Agenda
Weather year selection
Panhandle interface limit margin
Miscellaneous updates

## Slide 3: Weather Year Selection

## Slide 4: Weather Year Selection
Weather Scenario | Demand Energy (GWH) | Peak Load (MW) | Coastal Wind Energy (GWh) | ERCOT Wind Energy (GWh) | Coastal Wind Capacity Factor (%) | ERCOT Wind Capacity Factor (%) | Solar Energy (GWh) | Solar Capacity Factor (%)
2011 | 468,692,051 | 87,019 | 8,596 | 76,225 | 37.90% | 39.30% | 851 | 30.20%
2010 | 456,562,020 | 85,497 | 7,995 | 73,255 | 35.30% | 37.90% | 831 | 29.60%
2008 | 447,557,131 | 82,770 | 8,270 | 76,945 | 36.50% | 39.60% | 826 | 29.30%
2014 | 451,844,383 | 82,597 | 8,397 | 75,842 | 37.10% | 39.10% | 780 | 27.70%
2009 | 450,212,289 | 84,525 | 8,105 | 71,952 | 35.90% | 37.10% | 807 | 28.70%
2017 | 447,434,837 | 81,813 | 8,114 | 73,607 | 35.90% | 38.00% | NA | NA
2012 | 450,814,006 | 86,025 | 7,686 | 72,669 | 33.90% | 37.50% | 802 | 28.30%
2013 | 452,402,734 | 84,378 | 7,825 | 71,581 | 34.60% | 36.90% | 782 | 27.70%
2006 | 449,427,739 | 83,502 | 7,506 | 71,480 | 33.20% | 36.90% | 826 | 29.50%
2015 | 452,642,420 | 84,295 | 7,772 | 68,412 | 34.30% | 35.30% | 753 | 26.70%
2003 | 445,994,739 | 85,709 | 7,070 | 67,387 | 31.30% | 34.70% | 827 | 29.60%
2005 | 448,842,796 | 82,531 | 6,964 | 66,411 | 30.80% | 34.30% | 832 | 29.90%
2016 | 448,595,247 | 84,169 | 7,166 | 70,867 | 31.70% | 36.50% | NA | NA
2004 | 441,399,247 | 81,576 | 7,911 | 69,730 | 34.90% | 35.90% | 785 | 28.20%
2007 | 443,880,030 | 81,989 | 7,515 | 66,355 | 33.30% | 34.30% | 806 | 28.60%

## Slide 5: Weather Year Selection (Rank)
Weather Scenario | Demand | Peak | Coastal Wind Energy | ERCOT Wind Energy | Coastal Wind Capacity Factor | ERCOT Wind Capacity Factor | Solar Energy | Solar Capacity Factor | Average
2011 | 1 | 1 | 1 | 2 | 1 | 2 | 1 | 1 | 1.3
2010 | 2 | 4 | 6 | 5 | 6 | 5 | 3 | 3 | 4.3
2008 | 11 | 10 | 3 | 1 | 3 | 1 | 5 | 6 | 5.0
2014 | 5 | 11 | 2 | 3 | 2 | 3 | 12 | 11 | 6.1
2009 | 7 | 5 | 5 | 7 | 5 | 8 | 7 | 7 | 6.4
2017 | 12 | 14 | 4 | 4 | 4 | 4 | NA | NA | 7.0
2012 | 6 | 2 | 10 | 6 | 10 | 6 | 9 | 9 | 7.3
2013 | 4 | 6 | 8 | 8 | 8 | 9 | 11 | 12 | 8.3
2006 | 8 | 9 | 12 | 9 | 12 | 7 | 6 | 5 | 8.5
2015 | 3 | 7 | 9 | 12 | 9 | 12 | 13 | 13 | 9.8
2003 | 13 | 3 | 14 | 13 | 14 | 13 | 4 | 4 | 9.8
2005 | 9 | 12 | 15 | 14 | 15 | 14 | 2 | 2 | 10.4
2016 | 10 | 8 | 13 | 10 | 13 | 10 | NA | NA | 10.7
2004 | 15 | 15 | 7 | 11 | 7 | 11 | 10 | 10 | 10.8
2007 | 14 | 13 | 11 | 15 | 11 | 15 | 8 | 8 | 11.9

## Slide 6: Weather Years Selection
2013 will be the base year selected for 2019 RTP Economic Analysis
2010 and 2004 will be selected as the two additional weather scenario for Economic transmission planning
Load, Wind and Solar profiles for appropriate years will be used in UPLAN economic transmission planning analysis

## Slide 7: Panhandle Interface Limit Margin

## Slide 8: Background
ERCOT’s Panhandle Interface was established in June 2015
Over the years the interface limit has been based on lower of System Strength or Voltage Stability limits
A 90% margin was used in prior ERCOT planning studies based on operations experience and feedback

## Slide 9: Panhandle Interface – Duration Curve
Chart: Duration curve-Panhandle Interface Flow(2015-present)

## Slide 10: Review of Historical Margins
Chart: Number of Binding SCED intervals
| 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100
2015 | 50 | 0 | 7 | 5 | 0 | 171 | 6 | 10 | 7 | 125 | 156 | 196 | 9 | 39 | 28 | 1
2016 | 144 | 0 | 5 | 2 | 5 | 177 | 16 | 595 | 608 | 439 | 2737 | 160 | 257 | 231 | 0 | 0
2017 | 98 | 0 | 15 | 5 | 12 | 174 | 25 | 124 | 221 | 467 | 12557 | 1635 | 448 | 1316 | 0 | 0
2018 | 27 | 38 | 22 | 2 | 41 | 100 | 23 | 64 | 60 | 939 | 10583 | 846 | 717 | 199 | 0 | 0
Reviewed the historical SCED interval data when the panhandle interface was binding

## Slide 11: Observations
In 2017 and 2018, the Panhandle Limit was being monitored at 95% of the Stability/WSCR limit
There has been a gradual shift towards 95% following more operating experience in the region

## Slide 12: Conclusion
ERCOT will use 95% of the Stability/WSCR as the panhandle interface limit in its 2019 RTP and 2020 LTSA economic planning analyses
Panhandle Interface Limit for 2021 and 2024 will be set at 4,519 MW
Panhandle Interface definition will include 345-kV circuits between
  Tesla to Jim Treece/Riley
  Tesla to Edith Clarke
  Cottonwood to Edith Clarke
  Cottonwood to Dermott
  Ogallala to Abernathy
  White River to Abernathy

## Slide 13: Miscellaneous Updates

## Slide 14: Input Assumptions: Start Cases
Start Cases
  Transmission topology based on 2021 and 2024 Final Reliability Cases from 2018 RTP
  P1 and P7 Contingencies applicable to above start cases
  LPL will be included in North Weather Zone
Temperature-dependent dynamic ratings based on Operations data used where available

## Slide 15: Natural Gas Price Forecast
Chart: Natural Gas Price Forecast
| 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
2018 AEO Ref* | 3.5451 | 4.2171 | 4.8982 | 4.8786 | 4.834 | 4.9685 | 5.2278 | 5.4519 | 5.7411 | 6.0134 | 6.2904 | 6.5598 | 6.7611 | 7.0466 | 7.1952 | 7.229 | 7.3318 | 7.5994
2018 AEO HOG* | 2.9652 | 3.253 | 3.5518 | 3.3611 | 3.2566 | 3.319 | 3.4531 | 3.605 | 3.8015 | 3.9899 | 4.1342 | 4.2345 | 4.2984 | 4.3817 | 4.447 | 4.479 | 4.5213 | 4.5941
Futures 1-15-2019**** | 3.035 | 2.7659 | 2.6653 | 2.6792 | 2.7243
World Bank 2018** | 2.9 | 2.7 | 2.7 | 2.8 | 2.9 | 3 | 3.2 | 3.3 | 3.44 | 3.58 | 3.72 | 3.86 | 4
IMF 2017* | 2.9852 | 2.8053 | 2.7797 | 2.8149 | 2.852
Source | 
* | https://www.eia.gov/ HOG: High Oil and Gas Production Case Ref: Reference Case
** | http://www.worldbank.org/en/research/commodity-markets
*** | https://www.imf.org/external/np/res/commod/index.aspx
**** | https://www.cmegroup.com/trading/energy/natural-gas/natural-gas.html

## Slide 16: Natural Gas Price Assumptions
Natural Gas Price Forecast (Nominal $/MMBtu)
Natural Gas Price forecast for 2019 RTP will be based on the 2018 EIA AEO High Oil and Gas Production case
Year | 2018 AEO HOG (Average) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
2021 | 3.36 | 3.69 | 3.11 | 3.02 | 3.11 | 3.20 | 3.40 | 3.46 | 3.45 | 3.50 | 3.44 | 3.48 | 3.49
2024 | 3.45 | 3.80 | 3.19 | 3.10 | 3.19 | 3.28 | 3.49 | 3.55 | 3.54 | 3.60 | 3.54 | 3.57 | 3.59

## Slide 17: Emission Cost Assumptions
Source: EPA Website
Emission | $/ton
NOx (Seasonal) | 150
NOx (Annual) | 2.75
SO2 | 0.00
CO2 | 0.00

## Slide 18: Questions & Feedback
Contact info:
Sandeep Borkar
sandeep.borkar@ercot.com
512.248.6642
Naga Kota
Naga.Kota@ercot.com
512.248.3173