## Slide 1
Challenges building resources near series capacitors
- An Update to the RPG 11/14/2017 presentation -
ERCOT System Planning
RPG, 1/22/2019

## Slide 2: Recap
On 11/14/2017, ERCOT made a presentation to RPG, warning of challenges connecting near series capacitors.
Around the same time,
  Three SSR events occurred with Valley Wind
  Correcting the issues took over a year and dozens of calls with manufacturers
Since then,
  Several GINR-SSR studies for units locating close to series caps have encountered unanticipated challenges

## Slide 3: Why is it so challenging to connect near series caps?

## Slide 4: Technical Challenges – Connecting Near Series Caps
Compensation level seen by IRR can be >100%
Potential Challenges:
  More SSR risk
  VRT / tripping issues
  “Energy accumulation” and inverter saturation
  Voltage Profile
  Voltage Control
This slide presented 11/14/2017 to RPG

## Slide 5: “Energy Accumulation”
Series capacitor will naturally charge up during a fault
Upon clearing fault, capacitor discharges:
  Creates an unbalanced voltage transient
  May saturate or trip radially connected generation
Inverter controls may saturate
  Results in SSR even though SSR mitigation is installed
  May result in tripping of IRR

## Slide 6: Generation Interconnection Studies

## Slide 7: Studies Become More Complex Near Series Caps
Close to series capacitors, effect of nearby generation is amplified
  May have a study where individually each wind farm is okay but all together show SSR
Valley SSR event highlighted the interaction of neighboring projects
  Not all OEM PSCAD models work well together in simulations  more study time
  Nearby projects create additional sensitivities  more study scenarios
  More time required to set up simulation and more data required

## Slide 8: FIS SSR Study Observation
For generators located close to series caps, not uncommon to identify SSR issues and other issues, including overvoltage.
Extra study time required (weeks~months) for TSPs, developers, and ERCOT to work with manufacturer to address the issues

## Slide 9: Key Takeaways
Close to series capacitors, SSR studies:
  Are more complex
  Take more time to perform
  Often find more than one type of issue
  May show mitigation damping controls are insufficient
  May require controller re-design or extensive R&D by the manufacturer

## Slide 10: References
South Texas SSR Event, presented to ROS http://www.ercot.com/content/wcm/key_documents_lists/139265/10._South_Texas_SSR_ERCOT_ROS_May_2018_rev1.pdf
Challenges Locating Near Series Capacitors, presented to RPG http://www.ercot.com/content/wcm/key_documents_lists/108892/ERCOT_Building_Near_Series_Capacitors.pptx