## Slide 1
PDCWG Report to ROS
Chair: Chad Mulholland, NRG
Vice Chair: Jimmy Jackson, CPS
ROS
February 7th, 2019

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-1 FMEs & IMFR
    2 FME in the month of December
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 1/16/19
  RRS Limits for NPRR863
    NPRR863 changes offer limits for RRS bids (currently the lesser of up to 20% of HSL, or 10 times the unit ramp rate) to be based upon historical RRS performance, this is a first kick-off for technical discussion of how the historical performance is to be defined
    ERCOT proposes that the effective droop of each RRS providing unit be calculated for historical frequency events, and that the droop then be converted to a MW limit value for each generator
  NOGRR Revisions for to Align with NPRR863
    The only noteworthy point from the PDC discussion of this topic is some “muddiness” with regard to responsibility for the performance of FFR resources between the QSE and the RE – ERCOT plans to follow up on this in February (section 2.3.1.2 of the NOGRR draft)
  Southern Cross DC Tie - Preliminary Findings in ERCOT Frequency Overshoot Study/Impacts to RRS
    ERCOT’s Resource Contingency Criteria (RCC) is defined as the largest N-2 contingency by BAL-003, and this value is used in ERCOT’s Ancillary Service Methodology to set RRS requirements
    If SC DC Tie is allowed to import greater than 1,375 MW (STP1 + STP2 = 1,375 MW + 1,375 MW = 2,750 MW ERCOT RCC), then ERCOT RCC will increase accordingly, up to a maximum of 3,375 MW
  Regulation & Frequency Control Reports
  PDCWG Leadership Changes

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There were 2 FMEs in December
  12/23/2018 06:53:15
    Loss of 854 MW
    Interconnection Frequency Response: 1,068 MW/0.1 Hz
    11 of 56 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    10 of 56 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  12/26/2018 09:24:12
    Loss of 491 MW
    Interconnection Frequency Response: 1,274 MW/0.1 Hz
    9 of 45 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    7 of 45 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Interconnection Minimum Frequency Response (IMFR) Performance
IMFR Performance currently 1055.26 MW/0.1Hz
Frequency Response Obligation (FRO): 381 MW/0.1 Hz

## Slide 7: Frequency Control Report
December 2018

## Slide 8: CPS1 Performance

## Slide 9: RMS1 Performance of ERCOT Frequency

## Slide 10: Frequency Profile Analysis

## Slide 11: Time Error Corrections

## Slide 12: ERCOT Total Energy

## Slide 13: ERCOT Total Energy from Wind Generation

## Slide 14: ERCOT % Energy from Wind Generation

## Slide 15
Questions?