## Introduction
TLF = Transmission Loss Factor
SIEL = Settlement Interval ERCOT system Load
SSC = Seasonal Slope Coefficient = (SONLF - SOFFLF)/(SONL - SOFFL)
SIC = Seasonal Intercept Coefficient = [(SOFFLF * SONL) - (SONLF * SOFFL)]/(SONL - SOFFL)
SONLF = Seasonal on-peak percent loss factor
SOFFLF = Seasonal off-peak percent loss factor
SONL = Seasonal on-peak Load value
SOFFL = Seasonal off-peak Load value

## 2019_Transmission_Losses
TRANSMISSION LOSS FACTORS for 2019 as of 11/05/18
Data from Seasonal SSWG Base Cases Updated with updates received by 11/05/18
Transmission Loss is from 60 kV or higher reporting only
NOIE INTERNAL refers to generation, load and losses behind NOIE meters
|  | ERCOT TOTAL |  |  |  | AEN (9) NOIE INTERNAL TOTAL |  |  |  |  | CPS (5) NOIE INTERNAL TOTAL |  |  |  |  | COG (20) NOIE INTERNAL TOTAL |  |  |  |  | GEUS (21) NOIE INTERNAL TOTAL |  |  |  |  | COD (19) NOIE INTERNAL TOTAL |  |  |  |  | BPUB (15) NOIE INTERNAL TOTAL |  |  |  |  | BTU (22) NOIE INTERNAL TOTAL |  |  |  |  | COCS (23) NOIE INTERNAL TOTAL
Case Type | Base Case Name | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV | Total Base Case Loss MW | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen)
Spring On Peak | 2019_SPG1 | 70167.8 | 68094.9 | 1516.37 | 1629.54 | 1642.4 | 2304.9 | 32.2 | 34.7 | 697.2 | 3221.5 | 4277 | 25.81 | 29.7 | 1085.2 | 219.1 | 424 | 3.69 | 3.7 | 208.6 | 61 | 73 | 0.37 | 0.4 | 12.4 | 56.3 | 333.4 | 0.76 | 0.9 | 278 | 104 | 298 | 0.71 | 0.8 | 194.8 | 66.7 | 369.1 | 3.96 | 4 | 306.4 | 0 | 171.3 | 0.26 | 0.3 | 171.6
Spring Off Peak | 2019_SPG2 | 44398.9 | 43426.5 | 892.71 | 953.62 | 1368 | 1318.1 | 12.8 | 14.5 | -35.4 | 1009 | 2309 | 10.3 | 11 | 1311 | 102.8 | 199 | 0.78 | 0.8 | 97 | 24 | 48.1 | 0.13 | 0.1 | 24.2 | 0 | 170 | 0.4 | 0.4 | 170.4 | 104 | 147.3 | 0.23 | 0.3 | 43.6 | 12 | 187 | 1.3 | 1.3 | 176.3 | 0 | 68.2 | 0.06 | 0.1 | 68.3
Summer On Peak | 2019_SUM1 | 85327.9 | 83493.3 | 1651.79 | 1789.34 | 2052 | 2738.1 | 48.66 | 51.4 | 737.5 | 4700.1 | 5120 | 36.75 | 43.8 | 463.7 | 524 | 568 | 6.5 | 6.9 | 50.9 | 109.6 | 110 | 0.71 | 1.2 | 1.6 | 226 | 371.7 | 2.71 | 3.3 | 149 | 104 | 320.7 | 0.8 | 0.9 | 217.6 | 260 | 458.2 | 4.98 | 5.9 | 204.1 | 0 | 207.6 | 0.25 | 0.3 | 207.9
Summer Off Peak | 2019_SUM2 | 53255.3 | 52311.2 | 844.26 | 925.14 | 1399.2 | 1636 | 17.27 | 19 | 255.8 | 1821.5 | 2765 | 11.17 | 12.2 | 955.7 | 113.7 | 212 | 1.29 | 1.3 | 99.6 | 61 | 65.9 | 0.31 | 0.3 | 5.2 | 30 | 189.6 | 0.64 | 0.6 | 160.2 | 46 | 162.9 | 0.24 | 0.3 | 117.2 | 46.2 | 239.3 | 1.45 | 1.4 | 194.5 | 0 | 74.1 | 0.11 | 0.1 | 74.2
Fall On Peak | 2019_FAL1 | 71495.9 | 69932.7 | 1424.86 | 1535.49 | 1646.1 | 2196 | 35.11 | 37.6 | 587.5 | 3213.7 | 4280 | 23.15 | 27 | 1093.3 | 206.1 | 384 | 2.97 | 3 | 180.9 | 61 | 86 | 0.29 | 0.3 | 25.3 | 7.5 | 300.5 | 0.83 | 0.8 | 293.8 | 104 | 292.8 | 0.64 | 0.8 | 189.6 | 23.3 | 432.3 | 5.72 | 5.7 | 414.7 | 0 | 166 | 0.39 | 0.4 | 166.4
Fall Off Peak | 2019_FAL2 | 45523.5 | 44413.5 | 1026.03 | 1090.47 | 968 | 1403 | 10.23 | 10.9 | 445.9 | 1026 | 2354 | 8.28 | 9 | 1337 | 104.9 | 195 | 0.54 | 0.5 | 90.6 | 24 | 47 | 0.07 | 0.2 | 23.2 | 0 | 153.2 | 0.6 | 0.6 | 153.8 | 42 | 137.5 | 0.21 | 0.3 | 95.8 | 12 | 221.2 | 1.78 | 1.8 | 211 | 0 | 74.1 | 0.07 | 0.1 | 74.2
Winter On Peak | 2020_WIN1 | 72916.5 | 71326.9 | 1440.94 | 1569.33 | 1654.1 | 1933 | 31.22 | 33.8 | 312.7 | 3878.4 | 4179 | 27.21 | 32.7 | 333.3 | 265 | 513 | 4.07 | 4.1 | 252.1 | 0 | 90.9 | 0.15 | 0.1 | 91 | 56.5 | 255.1 | 0.74 | 0.9 | 199.5 | 68 | 285.8 | 0.77 | 0.9 | 218.7 | 251 | 353.2 | 3.46 | 4.1 | 106.3 | 0 | 149.2 | 0.11 | 0.1 | 149.3
Winter Off Peak | 2020_WIN2 | 53930.3 | 52925.3 | 900.45 | 989.33 | 1100.1 | 1359 | 20.85 | 22.1 | 281 | 1091.6 | 2716 | 11.01 | 11.7 | 1636.1 | 125 | 242 | 1.73 | 1.7 | 118.7 | 0 | 71.1 | 0.09 | 0.1 | 71.2 | 46.9 | 130.1 | 0.63 | 0.7 | 83.9 | 28 | 190.2 | 0.39 | 0.5 | 162.7 | 12 | 241.8 | 1.95 | 2 | 231.8 | 0 | 83 | 0.18 | 0.2 | 83.2
Self Serve Load Modeled in Base Cases that does not contribute to transmission losses. | [8 empty] | NOIE TOTALS
Case Type | Base Case Name | CNP Self Serve MW | AEP Self Serve MW | TNMP Self Serve MW | BTU Self Serve MW | ONCOR Self Serve MW | AEP DC Ties Model MW | TOTAL |  | NOIE LOAD MW | NOIE External Resources MW | NOIE Load Served from Internal Resources MW | NOIE TOTAL Loss Above 60 kV | Base Case Name
Spring On Peak | 2019_SPG1 | 2798.65 | 936.67 | 570.3 | 42.96 | 113 | 0 | 4461.58 |  | 8250.7 | 2954.2 | 5296.5 | 67.76 | 2019_SPG1
Spring Off Peak | 2019_SPG2 | 2798.65 | 936.67 | 499 | 0 | 113 | 0 | 4347.32 |  | 4446.7 | 1855.4 | 2591.3 | 26 | 2019_SPG2
Summer On Peak | 2019_SUM1 | 2793.65 | 1295.15 | 570.3 | 43 | 113 | 0 | 4815.1 |  | 9894.3 | 2032.3 | 7862 | 101.36 | 2019_SUM1
Summer Off Peak | 2019_SUM2 | 2793.65 | 936.67 | 513.3 | 10.19 | 113 | 0 | 4366.81 |  | 5344.8 | 1862.4 | 3482.4 | 32.48 | 2019_SUM2
Fall On Peak | 2019_FAL1 | 2797.65 | 936.67 | 570.3 | 23.22 | 113 | 0 | 4440.84 |  | 8137.6 | 2951.5 | 5186.1 | 69.1 | 2019_FAL1
Fall Off Peak | 2019_FAL2 | 2797.65 | 936.67 | 495 | 0 | 113 | 0 | 4342.32 |  | 4585 | 2431.5 | 2153.5 | 21.78 | 2019_FAL2
Winter On Peak | 2020_WIN1 | 2838.65 | 974.25 | 570.3 | 43 | 113 | 0 | 4539.2 |  | 7759.2 | 1662.9 | 6096.3 | 67.73 | 2020_WIN1
Winter Off Peak | 2020_WIN2 | 2838.65 | 897.77 | 457.3 | 0 | 113 | 0 | 4306.72 |  | 5033.2 | 2668.6 | 2364.6 | 36.83 | 2020_WIN2
SEASON | ERCOT WITH SELF SERVE LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF
SPRING | 65706.22 | 40051.58 | 2.308% | 2.229% |  | 2304.9 | 1318.1 | 1.378% | 0.9618% |  | 4277 | 2309 | 0.5998% | 0.4441% |  | 424 | 199 | 0.8628% | 0.3904% |  | 73 | 48.1 | 0.5043% | 0.2695% |  | 333.4 | 170 | 0.2274% | 0.2347% |  | 298 | 147.3 | 0.2377% | 0.1559% |  | 369.1 | 187 | 1.061% | 0.6904% |  | 171.3 | 68.2 | 0.1516% | 0.0879%
SUMMER | 80512.8 | 48888.49 | 2.052% | 1.727% |  | 2738.1 | 1636 | 1.746% | 1.045% |  | 5120 | 2765 | 0.7127% | 0.4024% |  | 568 | 212 | 1.131% | 0.6048% |  | 110 | 65.9 | 0.6413% | 0.4682% |  | 371.7 | 189.6 | 0.7238% | 0.3364% |  | 320.7 | 162.9 | 0.2488% | 0.1471% |  | 458.2 | 239.3 | 1.075% | 0.6023% |  | 207.6 | 74.1 | 0.1203% | 0.1482%
FALL | 67055.06 | 41181.18 | 2.125% | 2.492% |  | 2196 | 1403 | 1.574% | 0.7239% |  | 4280 | 2354 | 0.538% | 0.3505% |  | 384 | 195 | 0.7675% | 0.2762% |  | 86 | 47 | 0.3361% | 0.1487% |  | 300.5 | 153.2 | 0.2754% | 0.3901% |  | 292.8 | 137.5 | 0.2181% | 0.1525% |  | 432.3 | 221.2 | 1.306% | 0.7983% |  | 166 | 74.1 | 0.2344% | 0.09438%
WINTER | 68377.3 | 49623.58 | 2.107% | 1.815% |  | 1933 | 1359 | 1.589% | 1.511% |  | 4179 | 2716 | 0.6469% | 0.4037% |  | 513 | 242 | 0.7871% | 0.7098% |  | 90.9 | 71.1 | 0.1647% | 0.1264% |  | 255.1 | 130.1 | 0.2892% | 0.4819% |  | 285.8 | 190.2 | 0.2687% | 0.2046% |  | 353.2 | 241.8 | 0.9701% | 0.8% |  | 149.2 | 83 | 0.07367% | 0.2164%
TRANSMISSION LOSS FACTORS FOR INSTALLATION IN ERCOT SYSTEMS IN RED BOXES
SEASON | ERCOT WITH SELF SERVE, MODEL & NOIE INTERNAL LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC
SPRING | 3.0755e-06 | 2.1057 |  |  |  | 0.00042159 | 0.40606 |  |  |  | 7.9137e-05 | 0.26137 |  |  |  | 0.0020993 | -0.027333 |  |  |  | 0.0094278 | -0.18393 |  |  |  | -4.4711e-05 | 0.24234 |  |  |  | 0.00054272 | 0.075958 |  |  |  | 0.0020379 | 0.3093 |  |  |  | 0.00061737 | 0.045794
SUMMER | 1.0267e-05 | 1.225 |  |  |  | 0.00063653 | 0.003237 |  |  |  | 0.00013176 | 0.038024 |  |  |  | 0.0014792 | 0.29121 |  |  |  | 0.0039253 | 0.20953 |  |  |  | 0.0021273 | -0.066926 |  |  |  | 0.00064462 | 0.042105 |  |  |  | 0.0021603 | 0.085323 |  |  |  | -0.00020936 | 0.16374
FALL | -1.4168e-05 | 3.075 |  |  |  | 0.0010716 | -0.77959 |  |  |  | 9.7336e-05 | 0.12138 |  |  |  | 0.0025997 | -0.23078 |  |  |  | 0.0048041 | -0.07708 |  |  |  | -0.00077849 | 0.50938 |  |  |  | 0.00042246 | 0.094406 |  |  |  | 0.0024045 | 0.26639 |  |  |  | 0.0015235 | -0.018515
WINTER | 1.5612e-05 | 1.0399 |  |  |  | 0.00013659 | 1.3254 |  |  |  | 0.00016621 | -0.047681 |  |  |  | 0.00028533 | 0.64075 |  |  |  | 0.0019355 | -0.01119 |  |  |  | -0.0015413 | 0.68244 |  |  |  | 0.00067016 | 0.077163 |  |  |  | 0.001527 | 0.43076 |  |  |  | -0.002156 | 0.39534
EFFECTIVE DATES | SEASON
03/01/2019 - 05/31/2019 | SPRING
06/01/2019 - 09/30/2019 | SUMMER
10/01/2019 - 11/30/2019 | FALL
12/01/2019 - 02/29/2020 | WINTER