## Slide 1: System Protection Working Group (SPWG) Update to ROS
February, 2019
Genardo T. Corpuz, P.E.

## Slide 2: SPWG Meeting
No meeting in January 2019
Next meeting will be held March 5-6, 2019
2019 SPWG Chair:
  Micheal A. Davis, Jr, P.E.
  CenterPoint Energy | Supervising Engineer | Transmission Planning - System Modeling
2019 SPWG Vice-Chair: ?

## Slide 3: Transmission Operator Protection System Misoperations 2018 Q3
ERCOT Protection System Misoperations Data – 138kV and 345kV Combined

## Slide 5: Protection System Misoperations 2018 Q3
 |  | Q3 | YTD
# of Misoperations | Total | 40 | 136
 | 345 kV | 13 | 45
 | 138 kV | 25 | 87
 | < 100 kV | 2 | 4
By Category | Failure to Trip | 0 | 4
 | Slow Trip | 0 | 4
 | Unnecessary Trip during Fault | 21 | 71
 | Unnecessary Trip – Non Fault | 19 | 56
 | SPS | 0 | 0
By Relay System Type | Electromechanical | 4 | 14
 | Solid State | 2 | 5
 | Microprocessor | 29 | 100
 | Other/ N/A | 5 | 17
By Equipment Protected | Line | 20 | 62
 | Transformer | 8 | 23
 | Generator | 2 | 11
 | Shunt/Series Capacitor | 2 | 2
 | Shunt/Series Reactor | 1 | 6
 | Dynamic VAR system | 0 | 0
 | Bus | 2 | 6
 | Breaker | 5 | 25

## Slide 6: Protection System Misoperations 2018 Q3

## Slide 7: Protection System Misoperations 2018 Q3

## Slide 8: Protection System Misoperations 2018 Q3

## Slide 9: Protection System Misoperations 2018 Q3

## Slide 10: Protection System Misoperations 2018 Q3

## Slide 11: Protection System Misoperations 2018 Q3
Human Performance Issues
  138kV line overtripped during a fault. A mistake was identified with the panel wiring drawing from a recent panel upgrade project.
  138kV line overtripped during a fault due to the carrier communication switch being left in the “OFF” position.
  Two 138kV lines overtripped during a fault due to incorrect calculation of settings. It was found that the lines were modeled incorrectly during the development of the settings.

## Slide 12: ERCOT SPWG Procedure Revision
6. Reporting of Protective Relay System Misoperations
  Reporting of protective relay system misoperations shall be submitted per Regional Entity procedures NERC Section 1600 Data Request and ERCOT Nodal Operating Guide Section 6.
  Protective relay system misoperations shall be reported in the format requested by the Regional Entity. The submitted data shall include all applicable protective relay system misoperations occurring on Resource Systems and at Transmission Facilities 100 kV and above.

## Slide 13: Questions ?