## Slide 1
ERCOT Frequency Control Report
January 2019
ERCOT
Operations Planning
PDCWG | February 13th, 2019

## Slide 2: Summary of January 2019
CPS1: 174.27%
Current CPS1 12-Month Rolling Average: 175.29%
3 BAAL Exceedance
2 hourly CPS1 scores below 100%
BAAL-003 Events have updated through 2018
2018 BAAL-003 FRM Performance: -895.19
2019 RMS1 Statistics
  Mean: 15.16 mHz
  Min: 12.92 mHz
  Max: 18.95 mHz
Energy Statistics
  Total Energy: 29,800,010 MWh
  Wind Energy: 6,434,375 MWh
  Percent Energy from Wind Generation: 21.59%
Minimum System Inertia
  Mean: 195,476
  Max: 273,060 on January 3rd
  Min: 146,802 on January 18th
Notes: Mean: 195,476
Max: 273,060 on January 3rd
Min: 146,802 on January 18th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
January-19 CPS1 (%): 174.27
Notes: Outliers:
1/18/19 00:00 90.8%
Large Expected Generation Deviation and Regulation Up Exhausted from 00:02 – 00:22
1/22/19 7:00 94.9%
Low starting frequency, DC Tie Schedule Change, Load Ramping, and Units in Startup, Regulation Exhausted

## Slide 5: BAAL Exceedances & Violations
There were 3 BAAL exceedances
  January 22, 2019
    Unit Trip at 7:05:06
    Loss of 657 MW
    Less than 59.91 Hz for 3 minutes
Notes: Low starting frequency, DC Tie Schedule Change, Load Ramping, and Units in Startup

## Slide 6: 15-Minute Average CPS1%
January-19 CPS1 (%): 174.27

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 175.29%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes: Mean is 15.16 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 15.16 mHz
Min: 12.92 mHz
Max: 18.95 mHz

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2018 BAL-003 Selected Events

## Slide 19: Op. Year 2018 BAL-003 FRM Performance

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 29,8000,010 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 6,434,264 MWh

## Slide 23: % Energy from Wind Generation
Notes: 21.59%

## Slide 24: ERCOT System Inertia

## Slide 25: Daily Minimum System Inertia
Notes: Minimum Inertia = 128,759 MW*s on 11/3/2018. Need details here.
Previous Minimum was 130,014 MW*s on 10/27/2017. This was also our record wind day.
Data:
Mean: 195,476
Max: 273,060 on January 3rd
Min: 146,802 on January 18th

## Slide 26: Questions?
Thank you!

## Slide 27: Op. Year 2017 BAL-003 Selected Events
Notes: Frequency Bias updated from 764 to 759 in April

## Slide 28: Op. Year 2017 BAL-003 FRM Performance