## Slide 1
NPRR 849 Problem Statements and Solutions
Stephen Solis
OWG Meeting
February 25, 2019

## Slide 2: Purpose
This set of slides is intended to provide a mechanism for coming to a common understanding the list of problems and the source of the feedback, that the latest NPRR 849 version is trying to collectively address.
Identify separate “problem statements” for each of the issues that ERCOT has intended to address with NPRR 849, including issues identified by ERCOT and by Market Participants during the discussion of the NPRR.
This list will be the basis for any future potential breakout of smaller NPRRs to address the problems individually or in smaller groups.
There still could be a separate path to determine if additional language changes could be made to achieve consensus with the current NPRR 849 draft.

## Slide 3: List of Problems and Solutions
Problem (ERCOT): Section 3.15 does not explicitly state the range of voltages within which a Generation Resource must have the required reactive capability.
  ERCOT solution: Clarify applicable range of voltages (ERCOT 9/27/17 NPRR submission).
Problem (NRG): ERCOT’s enforced range of voltages between .95 and 1.05 pu for the full .95 pf is unnecessary/inefficient in some areas (lagging requirements at higher voltages and leading requirements in lower voltages.)
  ERCOT solution: Reduce the range of voltages requirements to .95 to 1.04 for lagging and .98 to 1.05 for leading (ERCOT 9/27/17 NPRR submission).
Problem (ERCOT): Clarifying the range of applicable voltages would raise the question whether a generator can be instructed to provide voltage support outside of the stated range.
  ERCOT solution: Clarify that generator can be required to provide voltage support outside of ranges (ERCOT 9/27/17 NPRR submission).
Problem (ERCOT): Section 3.15 doesn’t clearly define obligation of generators to meet Voltage Set Point and does not explain how this relates to the duty to have 0.95 power factor capability within the defined range.
  ERCOT solution: Introduce language that explicitly requires generators to meet Voltage Set Point, clarifying that this is limited to physical capability of the generator and its dynamic VAr-capable devices; separately state capability requirement (ERCOT 6/21/18 comments).
Problem (ERCOT): Section 3.15 does not explicitly recognize TSP’s authority to instruct an IRR operating below 10% output to operate VAr-capable devices or to disconnect from ERCOT System.
  ERCOT solution: Revise 3.15(c) to clarify this authority (ERCOT 9/18/18 comments).

## Slide 4: List of Problems and Solutions
Problem (NRG, Invenergy): Set point ranges are unnecessarily broad;
  ERCOT solution: Further narrow the range of set points for leading capability to 1.0 to 1.05 per unit (ERCOT 10/25/18 comments).
Problem (Invenergy): Establishing set point ranges may create compliance risk for generators that designed to a narrower range.
  ERCOT solution: Completely re-write section 3.15(3) to require demonstration of capability over a range only during the interconnection study process and to clarify that the real-time capability requirement only applies if instructed to the Voltage Set Point in question (ERCOT 9/18/18 comments).
Problem (NRG, Invenergy): Protocols do not explicitly recognize 2% tolerance band stated in Operating Guide 2.7.3.5.
  ERCOT solution: Specify 2% tolerance band (ERCOT 9/18/18 comments).
Problem (ERCOT): Some generators are not always moving to newly assigned Voltage Set Points when the new Voltage Set Point is within 2% of the current Voltage Set Point.
  ERCOT solution: Require generators to achieve and maintain a voltage that is “as close as practicable” to the Voltage Set Point (ERCOT 10/28/18 comments).

## Slide 5: List of Problems and Solutions
Problem (ERCOT): Provisions in paragraph (3) of 3.15 should be arranged in chronological order to provide maximum clarity (i.e., interconnection study requirement in paragraph (c) should precede real-time operational requirements) (ERCOT 10/28/18 comments)
  ERCOT solution: Relocate interconnection study requirement before real-time operational requirement (ERCOT 10/25/18 comments).
Problem (ERCOT): Language imposing reactive requirements may be difficult to conceptualize, even with additional clarifications.
  ERCOT solution: Provide graphs illustrating requirement (ERCOT 10/25/18 comments).
Problem (OWG/Oncor): Language doesn’t explicitly require generators to provide all reactive capability when the Voltage Set Point is outside the established voltage ranges.
  ERCOT solution: Add new 3.15(3)(a)(iii) that explicitly requires generators to provide all reactive capability when the Voltage Set Point is outside the established voltage ranges (ERCOT 1/22/19 comments).
Problem (Invenergy/ERCOT): Graphs may misrepresent the literal requirement.
  ERCOT solution: remove graphs from NPRR, but provide them in another public location after making further modifications for accuracy (ERCOT 1/22/19 comments).
Problem (ERCOT): Generators that were grandfathered from 0.95 power factor (“rectangle”) reactive requirement are being repowered with modern technology that should be capable of providing 0.95 power factor requirement but are not providing 0.95 power factor.
  ERCOT solution: Language in current draft removes grandfathering for generators that are repowering (ERCOT 1/22/19 comments).

## Slide 6
Questions?