## Slide 1: Energy Emergency Operations

## Slide 2: ERCOT Role & Responsibilities

## Slide 3: Nodal Operating Guide 4.5, Energy Emergency Alerts (EEA)
4.5.1 – General: (1) At times it may be necessary to reduce ERCOT System demand because of a temporary decrease in available electricity supply. The reduction in supply could be caused by emergency outages of generators, transmission equipment, or other critical facilities; by short-term unavailability of fuel or generation; or by requirements or orders of government agencies. To provide an orderly, predetermined procedures for curtailing Demand during such emergencies, ERCOT shall initiate and coordinate the implementation of the Energy Emergency Alert (EEA) in accordance with Protocol Section 6.5.9.4, Energy Emergency Alert.
(2) The goal of the EEA is to provide for maximum possible continuity of service while maintaining the integrity of the ERCOT System to reduce the chance of cascading outages.

## Slide 4: Nodal Protocol 6.5.9, Emergency Operations
NP 6.5.9.3(2) – Communication under Emergency Conditions The type of communication ERCOT issues is determined primarily on the basis of the time available for the market to respond before an Emergency Condition occurs. The timing of these communications could range from days in advance to immediate. If there is insufficient time to allow the market to react, ERCOT may bypass one or more of the communication steps.
  Operating Condition Notice (OCN) [NP 6.5.9.3.1]
  Advisory [NP 6.5.9.3.2]
  Watch [NP 6.5.9.3.3]
  Emergency Notice [NP 6.5.9.3.4]

## Slide 5
ERCOT Energy Emergency Alert Communications
Emergency Levels* | Trigger | Grid Operators' Actions | Automated Emergency Notifications | Follow-up Communications from External Affairs | Media/Public Notifications
Normal Conditions | Reserves >3,000 MW | Normal operations |  |  | 
Control Room Operating Condition Notice (OCN) | Projected need for additional resources | Issue "OCN" to utilities — informational only | Public Utility Commission of Texas (PUC) and NERC regional entity (Texas Reliability Entity (Texas RE)) notified via daily emails |  | 
Conservation Alert | Used rarely, as needed, to encourage conservation when tight operating reserves are expected to be a reliability concern | Monitor need for additional generation and voluntary demand response resources | None – conservation messages entered and deployed manually in non-emergency situations | Coordinate public notification with PUC staff; notify media and market participants’ media contacts/PIOs of change in conditions | Spotlight on home page of ercot.com and mobile app; social media posts; app messages and/or news release
Control Room Advisory | Reserves <3,000 MW | Issue "Advisory" to utilities — informational only | PUC and Texas RE notified via daily emails; operations notices at control room discretion |  | 
Control Room Watch | Reserves <2,500 MW | Use quick-start capacity and release non-spinning reserves (available within 30 minutes) | Automated Emergency Notification System phone call and email to PUC staff, the Independent Market Monitor (IMM), Texas RE and FERC; operations notice at control room discretion | If potential emergency situation, additional information sent to SOC, PUC, OPUC, RRC, TCEQ, ERCOT Board, Government/Legislature, IMM, Texas RE, FERC and market participants' media contacts/PIOs | Consider conservation alert to support grid reliability
Energy Emergency Level 1 POWER WATCH - Conservation Needed | Reserves <2,300 MW and not expected to be recovered within 30 minutes | Use additional capacity available from other grids (via DC Ties; 500 MW on average) and commit all available units; implement weather-sensitive and 30-minute Emergency Response Service (ERS)** resources and TDSP Load Management programs if needed. Deploy Responsive Reserves if PRC <2000. | Above plus State Operations Center (SOC) (notifies city, county officials & law enforcement), Office of Public Utility Counsel (OPUC), Government/Legislature staff and ERCOT Board; media contacts for utilities | If needed, notify grid emergency lists with additional information | Emergency Alerts list***, Twitter and Facebook, mobile app alerts; spotlight on ercot.com and mobile app; news release if appropriate
Energy Emergency Level 2 POWER WARNING A- Conservation Critical | Frequency cannot be maintained above 59.91 Hz or Physical Responsive Capability (PRC) <1,750 MW and not expected to be recovered within 30 minutes | Deploy demand response resources: Load Resources under contract (typically ~1,150 MW) and/or remaining ERS** (currently 1,123 MW on peak), in either order. Begin block load transfers of load to other grids if appropriate. | Above, plus major news services | Same as above | Same as above
Energy Emergency Level 3 POWER WARNING B - High Risk of Rotating Outages | Frequency cannot be maintained above 59.91 Hz or PRC cannot be maintained >1,375 MW | Ensure all resources allowed under EEA 2 are deployed | Same as above | Same as above | Same as above
Energy Emergency Level 3 POWER EMERGENCY - Rotating Outages in Progress | Frequency cannot be maintained above 59.91 Hz or PRC <1,000 MW and not expected to be recovered within 30 minutes | Instruct transmission operators to implement rotating outages; areas affected are at the discretion of the utilities | Same as above | Same as above | Emergency Alerts list, Twitter and Facebook, mobile app alerts; spotlight on ercot.com and mobile app; issue news release; activate call center if needed
*Depending on system conditions overall, ERCOT Operations has some discretion regarding emergency levels and specific actions, based on these guidelines.
**Emergency Response Service (ERS) may include 10-minute, 30-minute and Weather-Sensitive Demand Response resources.
***Sign up for Emergency Alerts and News Bulletins email lists at http://lists.ercot.com

## Slide 6: Nodal Protocol 6.5.9.3.4, Emergency Notice
(2) ERCOT shall issue an Emergency Notice for one or both of the following reasons:
  ERCOT cannot maintain minimum reliability standards (for reasons including fuel shortages) during the Operating Period using every Resource practicably obtainable from the market; or
  Immediate action cannot be taken to avoid or relieve a Transmission Element operating above its Emergency Rating.
(3) The actions ERCOT takes during an Emergency Condition depend on the nature and severity of the situation.
(5) If the Emergency Condition is the result of a transmission problem, ERCOT shall act immediately to return the ERCOT System to a reliable condition, including instructing Resources to change output, curtailing any remaining DC Tie Load, and instructing TSPs or DSPs to drop Load.

## Slide 7: TDSP/DSP Role & Responsibilities

## Slide 8
ERCOT will declare EEA levels according to available Physical Responsive Capability (PRC) MW reserves, and will take the steps outlined in NOG 4.5.3.3, EEA Levels, to maintain steady state system frequency near 60 Hz and restore PRC appropriate for each EEA level.
When the TDSP/DSP receives Energy Emergency Alert (EEA) Load Shedding instructions from ERCOT, the TDSP/DSP’s responsibility is to perform all necessary actions as prescribed in the ERCOT Nodal Operating Guides (NOG) Section 4, Emergency Operations within the timelines as specified throughout this section.
Section 4: Emergency Operation

## Slide 9: Example: Timing of ERCOT Instructions to TDSPs
Initial Instructions:
ERCOT will instruct TDSP/DSPs to shed X MWs on the Distribution System within 30 minutes.
Follow-up Instructions:
After completing the initial 30 minute instruction, ERCOT operator may continue with further instructions if the PRC has not been restored.
Follow up instructions can range from ten (10) to thirty (30) minute durations with specific instructions for TDSP/DSPs to continue load shedding procedures until ERCOT declares the EEA event has been terminated (see slide 11-12)
Note: TDSPs rotate outages on the Distribution system only. The Transmission system is not subject to rotating outages.

## Slide 10: Nodal Operating Guide 4.5.3.4, Load Shed Obligation
Transmission Operator | 2017 Total Transmission Operator Load (%MW)
AEP Texas Central Company | 8.67
Brazos Electric Power Cooperative Inc. | 4.98
Brownsville Public Utilities Board | 0.37
Bryan Texas Utilities | 0.52
CenterPoint Energy Houston Electric LLC | 25.19
City of Austin DBA Austin Energy | 3.73
City of College Station | 0.29
City of Garland | 0.85
CPS Energy (San Antonio) | 6.8
Denton Municipal Electric | 0.50
GEUS (Greenville) | 0.16
LCRA Transmission Services Corporation | 5.82
Oncor Electric Delivery Company LLC | 36.2
Rayburn Country Electric Cooperative Inc. (DBA Rayburn Electric) | 1.11
South Texas Electric Cooperative Inc. | 2.35
Texas-New Mexico Power Company | 2.46
ERCOT Total | 100.00

## Slide 11: EEA Termination

## Slide 12: Nodal Operating Guide 4.5.3.5, EEA Termination
  (1) ERCOT shall:
    (a) Continue EEA until sufficient Resources are available to ERCOT to eliminate the shortfall and restore adequate reserves;
    (b) Restore full reserve requirements (normally 2300 MW);
    (c) Terminate the levels in reverse order, where practical;
    (d) Notify each QSE and TO of EEA level termination; and
    (e) Maintain a stable ERCOT System frequency when restoring Load.
  (2) QSEs and TOs shall:
    (a) Implement actions to terminate previous actions as EEA levels are released in accordance with these Operating Guides;
    (b) Notify represented Market Participants of EEA levels changes;
    (c) Report back to the ERCOT System Operator when each level is accomplished; and
    (d) Loads will be restored when specifically authorized by the ERCOT.

## Slide 13: Additional ERCOT Communications Information
  May 15th ERCOT Communications Workshop:
  For updated 2019 information related to ERCOT Summer Operations and Communications, please plan to attend the 2019 ERCOT Communications workshop to be held on May 15th at ERCOT METCenter.
  Reference Information:
  Tips for Conservation: http://ercot.com/about/conservation
  ERCOT EEA Communications Matrix: http://www.ercot.com/content/wcm/lists/144929/ERCOT_Energy_Emergency_Alert_Communications_Matrix_May_2018.pdf
  2018 ERCOT Summer Communications Overview:

## Slide 14
  Questions?