## Slide 1
Energy Emergency Alert -
ERCOT Responsibilities
ERCOT Operations
March 4, 2019

## Slide 2: Operating Notices
Notice | Trigger
Operating Condition Notice (OCN) | Issued in anticipation of a possible emergency condition when more resources may be needed
Conservation appeal | May be issued in anticipation of expected emergency conditions
Advisory | Operating Reserves, measured by Physical Responsive Capability (PRC), is less than 3,000 MW and not expected to recover within 30 minutes

## Slide 3: Energy Emergency Alert (EEA) levels
PRC<2,300 MW;
>30 mins
Order all resources online
Request DC-Tie emergency imports
Deploy Emergency Response Service (ERS) 30-minute demand response
Release generation Responsive Reserves
EEA 1
PRC<1,750 MW;
>30 mins
Deploy ERS 10-minute demand response
Deploy Load Resources
Request TDSP Load Management
Request TDSP Voltage Reduction
Issue conservation appeal
EEA 2
EEA 3
PRC<1,375 MW
Implement any measures not already being used
EEA 3
PRC<1,000 MW;
>30 mins
Implement load shed to match generation to load and bring PRC above 1,000 MW

## Slide 4: Load Shed Obligations
Table in Operating Guide 4.5.3.4 gives share of any load shed that each entity is expected to contribute:
Transmission Operator | 2018 Total Transmission Operator Load (%MW)
AEP Texas Central Company | 8.52
Brazos Electric Power Cooperative Inc. | 5.25
Brownsville Public Utilities Board | 0.36
Bryan Texas Utilities | 0.49
CenterPoint Energy Houston Electric LLC | 24.27
City of Austin DBA Austin Energy | 3.6
City of College Station | 0.28
City of Garland | 0.9
CPS Energy (San Antonio) | 6.53
Denton Municipal Electric | 0.50
GEUS (Greenville) | 0.16
LCRA Transmission Services Corporation | 5.74
Oncor Electric Delivery Company LLC | 37.44
Rayburn Country Electric Cooperative Inc. DBA Rayburn Electric | 1.19
South Texas Electric Cooperative Inc. | 2.21
Texas-New Mexico Power Company | 2.56
ERCOT Total | 100.00