## Slide 1: 10. Throw-over schemes for Voltage Transformer (Follow-Up Discussion)
Background: Throw-over VT transfer scheme at an EPS metering facility (which was tied to a blackstart facility) was initiated during switching and blackstart testing
It was discovered that during one of the switching activities, the EPS meters had CTs referenced at the local bus while the VTs referenced at a remote bus (blackstart)

## Slide 2: 10. Throw-over schemes for Voltage Transformer (Follow-Up Discussion)
Result: Some intervals of EPS meter data polled during the switching were corrupted.
Action: ERCOT Meter Engineering to reach out to each TDSP with known voltage-transformer throw-over scheme installed at any of their EPS metering facilities

## Slide 3: 10. Throw-over schemes for Voltage Transformer (Follow-Up Discussion)
A spreadsheet has been generated listing TDSPs with VT throw-over schemes installed at various EPS metering site.
The information on the spreadsheet will not be shared amongst TDSPs

## Slide 4: 10. Throw-over schemes for Voltage Transformer (Follow-Up Discussion)
Objectives - analyze if any of the EPS metering sites with VT throw-over scheme has the potential to experience meter data issues during VT switching-over - Explore the idea of proposing a standard for VT throw-over schemes to be discussed at future MWG meetings

## Slide 5: Throw-over schemes for Voltage Transformer (Follow-Up Discussion)
Any Questions?