## Slide 1
PDCWG Inertia Quarterly Update
Julia Matevosyan
Resource Adequacy
ERCOT
3/13/2019

## Slide 2: Effect of Synchronous Inertia on System Frequency
With increasing integration of inverter-based generation, there could be periods when total inertia of the system could be low since less synchronous machines will be dispatched.
  During such situations, it is essential to have adequate frequency response capabilities
UFLS trigger
Notes: UFLS trigger indicates the frequency (59.3 Hz) at which the first stage of involuntary underfrequency load shedding will happen. ERCOT plans and operates the system such that for the simultaneous trip of two largest generating units (2750 MW), UFLS should not be triggered, though it still can happen in some extreme unexpected situations.

## Slide 3: Inertia Calculation
In 2013, as instantaneous wind power penetration reached 30%, ERCOT started analyzing impacts of inverter-based generation on system inertia.
In 2015, ERCOT implemented a real-time inertia calculation using inertia parameters of each individual synchronous generator and its status (on/off) telemetry.
where I is the set of online synchronous generators or condensers,
MVAi is MVA base of on-line synchronous generator or synchronous condenser i, and
Hi is inertia constant for on-line generator or synchronous condenser i in a system (in seconds on machine MVAi)

## Slide 4: Inertia Monitoring in Real-Time and Forecasting
In 2016, inertia monitoring was implemented in the control room.

## Slide 5: ERCOT Inertia 2013-2019
Date and Time | 2013 3/10/13 3:00 AM | 2014 3/30/14 3:00 AM | 2015 11/25/15 2:00 AM | 2016 4/10/16 2:00 AM | 2017 10/27/17 4:00 AM | 2018 11/03/18 3:30 AM | 2019(Jan-Feb) 2/3/2019 2:00 AM
Min synch. Inertia (GW*s) | 132 | 135 | 152 | 143 | 130 | 128.8 | 139
System load at minimum synch. Inertia (MW) | 24,726 | 24,540 | 27,190 | 27,831 | 28,425 | 28,397 | 29,422
Non-synch. Gen. in % of System Load | 31 | 34 | 42 | 47 | 54 | 53.4 | 45.4
Notes: For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.

## Slide 6: Inertia duration curve

## Slide 7: Inertia by Unit Type during Minimum Inertia Times

## Slide 8: How is inertia information is being used?
RRS requirements are determined in the beginning of the year, for the whole year, based on historic inertia conditions.
ERCOT determines actual RRS needs based on expected inertia conditions in the Day-Ahead and closer to real-time, and monitors RRS sufficiency in the control room.
Inertia is monitored versus Critical Inertia value in real time.

## Slide 9: Critical Inertia
Critical Inertia is the minimum level of inertia at or below which a system cannot be operated reliably with existing frequency control practices.
For ERCOT Critical Inertia is the minimum level of inertia that, after a trip of 2,750 MW, will give Load Resources sufficient time to respond before frequency reaches the UFLS (59.3 Hz).
From a series of dynamic studies Critical Inertia for ERCOT was found and set to 100 GWs (if 2 STP units are online).
Critical Inertia is monitored in the control room and operator may take actions to increase critical inertia above 100 GWs, when needed.
With implementation of NPRR863, FFR response time is faster than that of Load Resources and trigger frequency is higher, Critical inertia can potentially be decreased to 90 GWs (based on dynamic studies)

## Slide 10: “Base” Inertia Analysis
What is the lowest inertia level that ERCOT system can go down to with current operational practices?
Analysis is based on low inertia (<145 GWs) instances for 2013-2018
Determining minimum inertia from components that are online “at all times” due to various operational practices:
Private Use Networks (generation at industrial load sites)
Generators providing RRS (min 1,150 MW of RRS is required from generation, each generator cannot be awarded RRS for more than 20% of its capacity)
Nuclear generation (always online unless on maintenance)

## Slide 11: “Base” Inertia Analysis (2013-2018 data)
Min nuclear units inertia,18 GW·s
Min inertia from AS providers, 45 GW·s
Min inertia Private Use Networks, 32GW·s
95 GW·s of base inertia
Critical inertia 100 GW·s
Additional 5 GW·s of inertia needed

## Slide 12: PUN Inertia
Jan- Feb

## Slide 13: Inertia from AS providers during minimum inertia times
Date of inertia min | Inertia of all units carrying AS | Inertia of non-PUN units carrying AS
11/3/2018 3:00 | 64,303 | 51,719
10/27/17 4:00 | 68,235 | 56,089
4/10/16 2:00 | 56,764 | 52,317
11/25/15 2:00 | 61,321 | 54,291
3/30/14 3:00 | 67,000 | 61,148
3/10/13 3:00 | 53,124 | 42,687

## Slide 14: Next Steps
Quarterly inertia updates to PDCWG (summer update may not be of interest?)
Report on inertia records and inverter-based generation penetration records
Report on PUN and AS-providers inertia
Any other items of interest?