## Slide 1
ERCOT Frequency Control Report
February 2019
ERCOT
Operations Planning
PDCWG | March 13th, 2019

## Slide 2: Summary of February 2019
CPS1: 173.46%
Current CPS1 12-Month Rolling Average: 175.04%
0 BAAL Exceedances
1 hourly CPS1 scores below 100%
BAAL-003 Events have updated through 2018
2018 BAAL-003 FRM Performance: -895.19
2019 RMS1 Statistics
  Mean: 15.42 mHz
  Min: 13.52 mHz
  Max: 17.90 mHz
Energy Statistics
  Total Energy: 26,060,591 MWh
  Wind Energy: 6,174,568 MWh
  Percent Energy from Wind Generation: 23.69%
Minimum System Inertia
  Mean: 177,451
  Max: 243,101 on February 9th
  Min: 138,761 on February 3rd

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
February-19 CPS1 (%): 173.46
Notes: Outliers:
2/5/19 16:00 98.96%
Wind decreased by 2,000 MW throughout the hour. Solar decreased by 200 MW. Large expected generation deviation. DC Tie schedule change. Reg Up exhausted the majority of the hour.

## Slide 5: BAAL Exceedances & Violations
There were no BAAL exceedances in February

## Slide 6: 15-Minute Average CPS1%
February-19 CPS1 (%): 173.46

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 175.04%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes: Mean is 15.28 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 15.42 mHz
Min: 13.52 mHz
Max: 17.90 mHz

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2018 BAL-003 Selected Events

## Slide 19: Op. Year 2018 BAL-003 FRM Performance

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 26,060,591 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 6,174,568 MWh

## Slide 23: % Energy from Wind Generation
Notes: 23.69%

## Slide 24: ERCOT System Inertia

## Slide 25: Daily Minimum System Inertia
Notes: Minimum Inertia = 128,759 MW*s on 11/3/2018.
Previous Minimum was 130,014 MW*s on 10/27/2017. This was also our record wind day.
Data:
Mean: 177,451
Max: 243,101 on February 9th
Min: 138,761 on February 3rd

## Slide 26: Questions?
Thank you!