## Slide 1
2019 ERCOT UFLS Survey Overview and Timeline
Daniel Sanchez
ERCOT Compliance Analyst
March 21, 2019

## Slide 2: Survey Overview and Requirements
ERCOT ISO conducts the UFLS survey annually to ensure that the required automatic under-frequency load shed circuits are configured to provide the appropriate load relief in an under-frequency event.
ERCOT Nodal Operating Guides, 2.6.1 (1), Automatic Firm Load Shedding
In the event of an under-frequency event, each Transmission Operator (TO) shall provide Load relief by shedding the required percentage of its Distribution Service Provider (DSP)-connected Load and transmission-level Customer Load using automatic under-frequency relays, as specified in the table below. The TO Load will be the amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load.
Frequency Threshold | Load Relief
59.3 Hz | At least 5% of the TO Load
58.9 Hz | A total of at least 15% of the TO Load
58.5 Hz | A total of at least 25% of the TO Load

## Slide 3: Survey Overview and Requirements
ERCOT Nodal Operating Guides 2.6.1 (2)
ERCOT will, prior to the peak each year, survey each TO’s compliance with the automatic Load shedding requirements described in paragraph (1) above, and report its findings to the Technical Advisory Committee (TAC). For purposes of determining a TO’s compliance with this annual survey requirement, TO Load will be the total amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, at the specified time of the survey.
The TO shall identify those circuits armed with under-frequency relays, the corresponding amount of Load, and identify the frequency threshold.
A TO shall not equip the entirety of its Load shed obligation in any one tier, and should endeavor to shed in controlled amounts that equal the difference between the TO Load relief required for each tier. If ERCOT identifies potential reliability issues related to distribution of Load shed across the tiers, ERCOT may require the TO to redistribute Load relief closer to the minimum amount required after submitting ERCOT’s proposal to redistribute Load relief to the TO and considering any comments submitted by the TO regarding the proposal.
Compliance with this annual survey does not excuse the TO from compliance with the requirements of paragraph (1) above in an actual frequency event. To assist TOs, ERCOT will provide the TO’s inventory, including substation and capacity amounts, of registered Load Resources in its area within ten Business Days of receiving a request in writing from a TO.

## Slide 4: 2019 UFLS Survey Activity Timeline
Date | Activity
March 21st | Announcement of survey timeline to OWG.
April 2nd | Market Notice sent to TO Authorized Representatives.
May 9th @ 11:00 AM | Date and time of survey.
June 12th | Survey results due to ERCOT.
August – September | Results reported to OWG, ROS, and TAC.