## Slide 1
Review of Commercial Impacts of DC Tie Curtailments
WMWG
March 25, 2019
Market Analysis

## Slide 2: DC Tie Tag Curtailments – January 2019
There was 1 DC tie tag curtailment event
  Due to local congestion
ERCOT posted a DC tie curtailment notice to MIS during this event

## Slide 3: DC Tie Tag Curtailments – January 2019
Date | DC Tie | Curtailing Period | # of Tags Curtailed | Initiating Event | Curtailment Reason
01/25/2019 | DC-S | HE9, HE10 | 1 | SBEVASH8, loss of Asherton to Bevo 138 kV, overloads Hamilton to Maverick 138 kV | Local Congestion
Constraint was not activated in SCED due to no Resources having meaningful shift factors.

## Slide 4: DC-S (Eagle Pass) and Constraint Locations
X
overloaded
element
DC-S
contingency
O

## Slide 5: 1/25/2019 Curtailment of DC-S
Chart: DC Tie Export (MW)
| 43490.333472222221 | 43490.336909722224 | 43490.340405092589 | 43490.343877314815 | 43490.347361111111 | 43490.350821759261 | 43490.35429398148 | 43490.357777777775 | 43490.361238425925 | 43490.364699074074 | 43490.36818287037 | 43490.371655092589 | 43490.375185185185 | 43490.378611111111 | 43490.382071759261 | 43490.38554398148 | 43490.389027777775 | 43490.392488425925 | 43490.395960648151 | 43490.399444444447 | 43490.40289351852 | 43490.406377314815 | 43490.409849537034 | 43490.413321759261 | 43490.416828703703 | 43490.420266203706 | 43490.423738425925 | 43490.427199074074 | 43490.43068287037 | 43490.434155092589 | 43490.437615740739 | 43490.441087962965 | 43490.444571759261 | 43490.44804398148 | 43490.451516203706 | 43490.454976851855 | 43490.458483796298
DC_S Export | 0.5 | 0.5 | 0.5 | 30 | 30 | 30 | 30 | 20.1 | 20.1 | 20.1 | 20.1 | 20.1 | 20.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.2 | 25.2 | 26.4 | 30.1 | 30.1 | 30.1 | 30.1 | 30.1 | 30.2 | 30.2 | 30.1 | 30.2 | 30.2 | 30.2 | 30.2
Export Limit | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
System Lambda | 52.646 | 37.4174 | 35.3819 | 35.8096 | 34.0968 | 32.4292 | 29.9975 | 29.2674 | 29.0445 | 30.8976 | 29.8559 | 31.1445 | 34.3315 | 32.0548 | 30.1383 | 29.0489 | 26.7725 | 27.5164 | 25.8211 | 25.3043 | 24.9759 | 24.7387 | 24.555 | 24.3561 | 24.9164 | 24.872 | 24.3415 | 23.6246 | 23.1455 | 23.5065 | 23.2659 | 23.6771 | 23.5277 | 23.3914 | 23.2099 | 22.9844 | 23.3497
DCTIE_LMP | 39.4423 | 37.5659 | 35.5162 | 35.2644 | 34.1359 | 32.4574 | 30.0086 | 29.2735 | 28.0827 | 29.8825 | 28.8717 | 30.1284 | 33.2341 | 31.0235 | 29.1606 | 28.1021 | 25.8788 | 26.605 | 24.9591 | 24.4612 | 24.1437 | 23.9144 | 24.5909 | 24.3924 | 24.9534 | 24.05 | 24.3216 | 23.6537 | 22.4623 | 22.7754 | 22.5416 | 22.9395 | 22.7944 | 23.3584 | 23.1763 | 22.9512 | 23.3174

## Slide 6: 1/25/2019 LMPs Related to DC-S Curtailment
Chart: Price ($/MWh)
| 43490.333472222221 | 43490.336909722224 | 43490.340405092589 | 43490.343877314815 | 43490.347361111111 | 43490.350821759261 | 43490.35429398148 | 43490.357777777775 | 43490.361238425925 | 43490.364699074074 | 43490.36818287037 | 43490.371655092589 | 43490.375185185185 | 43490.378611111111 | 43490.382071759261 | 43490.38554398148 | 43490.389027777775 | 43490.392488425925 | 43490.395960648151 | 43490.399444444447 | 43490.40289351852 | 43490.406377314815 | 43490.409849537034 | 43490.413321759261 | 43490.416828703703 | 43490.420266203706 | 43490.423738425925 | 43490.427199074074 | 43490.43068287037 | 43490.434155092589 | 43490.437615740739 | 43490.441087962965 | 43490.444571759261 | 43490.44804398148 | 43490.451516203706 | 43490.454976851855 | 43490.458483796298
System Lambda | 52.646 | 37.4174 | 35.3819 | 35.8096 | 34.0968 | 32.4292 | 29.9975 | 29.2674 | 29.0445 | 30.8976 | 29.8559 | 31.1445 | 34.3315 | 32.0548 | 30.1383 | 29.0489 | 26.7725 | 27.5164 | 25.8211 | 25.3043 | 24.9759 | 24.7387 | 24.555 | 24.3561 | 24.9164 | 24.872 | 24.3415 | 23.6246 | 23.1455 | 23.5065 | 23.2659 | 23.6771 | 23.5277 | 23.3914 | 23.2099 | 22.9844 | 23.3497
HB_SOUTH_LMP | 50.3691 | 37.8335 | 35.8274 | 35.8355 | 34.1239 | 32.4485 | 30.0048 | 29.2711 | 28.8648 | 30.7114 | 29.6853 | 30.9923 | 34.1424 | 31.8725 | 29.9608 | 28.8752 | 26.6015 | 27.3434 | 25.6558 | 25.1437 | 24.8172 | 24.5821 | 24.5909 | 24.3924 | 24.9534 | 24.717 | 24.3703 | 23.6537 | 23.0578 | 23.4113 | 23.171 | 23.58 | 23.4311 | 23.4108 | 23.2285 | 23.0035 | 23.3697
LZ_SOUTH_LMP | 49.7962 | 37.8353 | 35.8293 | 37.47 | 34.1244 | 32.4488 | 30.005 | 29.2711 | 28.8212 | 30.6647 | 29.6396 | 30.9444 | 34.0905 | 31.8232 | 29.915 | 28.8309 | 26.5607 | 27.3014 | 25.6165 | 25.1053 | 24.7796 | 24.5448 | 24.5909 | 24.3924 | 24.9534 | 24.681 | 24.3676 | 23.6537 | 23.0259 | 23.3768 | 23.1375 | 23.5462 | 23.3976 | 23.408 | 23.2258 | 23.0008 | 23.3669