## Slide 1: System Protection Working Group (SPWG) Update to ROS
April, 4, 2019
Micheal Davis, Jr, P.E.

## Slide 2: SPWG Meeting
Meeting held on March 5, 2019
2019 SPWG Vice-Chair Nominee:
  John Karlik, P.E.
  Austin Energy | Power System Engineer Sr.| Protection Engineering

## Slide 3: Transmission Operator Protection System Misoperations 2018 Q4
ERCOT Protection System Misoperations Data – 138kV and 345kV Combined

## Slide 5: Protection System Misoperations – 2018 Q4
 |  | Q4 Partial | 2018
# of Misoperations | Total | 28 | 160
 | 345 kV | 10 | 52
 | 138 kV | 16 | 102
 | < 100 kV | 2 | 6
By Category | Failure to Trip | 1 | 5
 | Slow Trip | 0 | 4
 | Unnecessary Trip during Fault | 15 | 85
 | Unnecessary Trip – Non Fault | 12 | 66
 | SPS | 0 | 0
By Relay System Type | Electromechanical | 5 | 19
 | Solid State | 0 | 5
 | Microprocessor | 13 | 107
 | Other/ N/A | 5 | 29
By Equipment Protected | Line | 10 | 72
 | Transformer | 5 | 25
 | Generator | 4 | 12
 | Shunt/Series Capacitor | 2 | 4
 | Shunt/Series Reactor | 0 | 6
 | Dynamic VAR system | 0 | 0
 | Bus | 3 | 8
 | Breaker | 4 | 28

## Slide 6: Protection System Misoperations 2018 Q4

## Slide 7: Protection System Misoperations 2018 Q4

## Slide 8: Protection System Misoperations 2018 Q4

## Slide 9: Protection System Misoperations 2018 Q4

## Slide 10: Protection System Misoperations 2018 Q4

## Slide 11
Manufacturer | Relay Type | # of failures resulting in a misoperation
GE | B30 | 3
GE | B90 | 3
GE | BDD | 2
GE | CFD | 1
GE | D60 | 8
GE | F35 | 2
GE | FANUC PLC | 3
GE | G60 | 2
GE | GCX | 2
GE | ICW | 3
GE | L90 | 9
GE | SAM | 1
GE | SBC | 1
GE | SLY | 1
GE | SPD11 | 2
GE | T60 | 2
Manufacturer | Relay Type | # of failures resulting in a misoperation
SEL | 311 | 4
SEL | 321 | 15
SEL | 351 | 3
SEL | 411 | 3
SEL | 421 | 11
SEL | 451 | 3
SEL | 487 | 2
SEL | 551 | 1
Manufacturer | Relay Type | # of failures resulting in a misoperation
Basler | BE1-50BF | 1
Beckwith | M3425 | 1
Beckwith | M3430 | 1
Electroswitch | Lockout relay | 16
Qualitrol | SPR or Pressure Relief | 4
RFL | RFL9300 | 8
Manufacturer | Relay Type | # of failures resulting in a misoperation
ABB | AR | 1
ABB | HCB-1 | 5
ABB | HU-1 | 2
ABB | IRD-9 | 2
ABB | IRP | 1
ABB | ITH | 1
ABB | KA-4 | 2
ABB | KC | 2
ABB | KD | 7
ABB | KF | 2
ABB | KLF | 1
ABB | KRP | 1
ABB | LCB-II | 10
ABB | MDAR | 1
ABB | REL-512 | 1
ABB | TD | 3
Relay Failures Resulting in a Misoperation
Period: 2012-2018
Notes:
190 misoperations reported from 2012-2018 with Relay Failure/Malfunction as the cause
160 misoperation reports contained sufficient detail on manufacturer and relay type
This data should not be used as an indicator of relay failure rates
Relay Failures by Scheme | 
Step Distance | 4
DCB | 17
POR/POTT | 2
DUTT | 1
Phase Comparison | 1
Line Current Differential | 21
Differential | 22
DTT | 2
Breaker Failure | 4
Other | 6
No data | 110
Relay Failures by Failure Mode | 
Relay - Power Supply Failure/Malfunction | 8
Relay - AC I/O Module Failure/Malfunction | 19
Relay - Digital I/O Module Failure/Malfunction | 11
Relay - Communication Module Failure/Malfunction | 5
Relay - Self-Diagnostic Failure/Malfunction | 3
Relay - CPU Processor Failure/Malfunction | 24
Relay - Incorrect Manufacturer Programming ('Bug') | 3
Relay - Incorrect Manufacturer Design | 1
Relay - Unknown | 15
Relay - Other | 54
No data | 47

## Slide 12
Summary of Human Performance Issues noted for 2018 Q4:
During commissioning and first energization of the cap banks at a wind farm, the cap banks were incorrectly grounded. This caused current flow in the main power transformer, the CT ratio on the low side had been incorrectly changed, and this resulted in the relay incorrectly picking up on differential and issuing a trip. In addition, the time delay on the breaker failure logic had not been correctly implemented.
138kV line overtrip. Field settings did not match engineering settings.
138kV capacitor bank trip. Auxiliary contact field wiring did not match drawing.
138kV bus trip during a remote fault due to an incorrectly connected CT input from an autotransformer to the bus differential.
138kV line overtrip due to incorrect jumper settings in the power line carrier.
Failure to Trip/Slow Trip Misoperations in 2018 Q4:
138kV CCVT failure disabled relay directional elements, by design, resulted in remote clearing of the fault.
Protection System Misoperations 2018 Q4

## Slide 13: ERCOT SPWG Procedure Revision
6.1.2.2 Fault Recording and Sequence of Events Recording Equipment Location Requirements
  (2) Facility owners shall install the fault recording and sequence of events recording equipment identified in paragraphs (1)(a) and (1)(b) above. This installation shall occur such that half of the identified facilities have the associated equipment installed by July 1, 2020, and all of the identified facilities by July 1, 2022.
  (3) Facility owners shall install the fault recording and sequence of events recording equipment identified in paragraph (1)(c) above by July 1, 2019.

## Slide 14: ERCOT SPWG Procedure Revision
6.1.3.2 Location Requirements
(3) Facility owners identified under paragraphs (1) or (2) above shall install dynamic disturbance recording equipment such that half of the identified facilities have the associated equipment installed by July 1, 2020, and all of the identified facilities by July 1, 2022. by July 1, 2019.

## Slide 15: Questions ?