## Slide 1
Discussion on GUC’s Request and Proposal
Market Analysis and Validation
CMWG
April 1st, 2019

## Slide 2: Constraint SWCSBOO8:BARL_FTSW1_1
The constraint SWCSBOO8:BARL_FTSW1_1 was originally identified as irresolvable constraint on Jan.30, 2017, and its max shadow price was set as $2,000.
On Sept. 23, 2017, the Net Margin for this irresolvable constraint reached $95,000. This triggered another calculation of max shadow price, which was again set as $2,000.
At the end of year 2017, this constraint was reviewed and kept as irresolvable, and its max shadow price was recalculated as $2,800.
Again, at the end of year 2018, this constraint was kept as irresolvable and the max shadow price was recalculated as $2,800.

## Slide 3: ERCOT actions for SWCSBOO8:BARL_FTSW1_1 when its net margin exceeding $95,000/MW (9/2017)
Outage: The direct cause of high congestion was a local outage which ended on 9/25/2017. Other outages in the area were also reviewed, which were all due to new construction and could not be recalled.
CMP: RAP was not applicable as the line had the same emergency and load shed rating. CMPs had been developed and in use since the congestion began in 2017.
Transmission Project: Transmissions project had been identified that might reduce the congestion.

## Slide 4: Congestion in Far West
Since 2017, high congestion has been observed on multiple constraints in Far West.
The high congestion in the area was mostly due to the load increase in Far West, while the transmission outages to upgrade existing transmission facilities and the increase of local renewable output also play some role in the congestion.
Multiple transmission projects are on-going or has been planned to improve the transmission network around the area.
CMPs are being used to facilitate Outages in the area.

## Slide 5: Current transmission improvement projects
Project Number | Project Title | Project Description | Projected In-Service Date
45503 | Lynx: Expand 138 kV station | Terminate the TNMP 16th Street to Rio Pecos 138 kV line into Lynx station | May-20
44359 | Solstice: Install 138 kV PST and capacitor bank | Install PST on the Fort Stockton Plant to Solstice 138 kV line at Solstice | Mar-20
44361 | Ft. Stockton SW: Build 138 kV station | Rebuild Barrilla Junction to Ft. Stockton SW to Rio Pecos 69 kV line, convert to 138 kV, reterminate into Solstice, install 138 kV capacitor bank at Solstice, and build new Ft. Stockton Switch 138 kV station | Mar-20
7027 | Barrilla Junction to Ft. Stockton SW: Rebuild 69 kV line | Rebuild Barrilla Junction to Ft. Stockton SW to Rio Pecos 69 kV line, convert to 138 kV, reterminate into Solstice, install 138 kV capacitor bank at Solstice, and build new Ft. Stockton Switch 138 kV station | Mar-20
7028 | Ft. Stockton SW to Rio Pecos: Rebuild 69 kV line | Rebuild Barrilla Junction to Ft. Stockton SW to Rio Pecos 69 kV line, convert to 138 kV, reterminate into Solstice, install 138 kV capacitor bank at Solstice, and build new Ft. Stockton Switch 138 kV station | Mar-20
5539 | Solstice to Bakersfield: Build 345 kV line | Construct new 345 kV station with two 345/138 kV autotransformers, reactor, and build two new 345 kV lines from Solstice to Bakersfield | Dec-20
From ERCOT Transmission Project and Information Tracking http://www.ercot.com/gridinfo/planning

## Slide 6: Exceeding $10,000/MW of binding element rating in February, 2019
Constrained Element | Contingency Name | Sum of Shadow Price x Interval($/MW) | Total Congestion Rent ($)
BARL_FTSW1_1 | SWCSBOO8 | 110,934 | 3,967,314
16TH_WRD2_1 | MLOTYUC8 | 41,850 | 5,781,930
HAMILT_MAVERI1_1 | DBIGKEN5 | 34,836 | 4,118,599
WHITE_PT_69A1 | SPORWH28 | 29,507 | 2,721,422
6437__F | DMTSCOS5 | 24,789 | 5,475,694
HILL_MAR_2_1 | DELMELM5 | 24,412 | 26,958,430
TREADW_YELWJC1_1 | DBIGKEN5 | 10,272 | 2,058,331
COOPERCK_ARCO_1 | DCRLLSW5 | 9,791 | 2,110,532
All constraints meeting this condition in February have been included in ERCOT February Operations Report, and will be presented in April ROS meeting.

## Slide 7: Exceeded $95,000/MW of binding element rating in 2018
Constrained Element | Contingency Name | Sum of Shadow Price x Interval ($/MW) | Total Congestion Rent ($)
6332__A | SWCSBOO8 | 1,535,807 | 251,852,003
591__A | DCRLLSW5 | 220,260 | 60,311,425
BARL_FTSW1_1 | SWCSBOO8 | 198,390 | 6,633,871
588_A_1 | SLWVLWS8 | 188,005 | 35,839,701
6270__C | DEMSSAG8 | 161,907 | 35,676,195
6437__F | DMTSCOS5 | 125,043 | 25,724,485
LOYOLA_69_1 | SKLELOY8 | 123,838 | 4,557,923
BRUNI_69_1 | SLAQLOB8 | 120,516 | 4,245,829
HEXT_YELWJC1_1 | SJUNYEL9 | 115,227 | 3,665,333
MHONDOCR_1 | DCASTXR8 | 113,927 | 15,342,875
CRTVLE_EINSTEN_1 | SSTLEIN8 | 107,328 | 9,169,389
16TH_WRD2_1 | SWOORI38 | 93,644 | 13,666,794