## Slide 1
April 10, 2019
PDCWG
ERCOT Staff
Update on the 20% Limits When Providing RRS

## Slide 2: Protocol Section 3.1.8 (3)
Current protocols state that the amount of RRS provided by thermal units and hydro units not operating in synchronous condenser fast response mode is limited to 20% of their respective HSL.
Starting June 2019, ERCOT systems will allow non thermal units that are qualified to provide RRS (and have demonstrated the capability), to carry more than 20% of their respective HSL as RRS.
ERCOT will continue to monitor RRS being carried in Real Time to ensure that the total quantity of RRS Gen is spread across multiple resources.
3.18 Resource Limits in Providing Ancillary Service
(3) For RRS:
(a) The full amount of RRS provided from a Generation Resource must be less than or equal to 20% of thermal unit HSL for an Ancillary Service Offer, and must be less than or equal to ten times the Emergency Ramp Rate, and must be frequency responsive;
(b) Hydro Generation Resources operating in the synchronous condenser fast-response mode may provide RRS up to the hydro Generation Resource’s proven 20-second response capability (which may be 100% of the HSL). The initiation setting of the automatic under-frequency relay setting shall not be lower than 59.80 Hz;
(c) For any hydro Generation Resource with a 5% droop setting operating as a generator, the amount of RRS provided may never be more than 20% of the HSL; and
(d) The amount of RRS provided from a Load Resource must be less than or equal to the HSL minus the sum of the LSL, Reg-Up Resource Responsibility, Reg-Down Resource Responsibility, and Non-Spin Resource Responsibility.

## Slide 3: Protocol Section 3.1.8 (3) NPRR863
Upon implementation of NPRR863, the amount of RRS provided by any Generation Resource (excluding Hydro units operating in synchronous condenser fast response mode and resources providing FFR) will be dependent on its verified droop performance
3.18 Resource Limits in Providing Ancillary Service
(3) For RRS:
(a) The full amount of RRS awarded to or self-arranged from an On-Line Generation Resource is dependent upon the verified droop characteristics of the Resource. ERCOT shall calculate and update, using the methodology described in the Nodal Operating Guide, a maximum MW amount of RRS for each Generation Resource subject to verified droop performance. The default value for any newly qualified Generation Resource shall be 20% of its HSL. A Private Use Network with a registered Resource may use the gross HSL for qualification and establishing a limit on the amount of RRS capacity that the Resource within the Private Use Network can provide;
(b) Hydro Generation Resources operating in the synchronous condenser fast-response mode may provide RRS up to the hydro Generation Resource’s proven 20-second response capability (which may be 100% of the HSL). The initiation setting of the automatic under-frequency relay setting shall not be lower than 59.80 Hz……
(c) The initiation setting of the automatic under-frequency relay setting for Load Resources providing RRS shall not be lower than 59.70 Hz; and
(d) The amount of RRS provided from a Resource capable of providing FFR must be less than or equal to its 15-minute rated capacity….