## Slide 1
ERCOT Frequency Control Report
March 2019
ERCOT
Operations Planning
PDCWG | April 10, 2019

## Slide 2: Summary of March 2019
CPS1: 173.12%
Current CPS1 12-Month Rolling Average: 174.64%
3 BAAL Exceedances
1 hourly CPS1 scores below 100%
BAAL-003 Events have updated through 2018
2018 BAAL-003 FRM Performance: -895.19
2019 RMS1 Statistics
  Mean: 15.51 mHz
  Min: 13.05 mHz
  Max: 18.46 mHz
Energy Statistics
  Total Energy: 27,806,530 MWh
  Wind Energy: 6,058,318 MWh
  Percent Energy from Wind Generation: 21.79%
Minimum System Inertia
  Mean: 176,527
  Max: 282,123 on March 5th
  Min: 134,534 on March 27th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
March-19 CPS1 (%): 173.12
Notes: Outliers:
3/11/19 21:00 90.21%
Unit Loss and large manual offset. Large positive expected generation deviation. Non conforming load dropped by 200 MW while frequency was high. Load was decreasing.

## Slide 5: BAAL Exceedances & Violations
There were 3 BAAL exceedances in March
  March 2, 2019
    Unit Trip at 03:18:53
    Loss of 1224 MW
    Less than 59.91 Hz for 1 minute
  March 11, 2019
    Unit Trip at 21:24:04
    Loss of 610 MW
    Less than 59.91 Hz for 2 minutes

## Slide 6: 15-Minute Average CPS1%
February-19 CPS1 (%): 173.12

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 174.64%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes: Mean is 15.28 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 15.51 mHz
Min: 13.05 mHz
Max: 18.46 mHz

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2018 BAL-003 Selected Events

## Slide 19: Op. Year 2018 BAL-003 FRM Performance
Notes: FRM Changed to -895 from -759 on April 1st at 10 AM

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 27,806,530 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 6,058,318 MWh

## Slide 23: % Energy from Wind Generation
Notes: 21.79%

## Slide 24: ERCOT System Inertia

## Slide 25: Daily Minimum System Inertia
Notes: Minimum Inertia = 128,759 MW*s on 11/3/2018.
Previous Minimum was 130,014 MW*s on 10/27/2017. This was also our record wind day.
Data:
Mean: 176,527
Max: 282,123 on March 5th
Min: 134,534 on March 27th

## Slide 26: Questions?
Thank you!