## Slide 1
Spring and Fall Wind Capacity Contributions Based on Potential Methodology Changes
Connor Anderson
Resource Adequacy
04/12/2019

## Slide 2: Effects of Changes on Spring 2019 (Preliminary SARA)
1,667 MW of planned wind
 | Original SARA | Modified SARA | Modified SARA with Capacity-Weighted Contributions
Coastal Contribution | 63% | 63% | 64%
Panhandle Contribution | N/A | 33% | 36%
South Non-Coastal Contribution | N/A | 46% | 49%
Other Contribution | N/A | 29% | 29%
Non-Coastal Contribution | 30% | N/A | N/A
Change in Planned Wind Contribution | N/A | +46 MW | +70 MW

## Slide 3: Effects of Changes on Spring 2019 (Final SARA)
102 MW of planned wind
 | Original SARA | Modified SARA | Modified SARA with Capacity-Weighted Contributions
Coastal Contribution | 63% | 63% | 64%
Panhandle Contribution | N/A | 33% | 36%
South Non-Coastal Contribution | N/A | 46% | 49%
Other Contribution | N/A | 29% | 29%
Non-Coastal Contribution | 30% | N/A | N/A
Change in Planned Wind Contribution | N/A | 0 MW | 0 MW

## Slide 4: Effects of Changes on Fall 2018 (Preliminary SARA)
961 MW of planned wind
 | Original SARA | Modified SARA | Modified SARA with Capacity-Weighted Contributions
Coastal Contribution | 40% | 40% | 36%
Panhandle Contribution | N/A | 43% | 45%
South Non-Coastal Contribution | N/A | 28% | 26%
Other Contribution | N/A | 36% | 36%
Non-Coastal Contribution | 18% | N/A | N/A
Change in Planned Wind Contribution | N/A | +123 MW | +126 MW

## Slide 5: Effects of Changes on Fall 2018 (Final SARA)
360 MW of planned wind
 | Original SARA | Modified SARA | Modified SARA with Capacity-Weighted Contributions
Coastal Contribution | 40% | 40% | 36%
Panhandle Contribution | N/A | 43% | 45%
South Non-Coastal Contribution | N/A | 28% | 26%
Other Contribution | N/A | 36% | 36%
Non-Coastal Contribution | 18% | N/A | N/A
Change in Planned Wind Contribution | N/A | +67 MW | +68 MW

## Slide 6: Current vs. Alternative Capacity Contribution Methodology, All Seasons
Region | Winter | Spring | Summer | Fall
Coastal | 43% | 63% | 59% | 40%
Non-Coastal | 20% | 30% | 14% | 37%
Region | Winter | Spring | Summer | Fall
Coastal | 46% | 64% | 63% | 36%
Panhandle | 28% | 36% | 29% | 45%
South Non-Coastal | 39% | 49% | 47% | 26%
Other | 17% | 29% | 13% | 36%
Region | Winter | Spring | Summer | Fall
Coastal | 865 | 1,267 | 1,186 | 804
Non-Coastal | 2,542 | 3,813 | 1,779 | 4,702
Total | 3,406 | 5,079 | 2,965 | 5,507
Region | Winter | Spring | Summer | Fall
Coastal | 925 | 1,287 | 1,267 | 724
Panhandle | 941 | 1,209 | 974 | 1,512
South Non-Coastal | 523 | 657 | 631 | 349
Other | 1,361 | 2,322 | 1,041 | 2,883
Total | 3,750 | 5,476 | 3,912 | 5,467
Difference | +344 | +396 | +947 | -39
Planned capacity with signed IAs (MW) – Nameplate capacity: 14,720 MW*
Capacity contributions (%)
*cumulative planned capacity through 2021, taken from March 2019 GIS Report

## Slide 7: Methodology Recommendations
ERCOT recommends:
  Adding a Panhandle region for wind capacity contribution calculations
  Using a capacity-weighted average approach (rather than a simple average) for both wind and solar capacity contribution calculations
At this time, ERCOT does not recommend adding a South Non-Coastal region for wind capacity contribution calculations due to its small geographic size
  We plan to investigate the impact of adding these counties to the Coastal region