## Slide 1
Intra-Hour Wind Forecast Accuracy Updates (Apr. 2019)
WMWG
Operations Analysis
April 22, 2019

## Slide 2: Current GTBD Parameters
Historical K factor tuning events:
12/4/18 10:05 AM – K6 Changed from 0 to 0.5
2/12/19 2:15 PM – K6 changed from 0.5 to 1.0
3/12/19 2:10 PM – PWRR Max/Min Threshold from 10 MW/min to 15 MW/min
3/19/19 2:15 PM – PWRR Max/Min Threshold from 15 MW/min to 20 MW/min
4/01/19 10:05 AM – K5 changed from 0.5 to 0.4 and Max. Integral ACE Feedback changed from 250 to 150
Notes: 3/12/18 – Integral ACE Time Constant Changed from 60 min to 45 min
5/17/18 – K4 Changed from 0.3 to 0.2 and K5 Changed from 0.4 to 0.5
12/4/18 – 10:05 AM – K6 Changed from 0 to 0.5
2/12/19 – 2:15 PM – K6 changed from 0.5 to 1.0
3/12/19 – 2:10 PM – PWRR Threshold from 10 to 15 MW/min
3/19/19 – 2:15 PM – PWRR Threshold from 15 to 20 MW/min
4/01/19 - K5 changed from 0.5 to 0.4 and Max. Integral ACE Feedback changed from 250 to 150

## Slide 3: Projected Wind Ramp Rate (PWRR) Error
Chart: April 6th, 2019
| 43561.003472222219 | 43561.006944444445 | 43561.010416666664 | 43561.013888888891 | 43561.017361111109 | 43561.020833333336 | 43561.024305555555 | 43561.027777777781 | 43561.03125 | 43561.034722222219 | 43561.038194444445 | 43561.041666666664 | 43561.045138888891 | 43561.048611111109 | 43561.052083333336 | 43561.055555555555 | 43561.059027777781 | 43561.0625 | 43561.065972222219 | 43561.069444444445 | 43561.072916666664 | 43561.076388888891 | 43561.079861111109 | 43561.083333333336 | 43561.086805555555 | 43561.090277777781 | 43561.09375 | 43561.097222222219 | 43561.100694444445 | 43561.104166666664 | 43561.107638888891 | 43561.111111111109 | 43561.114583333336 | 43561.118055555555 | 43561.121527777781 | 43561.125 | 43561.128472222219 | 43561.131944444445 | 43561.135416666664 | 43561.138888888891 | 43561.142361111109 | 43561.145833333336 | 43561.149305555555 | 43561.152777777781 | 43561.15625 | 43561.159722222219 | 43561.163194444445
Persistence Error | -9.5898 | 192.0264 | 76.75 | 60.7744 | -63.5273 | -125.5244 | -69.4082 | -59.8643 | 19.4746 | 98.8398 | 155.3574 | 200.6904 | 21.1582 | 115.3242 | 120.6426 | 355.9824 | 263.2988 | 252.2568 | 236.4209 | 259.0654 | 178.2158 | 174.6064 | 21.7744 | 84.0977 | 96.8643 | 152.291 | 248.8887 | 210.96 | 477.2412 | 475.4707 | 553.418 | 672.8281 | 521.6475 | 371.3486 | 267.666 | 250.2939 | 284.3267 | 160.8438 | 96.8613 | -35.4805 | 53.5288 | -83.3794 | -100.8296 | -104.0742 | 60.9922 | 190.3936 | 297.4766
PWRR Error | 21.5098 | 168.2256 | 31.1494 | -39.2246 | -80.1279 | -192.4229 | -48.6094 | -77.5625 | 68.873 | 120.3398 | 70.458 | 157.29 | -75.042 | 15.3242 | 61.042 | 269.6816 | 163.2988 | 152.2568 | 136.4209 | 159.0654 | 78.2158 | 74.6064 | -78.2256 | -15.9023 | 18.8633 | 88.9893 | 169.5898 | 110.96 | 377.2412 | 375.4707 | 453.418 | 572.8281 | 421.6475 | 271.3486 | 167.666 | 150.2939 | 184.3267 | 60.8438 | -3.1387 | -135.4805 | -46.4712 | -155.2798 | -152.0303 | -95.5742 | 97.1924 | 221.4937 | 241.8765
PWRR Error (No Threshold) | 21.6102 | 168.2264 | 31.05 | -39.1256 | -80.2273 | -192.4244 | -48.6082 | -77.5643 | 69.0746 | 120.2398 | 70.3574 | 157.1904 | -74.9418 | -19.2758 | 61.1426 | 269.7824 | 97.9988 | 104.3568 | 40.0209 | 75.7654 | -2.2842 | 14.1064 | -103.9256 | -65.2023 | 19.0643 | 89.091 | 169.6887 | 64.86 | 340.5412 | 284.6707 | 296.718 | 363.4281 | 174.7475 | -3.7514 | -78.934 | -34.0061 | 29.8267 | -63.3562 | -110.2387 | -180.6805 | -59.4712 | -155.2794 | -151.9296 | -95.7742 | 97.2922 | 221.4936 | 241.8766
Wind HSL | 15069.6973 | 14877.6709 | 14800.9209 | 14740.1465 | 14803.6738 | 14929.1982 | 14998.6064 | 15058.4707 | 15038.9961 | 14940.1562 | 14784.7988 | 14584.1084 | 14562.9502 | 14447.626 | 14326.9834 | 13971.001 | 13707.7021 | 13455.4453 | 13219.0244 | 12959.959 | 12781.7432 | 12607.1367 | 12585.3623 | 12501.2646 | 12404.4004 | 12252.1094 | 12003.2207 | 11792.2607 | 11315.0195 | 10839.5488 | 10286.1309 | 9613.3027 | 9091.6553 | 8720.3066 | 8452.6406 | 8202.3467 | 7918.02 | 7757.1763 | 7660.3149 | 7695.7954 | 7642.2666 | 7725.646 | 7826.4756 | 7930.5498 | 7869.5576 | 7679.1641 | 7381.6875
Performance Metric | SCED PWRR (12/4 – 3/19) | Persistence Ramp* (12/4 – 3/19) | SCED PWRR (3/19 – 4/18) | Persistence Ramp* (3/19 – 4/18)
Monthly MAE (MW) | 65 | 76 | 65 | 82
Monthly MAE when 5-Min. Wind Ramp > 100 MW | 131 | 163 | 120 | 172
* Persistence Ramp assumes using a 0 MW wind ramp in PWRR

## Slide 4: Appendix The following slides were presented at March PDCWG

## Slide 5: Intra-Hour Wind Ramp Forecast Error (March 2019)

## Slide 6: Intra-Hour Wind Ramp Forecast Error (March 2019)