## Slide 1
Battery Energy Storage Systems (BESS) –Interconnection Issues
John Bernecker
Supervisor, Resource Integration
April 23, 2019

## Slide 2: Battery Interconnection Requests*
*Does not include transmission-connected batteries <10MW or distribution-connected batteries.
Chart: First Summer In-Service
| 2020 | 2021 | 2022
Stand-alone | 341.36 | 753.73 | 753.73
Co-located | 170 | 1670.11 | 2747.51
Total | 511.36 | 2423.84 | 3501.24

## Slide 3: RARF Issues
There is no RARF form designed specifically for BESS
BESS are currently modeled as both a Generation Resource (using the Gen Form) and a Controllable Load Resource (using the Load Resource Form)
  Charging load information is also included on the Transmission Form
Inverter and collector system details are not explicitly captured
  Equivalent models for the aggregate are captured instead
BESS-specific information, such as round-trip efficiency, is not captured

## Slide 4: Operational Constraints
Developers have made inquiries about constructing co-located solar / wind and storage and limiting the combined maximum injection to the ERCOT system to less than the sum of the individual resources’ capacities
  E.g. 100 MW solar PV coupled with 100 MW BESS limited to 100 MW maximum real power output at the point of interconnection
ERCOT systems cannot currently accommodate this behavior
  Each resource is studied and modeled individually
  Resources receive individual SCED basepoints

## Slide 5: DC-Coupled Solar and Storage
Developers have made inquiries about interconnecting DC-coupled solar PV and BESS
ERCOT is discussing issues that need to be addressed to accommodate DC-coupled resources
ERCOT’s current assumption is that all interconnection requests for co-located resources are AC-coupled