Proposed Battery Energy/Electric Storage Resource (BESR) Model

# Introduction

With increased battery penetration, ERCOT’s objective is to change software systems to take into account the unique characteristics of storage resources.

# High Level Schematic diagram of a Battery System

+

-

Xfmr

AuxLoad

Cooling & Control

Battery

Power Electronics

Point of Interconnection (POI) or

Point of Common Coupling (PCC)

-

~

meter

grid

RBattery

RPwerElec

RXfmr

AuxLoad

Cooling & Control

+

-

meter

grid

Point of Interconnection (POI) or

Point of Common Coupling (PCC)

Losses considered for Charging and Discharging efficiency calculations

MWdischarging@pcc

MWcharging@pcc

SOC_OperMaxMWh@tBattery

SOCMWHr@tBattery

SOC_OperMinMWh@tBattery

SOC_OperMaxMWh@tpcc

SOCMWh@tpcc

SOC_OperMinMWh@tpcc

# Losses in a Battery System

SOCMWHr@tBattery=Energy MWh Stored in Battery@t

SOC_OperMaxMWh@tBattery=Operating Max. Energy MWh that can be Stored in Battery@t

SOC_OperMinMWh@tBattery=Operating Min. Energy MWh that can be Stored in Battery@t

# Charging Efficiency Curve

The charging efficiency curve is represented as a function of the charging power (MW).

Charging Efficiency@MWchargingpcc %=100×MWchargingpcc-LossRBatery+LossRPwrElec+LossRXfmr+AuxLoadMWchargingpcc

# Discharging Efficiency Curve

The discharging efficiency curve is represented as a function of the discharging power (MW).

Disharging Efficiency@MWdischargingpcc %=100×MWdischargingpccMWdischargingpcc+LossRBatery+LossRPwrElec+LossRXfmr+AuxLoad

# The State of Charge (SOC) inside battery in MWh for a constant charging power (MWchargingpcc)

SOCMWh@t+∆tBattery=SOCMWh@tBattery+∆t×MWchargingpcc-LossRBatery+LossRPwrElec+LossRXfmr+AuxLoad

# The State of Charge (SOC) inside battery in MWh for a constant discharging power (MWdischargingpcc)

SOCMWh@t+∆tBattery=SOCMWh@tBattery-∆t×MWdischargingpcc+LossRBatery+LossRPwrElec+LossRXfmr+AuxLoad

# Example of Charge Efficiency Curve for a Li-Ion Battery

Ceff

# Example of Discharge Efficiency Curve for a Li-Ion Battery

Deff

# ERCOT Use of New Telemetry – Example calculations

## Assumption

The charging and discharging efficiencies are fairly constant across operating range.

Using the assumption stated above, Let the single number Ceff and Deff represent the single charging and single discharging efficiencies respectively across the whole operating range.

The round trip efficiency (RTE) is defined as RTE=Ceff×Deff

## Round Trip Efficiency (RTE)

The source of Round Trip Efficiency (RTE) will not be telemetry. For the first phase, RTE will be obtained from Resource Entity via a RFI initially and will be user enterable into the system for modifications. The default value will be 0.8

SOCMWh@tpcc=Energy MWh that can be discharged at PCC or POI @t

= Deff×SOCMWh@tBattery

SOCOperMaxMWh@tpcc=Operating Max. Energy MWh that can be discharged at PCC or POI @t

=Deff×SOC_OperMaxMWh@tBattery

SOCOperMinMWh@tpcc=Operating Min. Energy MWh that can be discharged at PCC or POI @t

=Deff×SOC_OperMinMWh@tBattery

## The State of Charge (SOC) at PCC or POI in MWh for a constant charging power (MWchargingpcc)

SOCMWh@t+∆tpcc=SOCMWh@tpcc+∆t×RTE×MWchargingpcc

## The State of Charge (SOC) at PCC or POI in MWh for a constant discharging power (MWdischargingpcc)

SOCMWh@t+∆tpcc=SOCMWh@tpcc-∆t×MWdischargingpcc

## The constant discharge power that can be sustained from time t1 to t2

MWdischarging(t1 to t2)poi=MinMaxOperDishargeMW,SOCMWh@t1poi-SOC_OperMinMWh@t1poit2-t1

## The constant charge power that can be sustained from time t1 to t2

MWcharging(t1 to t2)poi=MinMaxOperChargeMW,SOC_OperMaxMWh@t1poi-SOCMWh@t1poiRTE×t2-t1

# New Telemetry (ICCP) Points for Electric Storage Resources

| Name | Unit | Telemetry | Description |
| --- | --- | --- | --- |
| Maximum Operating State of Charge [SOC_OperMax] | MWh | X | For the current operating condition of the Storage Resource, represents the maximum amount of stored energy capability in MWh that should not be exceeded. This energy value is calculated at the Point Of Interconnection (POI) or Service Delivery Point (SDP). (FERC 841 Item: “Maximum State of Charge”). For example, if the Storage Resource currently has the capability of storing a maximum of 10 MWh and the discharge efficiency is 0.94, then this telemetered value (SOC_OperMax) = 0.94*10=9.4 MWh Note: The Resource Entity can provide this telemetry using other techniques/calculations as long as the telemetered value represents the “not to exceed” maximum stored energy capability as measured at the POI/SDP. |
| Minimum Operating State of Charge [SOC_OperMin] | MWh | X | For the current operating condition of the Storage Resource, represents the required minimum amount of stored energy in MWh that should not be discharged below. This energy value is calculated at the POI/SDP. (FERC 841 Item: “Minimum State of Charge”) For example, if the Storage Resource is required to store a minimum of 2 MWh and the discharge efficiency is 0.94, then this telemetered value (SOC_OperMin) = 0.94*2=1.88 MWh Note: The Resource Entity can derive this telemetry using other techniques/calculations as long as the telemetered value represents the “not to go below” required minimum stored energy as measured at the POI/SDP. |
| State of Charge [SOC_Telem] | MWh | X | For the current operating condition of the Storage Resource, represents the amount of energy in MWh that is being stored. This energy value is calculated at the POI/SDP. (FERC 841 Item: “State of Charge”) For example, if the Storage Resource is currently storing 6 MWh and the discharge efficiency is 0.94, then this telemetered value (SOC_Telem) = 0.94*6=5.64 MWh Note: The Resource Entity can derive this telemetry using other techniques/calculations as long as the telemetered value represents the current stored energy as measured at the POI/SDP. |
| Maximum Operating Discharge Power Limit [MaxOperDischargeMW] | MW | X | For the current operating condition of the Storage Resource, represents the maximum discharge power (MW) capability measured at the POI/SDP. (FERC 841 Item: “Maximum Discharge Limit”) |
| Maximum Operating Charge Power Limit [MaxOperChargeMW] | MW | X | For the current operating condition of the Storage Resource, represents the maximum charge power (MW) capability measured at the POI/SDP. (FERC 841 Item: “Maximum Charge Limit”) |

# BESR modeling/calculations

## Assumptions

This document describes the modeling/calculations in ERCOT Market Management System (MMS) for a Storage Resource with the following characteristics:

- Physically a single device with one electrical pathway to the modeled electrical network (NMMS CIM model)

  - The charging and discharging electrical path is the same

- Limited duration device (<= 24 hours). This implies that the MWh energy storage capacity of the Storage Resource cannot discharge at a MW level equal to its rating continuously for 24 hours.

- Does not have temporal constraints (StartTime, MinUpTime, MinDownTime, etc.) and does not have transition times between charging and discharging

- Does not have startup, shutdown and transition costs

- Can smoothly transition from charging to discharging and vice-versa and there is no dead band around 0 MW

- Charging efficiency (ηchg) and Discharging efficiency (ηdischg) are constant over the operating range of the Storage Resource, i.e. Round Trip Efficiency ηrt=ηchg×ηdischg where ηchg=ηdischg

- Self discharge of Storage Resource is zero. Self discharge is the loss of energy when the Storage Resource is idle (not doing anything).

- All data inputs are measured at the Point of Interconnection (POI) or Point of Common Coupling (PCC)

- Single price curve from charging (Bid-To-Buy) to discharging (Offer-To-Sell) that is monotonically non-decreasing as the MW quantity increases . i.e. The single submitted price curve covers both the charging and discharging MW range and provides the Bid-to-Buy price for charging and the Offer-To-Sell price for discharging for the Storage resource

- The Storage Resource Status will be ON, ONXX, OFF, or OUT. This statement reflects current thoughts that new statuses are NOT required

- ERCOT considers the State of Charge operational limits but does not manage a Storage Resources State of Charge

With the above Storage Resource characteristics, the MMS modeling/calculations for Storage Resources becomes a dispatch problem for Real-Time (SCED), DAM and RUC processes.

Storage Resource will be settled at its Nodal LMP/SPP for both charging and discharging.

## Out of scope for this document

Storage Resource technologies that do not conform to the characteristics described above, likely to be pumped hydro and CAES as they could have separate electrical pathways for charging and discharging and also have temporal constraints and deadbands over the MW operating range (especially around 0 MW).

## Assumptions of other systems

NMMS

Replace the current model of a Controllable Load Resource and a Generation Resource including pseudo breakers (if any) with a single device.

EMS-Network Applications

Modeled as a device that can inject to or withdraw energy from the grid (mutually exclusive). Behaves like a generator with a negative Pmin. State Estimator and Power Flow need to allow negative injections for Storage Resource locations.

## Reserve Accounting for Storage Resource

Currently, for a Resource, reserves are considered in terms of MW. Inherently, this assumes that the Resource is capable of providing the reserve MW response for as long as required.

For a Storage Resource that has a limited duration, the reserve accounting (headroom for ORDC, frequency responsive capacity for PRC, Ancillary Service) should be based on the energy (MWh) taking into account State of Charge.

Physical Responsive Capability (PRC) contribution from Storage Resource: Convert the energy capability based on available State of Charge and the minimum operating State of Charge to an equivalent MW value for a specified time duration. This will require a determination of a time duration that the frequency response is required to be accounted for in PRC calculation (15 seconds, 5 minutes, 15 minutes, 1 hour?). For example, if the determination is that the frequency response from a Resource to be counted in PRC contribution is for a 15 minute duration, then equivalent MW PRC contribution from a Storage Resource will be:

MWsequivalentPRC=SOCsTelem-SOCsOperMin∆t, ∆t=14 hour

Operational Reserve Demand Curve (ORDC): There are two reserve levels calculated in ORDC, RTOLCAP (MW reserves that can respond to events within the next 1 hour) and RTOLCAP+RTOFFCAP where RTOFFCAP is the MW reserves that can respond to events occurring in the second half of the upcoming hour. The equivalent MW level determined for RTOLCAP from a storage resource, will depend on the time duration agreed upon for ORDC purpose (same as PRC?). If the time duration to determine the equivalent MW level is 1 hour, then will be:

MWsequivalentRTOLCAP=SOCsTelem-SOCsOperMin∆t, ∆t=1 hour

Ancillary Service: Depending on the type of Ancillary Service, different time duration will be used to determine whether a Storage Resource is capable of providing its MW responsibility.

This accounting will be used in Ancillary Service Responsibility Check and other processes

As an example:

Upward AS: (Regulation Up, FRRS-Up, RRS, Non-Spin, FFR*, ECRS*) (* NPRR 863)

Storage Resource is carrying upward ASMWresponsibilityASu, then to determine whether it is capable of providing this AS, apart from the standard checks used for other Resources, there is an additional check for energy:

ASuTypefsASuASMWresponsibilityASu, ∆tASu≤SOCsTelem-SOCsOperMin

Where,

fsASuASMWresponsibilityASu, ∆tASu is a linear function in ASMWresponsibilityASu, ∆tASu  depends on type of AS

A very conservative approach is to treat the AS responsibility the same as energy i.e.,

fsASuASMWresponsibilityASu, ∆tASu=ASMWresponsibilityASu×∆tASu

Downward AS: (Regulation Down, FRRS-Dn)

Storage Resource is carrying downward ASMWresponsibilityASd, then to determine whether it is capable of providing this AS, apart from the standard used for other Resources, there is an additional check for energy:

ASdTypefsASdASMWresponsibilityASd,ηrt, ∆tASd≤SOCsOperMax-SOCsTelem

Where,

fsASdASMWresponsibilityASd, ηrt,∆tASd is a linear function in ASMWresponsibilityASd, ∆tASd  depends on type of AS

A very conservative approach is to treat the AS responsibility the same as energy i.e.,

fsASdASMWresponsibilityASd, ηrt,∆tASd=ASMWresponsibilityASd×ηrt×∆tASd

## FERC Order 841: Storage Resource Parameters

| Physical or Operational Characteristic | Definition | ERCOT ICCP Request? |
| --- | --- | --- |
| State of Charge | State of Charge represents the amount of energy stored in proportion to the limit on the amount of energy that can be stored, typically expressed as a percentage. It represents the forecasted starting State of Charge for the market interval being offered into. | Yes [SOC_Telem], may require equivalent in COP [SOC_Target] ? unit of measure = MWh |
| Maximum State of Charge | Maximum State of Charge represents a State of Charge value that should not be exceeded (i.e., gone above) when a resource using the participation model for electric storage resources is receiving electric energy from the grid (e.g., 95% State of Charge). | Yes [SOC_OperMax] unit of measure = MWh |
| Minimum State of Charge | Minimum State of Charge represents a State of Charge value that should not be exceeded (i.e., gone below) when a resource using the participation model for electric storage resources is injecting electric energy to the grid (e.g., 5% State of Charge). | Yes [SOC_OperMin] unit of measure = MWh |
| Maximum Charge Limit | Maximum Charge Limit represents the maximum MW quantity of electric energy that a resource using the participation model for electric storage resources can receive from the grid. | Yes [MaxOperChargeMW] or LSL unit of measure = MW |
| Maximum Discharge Limit | Maximum Discharge Limit represents the maximum MW quantity that a resource using the participation model for electric storage resources can inject to the grid. | Yes [MaxOperDischargeMW] or HSL unit of measure = MW |
| Minimum Charge Time | Minimum Charge Time represents the shortest duration that a resource using the participation model for electric storage resources is able to be dispatched by the RTO/ISO to receive electric energy from the grid (e.g., one hour). |  |
| Maximum Charge Time | Maximum Charge Time represents the maximum duration that a resource using the participation model for electric storage resources is able to be dispatched by the RTO/ISO to receive electric energy from the grid (e.g., four hours). |  |
| Minimum Run Time | Minimum Run Time represents the minimum amount of time that a resource using the participation model for electric storage resources is able to inject electric energy to the grid (e.g., one hour). |  |
| Maximum Run Time | Maximum Run Time represents the maximum amount of time that a resource using the participation model for electric storage resources is able to inject electric energy to the grid (e.g., four hours). |  |
| Minimum Discharge Limit | The minimum MW output level that a resource using the participation model for electric storage resources can inject onto the grid. |  |
| Minimum Charge Limit | The minimum MW level that a resource using the participation model for electric storage resources can receive from the grid. |  |
| Discharge Ramp Rate | The speed at which a resource using the participation model for electric storage resources can move from zero output to its Maximum Discharge Limit. |  |
| Charge Ramp Rate | The speed at which a resource using the participation model for electric storage resources can move from zero output to its Maximum Charge Limit. |  |

## DAM and RTM: Security Constrained Economic Dispatch Formulation with Storage Resource

This formulation can be used for single interval or multi-interval, with and without AS co-optimization. It requires the cost curve setup as described below.

COP data from Storage Resource used in DAM:

SOCsOperMaxCOP : The maximum amount of stored energy capability in MWh that should not be exceeded. This energy value is calculated as the energy that can be discharged at the Point Of Interconnection (POI) or Service Delivery Point (SDP). (FERC 841 Item: “Maximum State of Charge”).

SOCsTargetCOP : The amount of stored energy in MWh that can be discharged as measured at the POI/SDP. (FERC 841 Item: “State of Charge”)

SOCsOperMinCOP : The minimum amount of stored energy capability in MWh that should not be discharged below. This energy value is calculated as the energy that can be discharged at the POI/SDP. (FERC 841 Item: “Minimum State of Charge”)

HSLs : (HSL – positive number) The maximum discharge power (MW) capability measured at the POI/SDP. (FERC 841 Item: “Maximum Discharge Limit”). This is primarily based on the invertor capability.

LSLs: (LSL – negative number) The maximum charge power (MW) capability measured at the POI/SDP. (FERC 841 Item: “Maximum Discharge Limit”). This is primarily based on the invertor capability

### Storage Resource Cost Curve:

The requirement is that:

- Cost curve be monotonically increasing from maximum charging MW to maximum discharging MW.

- The maximum price on the charging curve is less than the minimum price on the discharging curve i.e. δ>0

MW Discharging

(+ve)

MW Charging

(-ve)

HSL

LSL or LPC

$/MWh

δ>0

Outputs:

PsBP : SCED Base Point or DAM energy award to Storage Resource, negative when charging and positive when discharging

PsASu : AS award for upward AS, positive

PsASd : AS award for downward AS, positive

## SCED/DAM formulation

- For simplicity, only one Storage Resource in system

- For simplicity, demand bids are ignored (i.e demand is inflexible)

- Penalty/Slack variables not included in formulation

- Co-Optimized with two generic types of AS (up and down)

- Multi-interval optimization

- Define variable Ps,tBP=Ps,tDis-Ps,tChg, where Ps,tDis,Ps,tChg≥0, and  Ps,tDis×Ps,tChg=0

Note that the constraint (non convex) Ps,tDis×Ps,tChg=0 is not modeled (enforced). The rules on the Storage Resource cost curve ensures the condition, where both Ps,tDis,Ps,tChg≥0,  is simultaneously not possible.

The complimentary condition is enforced by the cost curve separation between charging and discharging.

Objective: Mint=124gCg,tePg,tBP×Pg,tBP+Cs,teDisPs,tDis×Ps,tDis-Cs,teChgPs,tChg×Ps,tChg+gCg,tASuPg,tASu×PgASu+gCg,tASdPg,tASd×Pg,tASd+Cs,tASuPs,tASu×Ps,tASu+Cs,tASdPs,tASd×Ps,tASd

Subject to:

System Wide Power Balance (∀t):

gPg,tBP+ Ps,tBP=Demandt

AS Requirements (∀t):

gPg,tASu+ Ps,tASu≥ AS_Up_Reqt

gPg,tASd+ Ps,tASd≥ AS_Dn_Reqt

Transmission Constraint (∀t,∀tc):

gSFg,ttc×Pg,tBP+SFs,ttc×Ps,tBP≤MathLimitttc

Generator MW Dispatch Limits (∀t,∀g) :

LSLg,t≤Pg,tBP-Pg,tASd

Pg,tBP+Pg,tASu≤HSLg,t

Note that, in DAM, LSL and HSL are modified from COP based on the min/max points on the Offer curve submitted in DAM

Storage Resource MW Dispatch Limits (∀t,s) :

LSLs,t≤Ps,tBP-Ps,tASd

Ps,tBP+Ps,tASu≤HSLs,t

Note that, in DAM, LSL and HSL are modified from COP based on the min/max points on the cost curve submitted in DAM

Storage Resource SOC Limits (∀t,s):

SOCs,t=SOCs,t-1+ηrt×Ps,tChg-Ps,tDis×∆t,     ∆t=1 hour

SOCs,tOperMin≤SOCs,t≤SOCs,tOperMax

Note that for the first hour, the initial State of Charge SOCs,1-1, more discussion needed on the how, what the where for the initial condition of State of Charge is

Storage Resource AS award limits as a function of SOC Limits (∀t,s):

ASuTypefs,tASuPs,tASu, ∆tASu≤SOCs,t-SOCs,tOperMin and

ASdtypefs,tASdPs,tASd,ηrt, ∆tASd≤SOCs,tOperMax-SOCs,t

Where,

fs,tASuPs,tASu, ∆tASu is a linear function in Ps,tASu, ∆tASu  depends on type of AS, and

fs,tASdPs,tASd,ηrt, ∆tASd is a linear function in Ps,tASd, ∆tASd depends on type of AS

A very conservative approach to account AS awards in the energy picture is to treat them the same as energy i.e.,

fs,tASuPs,tASu, ∆tASu=Ps,tASu×∆tASu=1 hour and,

fs,tASdPs,tASd,ηrt, ∆tASd=Ps,tASd×ηrt×∆tASd=1 hour