## Slide 1
Energy Storage Workshop
April 23, 2019
ERCOT Staff
Energy Storage Resources
RRS Limit,
PRC Estimation & Operations Studies

## Slide 2: RRS Limit - Current Protocol Section 3.1.8 (3)
Current protocols state that the amount of Responsive Reserve Service (RRS) provided by thermal units and hydro units not operating in synchronous condenser fast response mode is limited to 20% of their respective High Sustained Limit (HSL).
Starting June 2019, ERCOT systems will allow non-thermal units that are qualified to provide RRS (and have demonstrated the capability), to carry more than 20% of their respective HSL as RRS.
Note that, ERCOT will continue to monitor RRS being carried in Real Time to ensure that the total quantity of RRS from Generation Resources is spread across multiple resources.
3.18 Resource Limits in Providing Ancillary Service
(3) For RRS:
(a) The full amount of RRS provided from a Generation Resource must be less than or equal to 20% of thermal unit HSL for an Ancillary Service Offer, and must be less than or equal to ten times the Emergency Ramp Rate, and must be frequency responsive;

## Slide 3: RRS Limit - NPRR 863 Protocol Section 3.1.8 (3)
Upon implementation of NPRR863, the amount of RRS provided by any Generation Resource (excluding Hydro units operating in synchronous condenser fast response mode and resources providing FFR) will be dependent on its verified droop performance
3.18 Resource Limits in Providing Ancillary Service
(3) For RRS:
(a) The full amount of RRS awarded to or self-arranged from an On-Line Generation Resource is dependent upon the verified droop characteristics of the Resource. ERCOT shall calculate and update, using the methodology described in the Nodal Operating Guide, a maximum MW amount of RRS for each Generation Resource subject to verified droop performance. The default value for any newly qualified Generation Resource shall be 20% of its HSL. A Private Use Network with a registered Resource may use the gross HSL for qualification and establishing a limit on the amount of RRS capacity that the Resource within the Private Use Network can provide;

## Slide 4: PRC Contribution Estimation
Currently Physical Responsive Capability (PRC) for a Generation Resource is calculated in real-time based on the resource’s telemetered HSL, its current output, and a 20% limit.
  Real time PRC also includes contribution from Wind and Solar resources
  20% limit does not apply to hydro operating in synchronous condenser fast response mode
  Energy Storage Resource’s PRC contribution will also be limited to 20% limit per current Nodal Protocols even when they can provide more than 20% of their capacity as RRS.
Under NPRR 863 when providing resources capable of Fast Frequency Response (FFR) can provide RRS. ERCOT’s expectation is that like Load Resources providing RRS, FFR will contribute fully to PRC.
Thus, the assumptions currently being used to compute PRC, and ability to deliver on Ancillary Service (AS) responsibilities for limited duration devices such as Energy Storage Resources will need to reviewed. Operational parameters such as State of Charge and duration of response may need to be factored into these.

## Slide 5: Operations Studies
The scope of changes in business process, applications in Energy Management System (EMS) will need to be reviewed to appropriately model and analyze a Energy Storage Resource’ characteristics both in near term and look ahead studies. For e.x.
  How should State of Charge and duration be Energy Storage Resource be accounted for in studies like power flow, contingency analysis, outage evaluations, etc.?
    Currently some forward looking studies and reports (CDR, SARA, etc.) do not account for any MWs from Energy Storage Resource. This may not be the most appropriate assumption going forward.
  Would new contingencies be needed to assess impacts on the grid when an Energy Storage Resource has run out of State of Charge?
  Would a new outage type be needed to track energy derates on Energy Storage Resources?
Would rules related to Compliance will need to be revisited/developed?
ERCOT CIM model for Energy Storage will need to be reviewed and updated once the requirements from all ERCOT systems/areas (like EMS, MMS, planning) are hashed out.