## Slide 1
PDCWG Report to ROS
Chair: Chad Mulholland, NRG
Vice Chair: Jimmy Jackson, CPS
ROS
May 2nd, 2019

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-1 FMEs & IMFR
    2 FMEs in the month of March
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 4/10/19
  Southern Cross DC Tie – Directive 3, DC Tie Ramping Limits
    Topic introduction – PDC members provided ERCOT with initial questions
  ERCOT Frequency Response Modeling – RRS Analysis
  Discussion of LCRA FR analysis, FR Model verification, RRS bid/offer limits for NPRR 863, RRS limits in Protocols (20% of HSL)
    Several related topics discussed collectively – All sub-topics deal with the analysis methods and accuracy in how ERCOT analyzes interconnection frequency response (and RRS needs)
    PDCWG will draft an action item to identify the scope of a mini-project to identify how ERCOT models can be improved (via stakeholder inputs and industry experts)
    Some concerns and issues have been raised by both ERCOT and other stakeholders regarding the concept of creating a new RRS bid/offer cap in association with NPRR 863 – analysis & discussion ongoing
    Protocols currently only apply the limit of 20% of HSL for RRS bids on thermal units, and at present, only thermal and hydro units are qualified for RRS, but NPRR 863 may change this – sort of an open question for PDCWG to be aware of – technologies and the market are changing rapidly – more changes are likely coming to this element of the Protocols and the market
  Regulation & Frequency Control Reports

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There was 2 FME in February
  3/2/2019 03:18:53
    Loss of 1224 MW
    Interconnection Frequency Response: 1,275 MW/0.1 Hz
    2 of 42 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    4 of 42 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  3/21/2019 13:39:57
    Loss of 650 MW
    Interconnection Frequency Response: 803 MW/0.1 Hz
    5 of 29 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    4 of 29 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Interconnection Minimum Frequency Response (IMFR) Performance
IMFR Performance currently 1030.94 MW/0.1Hz
Frequency Response Obligation (FRO): 381 MW/0.1 Hz

## Slide 7: Frequency Control Report
March 2019

## Slide 8: CPS1 Performance

## Slide 9: RMS1 Performance of ERCOT Frequency

## Slide 10: Frequency Profile Analysis

## Slide 11: Time Error Corrections

## Slide 12: ERCOT Total Energy

## Slide 13: ERCOT Total Energy from Wind Generation

## Slide 14: ERCOT % Energy from Wind Generation

## Slide 15
Questions?