## Slide 1
Load Frequency Control (LFC) Changes Under RTC
Sai Moorty
Principal, Market Design and Analysis
April 30, 2019

## Slide 2: Overview
Identify scenario(s) where LFC changes are appropriate
Real-Time Market timeline
Regulation related calculations in RTC
Explanation of Updated Desired Base Point (UDBP) and Regulation Deployment
Two extreme scenarios and potential solutions
  Scenario 1: Reg-Up responsibility change to zero
  Scenario 2: Reg-Up responsibility change >0
Summary and next steps
Problem Statement:
“Identify changes, if any, required for LFC under RTC.”

## Slide 3: Load Frequency Control (LFC) Under RTC
So far, ERCOT has identified a couple of scenarios under RTC where changes to LFC may be appropriate.
Under RTC, based on economics and system conditions, Regulation Up/Down Awards to a Resource can be different for each RTC run (which normally runs every 5 minutes).
The change of Regulation responsibility across the hour boundary that occurs in today’s Real-Time Market (RTM) is similar to what would occur under RTC.
Two extreme scenarios are presented and proposals for changes to LFC presented.
QSE 2
_
+
f60
factual
-10*Bias
Filter
Regulation
Required
UDBP Calc
Allocate
Reg
QSE 1
QSE n
Raw ACE
Filt. ACE
LFC block diagram
Telemetry Snapshot
Base Points

## Slide 4: Real-Time Market Timeline – Today
SCED Run
Time
11:00:05
11:00:20
SCED Inputs@11:00:05
Telemetry Snapshot
Offers
GTBD
11:00:24
LFC
LFC Inputs@11:00:20
Telemetry Snapshot
Frequency
Base Points
SCED Base Points, LMP Binding till next SCED Run
11:05:05
SCED Run
Less impacted by renewable Resource variability
Less impacted by forecast errors (load, wind, solar)
Ability to economically dispatch RRS and still meet reliability timelines
Uniquely different than other ISOs where Base Points and LMPs are binding starting at least 5 minutes into the future
4s

## Slide 5: Real-Time Market Timeline – No Change Under RTC
RTC Run
Takeaway: Retain benefits of current timeline. RTC does not change the timeline (i.e., LMP, Base Point, AS Awards, MCPCs are binding immediately after RTC is finished).
Time
11:00:05
11:00:20
RTC Inputs@11:00:05
Telemetry Snapshot
Offers
GTBD
11:00:24
LFC
LFC Inputs@11:00:20
Telemetry Snapshot
Frequency
Base Points
RTC Base Points, LMP, AS Awards, AS MCPCs
Binding till next RTC Run
11:05:05
RTC Run
4s

## Slide 6: Real-Time Market Timeline (Cont.)
QSE systems receiving Reg. Awards and Reg. instructions
  Takeaway: QSEs control systems can get Regulation Awards and Regulation instructions simultaneously. In extreme cases, they may get Regulation instructions before receiving Regulation Awards (orders of milli-seconds to seconds latency between receiving Reg. Awards and Reg. instructions).
Market DB
EMS AppDB
SCADA DB
SCED
LFC/RLC
Interface
6
QSE 2
QSE 1
QSE n
ICCP
MIS DB
QSE 2
QSE 1
QSE n
XML I/F
Interface

## Slide 7: Regulation Related Calculations Under RTC
RLC : Limit calculation
  )
RTC constraints related to Regulation
    Using Normal Ramp Rate Down allows Reg-Up Recall
    Using Normal Ramp Rate Up allows Reg-Dn Recall
    RTC dynamically allocates Normal Ramp Rate Up between Base Point and Reg-Up Award based on economics
    RTC dynamically allocates Normal Ramp Rate Down between Base Point and Reg-Down Award based on economics

## Slide 8: Updated Desired Base Point (UDBP) and Regulation Deployment
UDBP is a Resource-specific tracking signal for Resources to ramp to new Base Points
  It is a 4-minute ramp starting from previous Base Point and ending at the next Base Point
  The UDBP ramp is calculated whenever new results of SCED are input to LFC (normally every 5 minutes)
Every LFC cycle (4 seconds), ERCOT sends QSEs the Resource-specific UDBP and QSE portfolio level Regulation instruction
QSE system distributes its QSE portfolio level Regulation instruction among its Resources providing Regulation (Resource Regulation instruction)
The Resource control system MW Set-Point for any instant of time (t) is :
Resource Set-Point(t) = UDBP(t)+ Resource Regulation Instruction(t)
SCED@11:00
Time
UDBP
11:00
11:05
BP@SCED 10:55
BP@SCED 11:00
ERCOT LFC tracks the expected response of a Resource using its UDBP(t) and Resource allocation of QSE Regulation Instruction(t) based on Resource Participation Factors telemetered by QSE

## Slide 9: Scenario 1: RegUp Responsibility Change to Zero
HSL
Time
11:00
11:05
HASL
HSL, HASL
RegUp
Resp.
Time
11:00
11:05
HSL
HASL
HSL, HASL
RegUp
Resp.
BP@SCED 10:55
Time
11:00
11:05
HSL
HASL
HSL, HASL
RegUp
Resp.
BP@SCED 10:55
UDBP
Time
11:00
11:05
HSL
HASL
HSL, HASL
RegUp
Resp.
BP@SCED 10:55
UDBP
RegUp Instruction
Time
11:00
11:05
HSL
HASL
HSL, HASL
RegUp
Resp.
BP@SCED 10:55
RegUp Instruction
UDBP
MW output (tracking UDBP + Reg Instruction)
Time
11:00
11:05
HSL
HASL
HSL, HASL
RegUp
Resp.
BP@SCED 10:55
RegUp Instruction
SCED@11:00
BP@SCED 11:00
UDBP
MW output (tracking UDBP + Reg Instruction)
Time
11:00
11:05
HSL
HASL
HSL, HASL
RegUp
Resp.
BP@SCED 10:55
RegUp Instruction
SCED@11:00
BP@SCED 11:00
UDBP
SCED@11:00
RegUp Instruction
MW output (tracking UDBP + Reg Instruction)
Time
UDBP
11:00
11:05
HSL
HASL
RegUp
Resp.
BP@SCED 11:00
HSL, HASL
BP@SCED 10:55
After SCED@11:00, MW output ramps down and then increases as the Resource control system tracks UDBP
Unnecessary MW movement
  Potential loss of revenue
Issue is that the starting point of UDBP ramp is previous Base Point and does not consider the fact that with Regulation instruction, the Resource’s expected MW could be far away from previous Base Point

## Slide 10: Potential Changes Under Consideration For RTC
Replace Resource-specific tracking signal UDBP with “Updated Desired Gen (UDG)”
UDG for a Resource from ERCOT LFC (@time t):
UDG(t) = Base Ramp(t) + Resource Specific Regulation Instruction(t)
UDBP(t) and UDG(t) are same for Resource with no Regulation responsibility
RegUp Instruction
Time
UDBP
11:00
11:05
HSL
RegUp
Resp.
BP@ 10:55
BP@ 11:00
UDG
What is Base Ramp?
Like UDBP:
  Is a 4-minute ramp to a new Base Point
  Ending MW point of Base Ramp is the next RTC Base Point
Differs from UDBP only in the starting MW point for the ramp
  Starting MW point of Base Ramp is the expected MW output from Resource at the time new Base Points are received. It is the sum of:
    Previous RTC Base Point
    Last LFC (t-1) Regulation-Up/Down instruction
A new Base Ramp is computed whenever new Base Points from RTC are input to LFC

## Slide 11: Scenario 2: RegUp Responsibility Change > Zero
After SCED@11:00, LFC Regulation instruction not feasible because, when added to current MW output, it exceeds the HSL limit of Resource
Eventually, Resource able to provide requested Regulation instruction as MW output ramps down to next Base Point
Issue is that in determining the QSE level Regulation instruction, does not consider available room (HSL-expected MW output) for Reg-Up and (expected MW – LSL) for Reg-Dn
Time
11:00
11:05
HSL,HASL
HASL
RegUp
Resp.
HSL
Time
11:00
11:05
HSL,HASL
HASL
RegUp
Resp.
HSL
BP@SCED 10:55
Time
11:00
11:05
HSL,HASL
HASL
RegUp
Resp.
HSL
BP@SCED 10:55
UDBP
Time
11:00
11:05
HASL
RegUp
Resp.
HSL
BP@SCED 10:55
MW output (tracking UDBP + Reg Instruction)
HSL,HASL
UDBP
Time
11:00
11:05
HSL,HASL
HASL
RegUp
Resp.
HSL
BP@SCED 10:55
UDBP
MW output (tracking UDBP + Reg Instruction)
SCED@11:00
BP@SCED 11:00
Time
11:00
11:05
HSL,HASL
HASL
RegUp
Resp.
HSL
MW output (tracking UDBP + Reg Instruction)
SCED@11:00
BP@SCED 11:00
UDBP
BP@SCED 10:55
Time
11:00
11:05
HSL,HASL
HASL
RegUp
Resp.
HSL
SCED@11:00
BP@SCED 11:00
UDBP
RegUp Instruction
BP@SCED 10:55
Time
11:00
11:05
HSL,HASL
HASL
RegUp
Resp.
HSL
SCED@11:00
BP@SCED 11:00
UDBP
MW output (tracking UDBP + Reg Instruction)
RegUp Instruction
BP@SCED 10:55

## Slide 12: Potential Changes Under Consideration For RTC (Cont.)
Some combination of:
  Modify process in LFC that allocates system wide Regulation instruction to Resources by:
    Accounting for available room on Resources (HSL(t) - Base Ramp(t)) for Reg-Up and (Base Ramp (t) – LSL) for Reg-Dn
    After above step, reallocate any remaining Regulation Instructions on Resources still having available room
  Adjust Regulation instruction considering UDG, or reset Regulation instruction to zero when LFC gets new outputs from RTC (Base Points, AS Awards)
Time
Base Ramp
11:00
11:05
HSL
RegUp
Resp..
BP@ 11:00
UDG
BP 10:55
RegUp Instruction

## Slide 13: Reg-Up Award Change and its Deployment Under RTC
SCED@11:00
RegUp Instruction
MW output (tracking UDBP + Reg Instruction)
Time
UDBP
11:00
11:05
HSL
HASL
RegUp
Resp.
RTC@11:00
RegUp Instruction
MW output (tracking UDG)
Time
Base Ramp
11:00
11:05
HSL
RegUp
Award
BP@SCED 10:55
BP@SCED 11:00
HSL, HASL
BP@RTC 10:55
BP@RTC 11:00
UDG
MW output
(tracking UDG)
RegUp Instruction
Time
UDBP
11:00
11:05
HSL,HASL
HASL
MW output (tracking UDBP + Reg Instruction)
SCED@11:00
RegUp
Resp.
HASL
HSL
BP@SCED 10:55
BP@SCED 11:00
RegUp Instruction
Time
Base Ramp
11:00
11:05
HSL
RTC@11:00
RegUp
Award.
BP@RTC 10:55
BP@RTC 11:00
UDG
Scenario 2: RegUp Responsibility Change > Zero
Scenario 1: Reg-Up Responsibility Change to Zero

## Slide 14: Summary and Next Steps
Summary
Presented proposal on changes to LFC
  Change ERCOT LFC Regulation instruction from QSE portfolio level to Resource-specific
Next steps
ERCOT will continue examining additional scenarios and refine proposal to change LFC
Feedback requested on additional scenarios to examine
Feedback requested on proposed changes to LFC or other alternative proposals

## Slide 15
Discussion