| NPRR Number |  | NPRR Title | Modifications to Instrument Transformer Testing Schedule & Removal of Reference to Fiber Optic Current Transformers |
| --- | --- | --- | --- |
| Date Posted |  |  |  |
| Requested Resolution |  | Normal or Urgent, and justification for Urgent status |  |
| Nodal Protocol Sections Requiring Revision |  | 10.6.1.2 TSP and DSP Testing Requirements for EPS Metering Facilities |  |
| Related Documents Requiring Revision/Related Revision Requests |  | Settlment Metering Operating Guide 7.2 Application 7.5.2 Current Transformers 7.5.3.4 Rated Output (Fiber Optic System) 7.5.3.6 Accuracy and Burden (Fiber Optic System) |  |
| Revision Description |  | Incorporate changes in ANSI Standards, increase test schedule for CCVTs tested in the last quarter of a year and remove references to fiber optic instrument transformers. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | Synchronization of Protocol language with changes in published ANSI C12 metering standards in regards to instrument transformer testing. Adapting the testing schedule of CCVT’s to recognize the TDSP business process of ordering CCVTs in the last quarter of the prior year. This change modifies the test cycle for CCVTs tested in the last quarter of the prior year to acknowledge preplanning by the TDSP to have the units on hand so they can take advantage of any outages scheduled early in the year for sites due for CCVT testing. Removal of reference to fiber optic instrument transformers. There are currently no fiber optic instrument transformers being utilized for EPS metering installations. This technology was initially deployed at some installations but has since been replaced with high accuracy wirewound instrument transformers. The use of high accuracy wirewound instrument transfomrers provides needed accuracy ranges without the added complexity of the electronics associated with the fiber optic systems. This NPRR and the companion SMOGRR removes the option to install fiber optic instrument transformers. |  |

| Sponsor |  |
| --- | --- |
| Name |  |
| E-mail Address |  |
| Company |  |
| Phone Number |  |
| Cell Number |  |
| Market Segment |  |

| Market Rules Staff Contact |  |
| --- | --- |
| Name |  |
| E-Mail Address |  |
| Phone Number |  |

Proposed Protocol Language Revision

- 10.6	Auditing and Testing of Metering Facilities

- 10.6.1	EPS Meter Entities

- 10.6.1.1	ERCOT Requirement for Audits and Tests

(1)	ERCOT shall have the right to audit any EPS Metering Facility that it considers necessary or to request and witness a test carried out by a TSP or DSP EPS Meter Inspector.

- 10.6.1.2	TSP and DSP Testing Requirements for EPS Metering Facilities

(1)	At a minimum, the TSP and DSP EPS Meter Inspector shall conduct testing of EPS Meters on an annual basis, within the same month of each year as the previous year’s test.  Metering Facilities used in the ERCOT system for settlement must be tested pursuant to the TSP or DSP tariffs, the SMOG and these Protocols.

(2)	Instrument transformers used in settlement metering circuits must be tested per the ANSI C12.1 guidelines:

(a)	Magnetic Instrument Transformers do not require periodic testing;

(b)	Coupling Capacitor Voltage Transformers (CCVTs) shall be tested for accuracy

(i) by the end of the year  in which the fifth anniversary of the previous test occurs; or

(ii) by the end of the year in which the sixth anniversary of the previous test occurs, if the previous test occurred during the fourth quarter of the year.

(3)	ERCOT may determine that periodic testing of CCVTs is not required once these devices have been proven to be stable.  If the devices have shown themselves to be unstable, ERCOT may discontinue the use of these devices for settlement purposes.