## Slide 1
ERCOT Frequency Control Report
April 2019
ERCOT
Operations Planning
PDCWG | May 8, 2019

## Slide 2: Summary of April 2019
CPS1: 170.77%
Current CPS1 12-Month Rolling Average: 174.21%
3 BAAL Exceedances
5 hourly CPS1 scores below 100%
BAAL-003 Events have updated through 2018
2018 BAAL-003 FRM Performance: -895.19
2019 RMS1 Statistics
  Mean: 15.51 mHz
  Min: 13.05 mHz
  Max: 18.46 mHz
Energy Statistics
  Total Energy: 26,814,321 MWh
  Wind Energy: 7,163,342 MWh
  Percent Energy from Wind Generation: 26.71%
Minimum System Inertia
  Mean: 169,542
  Max: 204,174 on April 24th
  Min: 138,843 on April 3rd

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
April-19 CPS1 (%): 170.77
Notes: Outliers:
4/4/2019 18:00 96.94%
Large expected generation deviation. Unit ramped down 600 MW within the hour, not following BP. Solar decreased by 500 MW in 15 minutes. Reg Up exhausted the majority of the hour
4/6/2019 02:00 6.09%
Wind ramped by >4,000 MW throughout the hour. Large expected generation deviation. A few units not following BP. Reg Up exhausted the majority of the hour
4/18/2019 17:00 98.84%
Several wind units tripped off due to a system disturbance. Non-conforming load increased by 100 MW. Solar ramped-down by 200 MW within the hour. Reg Up exhausted the majority of the hour
4/18/2019 18:00 88.79%
Wind ramped down by >2,000 MW throughout the hour. Solar ramped down by >500 MW throughout the hour. Reg up exhausted majority of the hour.
4/27/2019 02:00 98.52%
Wind ramped down by <2,500 MW throughout the hour. Large expected generation deviation. Unit ramps back faster than BP when below LSL. A few units no following BP. Reg Up exhausted the majority of the hour.

## Slide 5: BAAL Exceedances & Violations
There were 3 BAAL exceedances in April
  April 11, 2019
    Unit Trip at 03:37:56
    Loss of 664 MW
    Less than 59.91 Hz for 1 minute
  April 25, 2019
    Unit Trip at 11:20:04
    Loss of 555 MW
    Less than 59.91 Hz for 2 minutes

## Slide 6: 15-Minute Average CPS1%
April-19 CPS1 (%): 170.77

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 174.21%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes: Mean is 15.28 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 15.51 mHz
Min: 13.05 mHz
Max: 18.46 mHz

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2018 BAL-003 Selected Events

## Slide 19: Op. Year 2018 BAL-003 FRM Performance
Notes: FRM Changed to -895 from -759 on April 1st at 10 AM

## Slide 20: Op. Year 2018 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 21: Op. Year 2018 BAL-003 FRM Performance - Update

## Slide 22: ERCOT Energy Statistics

## Slide 23: Total Energy
Notes: 26,814,321 MWh

## Slide 24: Total Energy from Wind Generation
Notes: 7,163,342 MWh

## Slide 25: % Energy from Wind Generation
Notes: 26.71%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 128,759 MW*s on 11/3/2018.
Previous Minimum was 130,014 MW*s on 10/27/2017. This was also our record wind day.
Data:
Mean: 169,542
Max: 204,174 on April 24th
Min: 138,843 on April 3rd

## Slide 28: Questions?
Thank you!