## Slide 1
2019 RTP Update
May 2019
RPG Meeting

## Slide 2: Agenda
2019 RTP case information/assumption update
Status update
Next steps
Appendix
  2019 RTP Final Load Levels

## Slide 3: 2019 RTP Status Update
Initial reliability start cases were posted on MIS Secure on March 15, 2019.
Load forecast values for economic analysis were posted on MIS Secure on April 8, 2019.
Currently in progress:
  Single-event (N-1) reliability analysis
  Economic analysis

## Slide 4: 2019 RTP Assumptions Update (1/2)
Resources that have been publicly announced to shut down will be taken offline
  Decker Units 1 and 2 (announced April 17, 20191)
  Oklaunion (announced September 20, 20182)
  ERCOT will submit a PGRR to codify this assumption
Horse Hollow switching considerations?
1 https://www.austintexas.gov/edims/document.cfm?id=317748
2 https://aep.com/Assets/docs/investors/AnnualReportsProxies/docs/18annrep/2018AnnualReportAppendixAtoProxy.pdf

## Slide 5: 2019 RTP Assumptions Update (2/2)
DC tie curtailment will be utilized before proposing transmission upgrades for P0, P1, P2.1, and P7 contingencies
There is a new stability interface limit that will be modeled for the Lobo-North Edinburg 345 kV line

## Slide 6: 2019 RTP Gas Price Assumption
EIA AEO scenario (2018 $) | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Reference case | $3.03 | $3.08 | $3.00 | $3.00 | $3.13 | $3.31 | $3.53 | $3.60
High economic growth | $3.01 | $3.08 | $3.01 | $3.02 | $3.16 | $3.37 | $3.59 | $3.67
Low economic growth | $3.03 | $3.07 | $2.99 | $2.96 | $3.06 | $3.24 | $3.43 | $3.55
High oil and gas resource and technology | $2.83 | $2.76 | $2.60 | $2.55 | $2.61 | $2.74 | $2.90 | $2.99

## Slide 7: Next Steps
Case conditioning
Initial start cases, and contingency list ready
Set 1 (P1, P7),
Set 2 (P2, P4, P5) contingency analysis for the base cases
Economic analysis
2018 RTP Report
Blue box: complete
Yellow box: in progress
Short circuit study
Long-lead time equipment study
Sensitivity analysis
Other Reliability Studies
Multiple element outage and cascading analyses
P3, P6.2 contingency analysis for the base cases

## Slide 8
Send comments to:
Ping.Yan@ercot.com

## Slide 9: 2019 RTP Load Level – less self-served and losses (final)
Year | Coast | East | Far West | North | North Central | South Central | Southern | West
2021 | 23,828 | 2,884 | 5,690 | 2,221 | 26,723 | 13,658 | 6,349 | 2,318
2022 | 24,343 | 2,903 | 5,865 | 2,229 | 27,026 | 13,906 | 6,583 | 2,381
2024 | 24,907 | 2,966 | 6,151 | 2,246 | 27,636 | 14,399 | 7,332 | 2,507
2025 | 25,087 | 3,002 | 6,256 | 2,254 | 27,939 | 14,639 | 7,707 | 2,568
 | Bounded (based on 5% threshold)
 | 90th percentile
 | SSWG Forecast
 | Adjusted based on ERCOT review of TSP information
All load levels in MW

## Slide 10: SSWG load v/s ERCOT 90/10 (less losses and self served)
Chart: Coast Load (MW)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025
SSWG | 24437.26 | 24617.03 | 24909.44 | 25088.89
ERCOT 90/10 | 22695.2548 | 23185.512 | 24167 | 24651.9926
2019 RTP Load | 23828.07 | 24343.04 | 24907.28 | 25086.74
Chart: East Load (MW)
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025
SSWG | 2884.56 | 2902.64 | 2966.09 | 3002.34
ERCOT 90/10 | 2850.4463 | 2881.0897 | 2932.2234 | 2956.4811
2019 RTP Load | 2884.48 | 2902.73 | 2966.12 | 3002.28
Chart: North Load (MW)
| 2021 | 2022 | 2024 | 2025
SSWG | 2055.26 | 2063.56 | 2083.07 | 2099.94
ERCOT 90/10 | 2217.7565 | 2226.0293 | 2242.6162 | 2250.7003
2019 RTP Load | 2220.77 | 2229.02 | 2245.56 | 2253.67
Chart: North Central Load (MW)
| 2021 | 2022 | 2024 | 2025
SSWG | 25543.47 | 25871.79 | 26648.3 | 27061.37
ERCOT 90/10 | 26719.1115 | 27022.4195 | 27632.7174 | 27935.364
2019 RTP Load | 26722.66 | 27025.69 | 27636.4 | 27938.9

## Slide 11: SSWG load v/s ERCOT 90/10 (less losses and self served)
Chart: Far West Load (MW)
| 2021 | 2022 | 2024 | 2025
SSWG | 6050 | 6261.26 | 6510.43 | 6625.33
ERCOT 90/10 | 4509.9809 | 4772.3381 | 5288.7089 | 5544.8848
2019 RTP Load | 5689.98 | 5865.39 | 6151.43 | 6256.29
Chart: West Load (MW)
| 2021 | 2022 | 2024 | 2025
SSWG | 2209.63 | 2220.7 | 2244.21 | 2267.32
ERCOT 90/10 | 2277.2747 | 2339.2864 | 2464.0565 | 2524.6803
2019 RTP Load | 2318.35 | 2380.77 | 2506.59 | 2567.63
Chart: South Central Load (MW)
| 2021 | 2022 | 2024 | 2025
SSWG | 13545.13 | 13801.63 | 14074.45 | 14440.11
ERCOT 90/10 | 13658.1521 | 13905.9633 | 14398.6301 | 14638.6037
2019 RTP Load | 13658.16 | 13905.98 | 14398.72 | 14638.7
Chart: South Load (MW)
| 2021 | 2022 | 2024 | 2025
SSWG | 6490.32 | 6724.95 | 7203.68 | 7302.1
ERCOT 90/10 | 6325.4117 | 6505.2859 | 6879.3877 | 7066.1466
2019 RTP Load | 6348.59 | 6583.16 | 7331.83 | 7707.27