## Slide 1: Geomagnetically Induced Current (GIC) Impacts on Protective Relay Performance
Karl Zimmerman and Derrick Haas Schweitzer Engineering Laboratories, Inc.

## Slide 2: Overview
Goal of protection
GIC mechanism
History of GIC impact on protection
Overview of relay filtering
Impact of GIC on CTs
Impact of GIC on relay applications
GIC monitoring

## Slide 3: Goals of Protective Relaying During GIC Events
Maintain security, dependability, speed, and sensitivity for faults
Detect and monitor transformers for overheating resulting from half-cycle saturation

## Slide 4: GIC Mechanism
Solar storms → ionospheric current (iION) → magnetic field (bION) → geoelectric EMF (eGEO) → current flow (iGIC)
GIC circulates between grounding points and is added to system frequency current (iSYS)

## Slide 5: GIC Characteristics
Changes very slowly – quasi-dc
Produces up to 300 A primary, measured in neutral CT
Splits equally between phases (100 A per phase)
GIC measured in transformer neutral in Finland during geomagnetic storm on March 24, 1991

## Slide 6: Events Attributed to GIC
March 1989 – most impact in Quebec and eastern North America
  Seven tripped static VAR compensators (SVCs) due to elevated harmonics
  Multiple line relay operations
  Severe voltage fluctuations
  Elevated transformer heating at several utilities
October 2003 – capacitor trip, several line operations, and elevated heating

## Slide 7: Factors Affecting Protection
Relay filtering in digital relays
Performance of CTs
Protection algorithms

## Slide 8: Relay Filtering Overview
Removes “noise” and retains signal of interest
Varies based on
  Relay vintage
  Manufacturer
  Application
SEL-T400L Time-Domain Line Protection
SEL-21 Distance Relay Fault Locator

## Slide 9: Line Relay Principles Filtering Requirements
Algorithm | Phasor-Based | Differential Equations | Traveling Waves
Spectrum | 50 / 60 Hz | 1 kHz | 100 kHz
Filtering |  |  | 
Sampling | 16–32 samples / cycle | 8 kHz | 1 MHz
Line theory |  |  | 
Operating time | ~1 cycle | A few milliseconds | 1 ms

## Slide 10: Generator Protection Filtering

## Slide 11: Examples of Phasor-Based Relay Filtering
1984 Line Relay Design
4 samples per cycle, CAL filter

## Slide 12: Examples of Phasor-Based Relay Filtering
1996 Line Relay Design
16 samples per cycle, cosine filter

## Slide 13: CT Saturated and Unsaturated Unfiltered Secondary Current
Actual system fault, taken from IEEE PSRC report,
“Distance Element Response to Distorted Waveforms”

## Slide 14: CT Saturated and Unsaturated Output of Cosine Filter

## Slide 15: Current Magnitude and Angle of Saturated vs. Unsaturated CT Magnitude

## Slide 16: Current Magnitude and Angle of Saturated vs. Unsaturated CT Phase Angle

## Slide 17: Low-Frequency GIC Produces Minimal Error
Lab simulation – (0.2 Hz, 150 A) + (60 Hz, 150 A)
Yellow solid line – primary ratio current
Blue dashed line – filtered secondary current

## Slide 18: CTs “Don’t Like” DC
Exponentially decaying component in fault current eventually saturates CT
Protection must be secure and dependable during saturation conditions
  Differential elements (line, transformer, and bus) must manage dissimilar CT performance
  Line protection (21, 67, 87L) must handle CT errors
DC can produce CT thermal stress

## Slide 19: Transient CT Performance Without GIC
C10, 150:5 CT – fault current of 1.6 kA rms with pre-fault load of 150 A rms and no GIC current

## Slide 20: Transient CT Performance With GIC
C10, 150:5 CT – fault current of 1.6 kA rms with pre-fault load of 150 A rms and 15 A dc GIC current

## Slide 21: Impact of GIC Similar to Residual Flux
Vs = Saturation Voltage

## Slide 22: CT Performance Questions
Do CTs “like” dc? No, CTs cannot measure dc
Do CTs “mind” dc? A little; standing dc impacts accuracy of ac measurement
What is the GIC impact on protection CTs? Very short-lived; similar to residual flux
Is protection affected? In general, impact is minimal

## Slide 23: GIC Induces Half-Cycle Saturation in Transformer Core

## Slide 24: Harmonic Content During Half-Cycle Saturation
Normal
GIC
1.6
1.4
1.2
1.0
0.8
0.6
0.4
0.2
0
1
2
3
4
5
6
7
Harmonic
Magnitude

## Slide 25: Line Distance and Overcurrent Protection
Conventional or time-delayed elements may slightly underreach due to steady-state CT errors
High-speed elements may slightly underreach or be delayed for substantial CT saturation in first half-cycle of fault current
Dependability and security must be maintained during GIC events

## Slide 26: Line Current Differential Protection
Include protection algorithms (percentage differential, Alpha Plane) to manage steady-state CT errors
Include algorithms to provide security for fast relay elements for transient CT errors (slow elements are secure since transient errors are short-lived)
Maintain dependability and security during GIC events

## Slide 27: Transformer Differential Protection (87)
Include percentage restraint to cope with steady-state CT saturation
Include algorithms that safeguard against misoperations and failures to operate

## Slide 28: Transformer Differential Protection (87) Algorithms
External fault detection prevents operation for external faults (improves security)
Harmonic blocking, harmonic restraint, and waveshape recognition prevent operation on inrush (improves security)
Harmonic blocking (by itself) should be avoided in theory, but in reality, magnitude of GIC is very small compared to fault current
Unrestrained element detects high-current internal faults (improves dependability)

## Slide 29: 5th Harmonic Blocking
Is typically applied to block tripping for overexcited transformer
In theory, could block differential element if fault occurs during GIC event, but in reality, fault currents are much higher than GICs
Should be applied where needed (e.g., on certain GSUs)

## Slide 30: Monitoring GIC
Presence of harmonics is used
Wide-area monitoring is applied
Direct measurement requires transducers
Logic can alarm based on multiple measurements

## Slide 31: Conclusions
Impact of GIC on protection presents challenges but is minimal overall
Digital filtering removes dc and harmonics
GIC impacts CT performance, but it is short-lived
Most relay algorithms are resilient to impact of GICs, just as they are resilient to other factors (e.g., magnetizing inrush, CT errors due to saturation)

## Slide 32: References
“Effects of Geomagnetic Disturbances on the North American Bulk Power System” (NERC report)
“Do CTs Like DC? Performance of Current Transformers With Geomagnetically Induced Currents” (IEEE technical paper)
“Distance Element Response to Distorted Waveforms” (IEEE PSRC report)
“Geomagnetically Induced Currents: Detection, Protection, and Mitigation” (SEL application guide)

## Slide 33: Questions?