| NOGRR Number | 189 | NOGRR Title | Align Disturbance Monitoring Requirements Deadline with NERC Reliability Standard PRC-002-2 |
| --- | --- | --- | --- |
| Date of Decision |  | May 22, 2019 |  |
| Action |  | Approved |  |
| Timeline |  | Normal |  |
| Effective Date |  | June 1, 2019 |  |
| Priority and Rank Assigned |  | Not applicable |  |
| Nodal Operating Guide Sections Requiring Revision |  | 6.1.2.2, Fault Recording and Sequence of Events Recording Equipment Location Requirements 6.1.3.2, Location Requirements |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) aligns the Nodal Operating Guides with North American Electric Reliability Corporation (NERC) Reliability Standard PRC-002-2 – Disturbance Monitoring and Reporting Requirements. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | The current Nodal Operating Guide uses a deadline for requirements that does not reflect what is required by NERC Reliability Standard PRC-002-2. This revision request relieves Transmission Facility owners from needing to meet a deadline that is a year sooner than the standard requires. |  |
| ROS Decision |  | On 4/4/19, ROS unanimously voted to recommend approval of NOGRR189 as submitted. All Market Segments were present for the vote. On 5/2/19, ROS unanimously voted to endorse and forward to TAC the 4/4/19 ROS Report and the Impact Analysis for NOGRR189. All Market Segments were present for the vote. |  |
| Summary of ROS Discussion |  | On 4/4/19, there was no discussion. On 5/2/19, there was no discussion. |  |
| TAC Decision |  | On 5/22/19, TAC unanimously voted to approve NOGRR189 as recommended by ROS in the 5/2/19 ROS Report as revised by TAC. All Market Segments were present for the vote. |  |
| Summary of TAC Discussion |  | On 5/22/19, participants reviewed the 5/17/19 Tenaska comments and the 5/21/19 ERCOT comments agreeing that applicability issues raised in the 5/17/19 Tenaska comments can be vetted separate from NOGRR189. |  |

| Sponsor |  |
| --- | --- |
| Name | Micheal Davis, Jr. on behalf of the System Protection Working Group (SPWG) |
| E-mail Address | micheal.davisjr@centerpointenergy.com |
| Company | CenterPoint Energy – Houston Electric, LLC |
| Phone Number | 713-207-4155 |
| Cell Number | 334-804-8757 |
| Market Segment | Not Applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Phillip Bracy |
| E-Mail Address | phillip.bracy@ercot.com |
| Phone Number | 512-248-6917 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Tenaska 051719 | Proposed clarifications that NERC Reliability Standard PRC-002-2 applies only to Transmission Facility and Generation Resource owners that are required to be registered with NERC |
| ERCOT 052119 | Expressed support for NOGRR189 as submitted and endorsed by ROS on 5/2/19, suggested the clarifications proposed in the 5/17/19 Tenaska comments be vetted through the stakeholder process in a separate NOGRR |

Proposed Guide Language Revision

6.1.2.2	Fault Recording and Sequence of Events Recording Equipment Location Requirements

(1)	The location criteria listed below applies to Transmission Facilities operated at or above 100 kV.  The Facility owner(s), whether a Transmission Facility owner or Generation Resource owner, shall install fault recording and sequence of events recording equipment at the following Facilities, at a minimum:

(a)	Locations identified by the Transmission Facility owner utilizing the methodology in Section 8, Attachment M, Selecting Buses for Capturing Sequence of Events Recording and Fault Recording Data;

(b)	Additional locations selected at the Transmission Facility owner’s discretion, utilizing the methodology in Section 8, Attachment M;

(c)	ERCOT mandatory fault recording and sequence of events recording locations operating at or above 100kV, as defined below.

(i)	Interconnections with non-ERCOT Control Areas (i.e., outside ERCOT Region);

(ii)	Substations where electrical transfers of equipment can be made between the ERCOT Control Area and non-ERCOT Control Area;

(iii)	At all generating station switchyards connected to the ERCOT System with an aggregated generating capacity above 100 MVA or at the remote line terminals of each generating station switchyard.

(2)	Facility owners shall install the fault recording and sequence of events recording equipment identified in paragraph (1) above such that half of the identified facilities have the associated equipment installed by July 1, 2020, and all of the identified facilities by July 1, 2022.

- 6.1.3.2	Location Requirements

(1)	ERCOT shall identify Transmission Elements operated at or above 100kV for which dynamic disturbance recording data is required, including the following:.

(a)	Generation Resource(s) with:

(i)	Gross individual nameplate rating greater than or equal to 500 MVA; or

(ii)	Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA;

(b)	Any one Transmission Element that is part of a stability (angular or voltage) related system operating limit;

(c)	Each terminal of a high-voltage, direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current portion of the converter;

(d)	One or more Transmission Elements that are part of an Interconnection Reliability Operating Limit (IROL); and

(e)	Any one Transmission Element within a major voltage sensitive area as defined by an area with an in-service Under-Voltage Load Shedding (UVLS) program.

(2)	ERCOT shall identify a minimum dynamic disturbance recording coverage, inclusive of those Transmission Elements identified above, of a least:

(a)	One Transmission Element; and

(b)	One Transmission Element per 3,000 MW of ERCOT’s historical simultaneous peak Demand.

(3)	Facility owners identified under paragraphs (1) or (2) above shall install dynamic disturbance recording equipment such that half of the identified facilities have the associated equipment installed by July 1, 2020, and all of the identified facilities by July 1, 2022.

(4)	The Facility owner(s), whether a Transmission Facility owner or new Generation Resource owner, shall install phasor measurement recording equipment at the following Facilities.

(a)	Flexible AC transmission system devices configured to actively control steady-state voltage or power transfer capability, operated at or above 100kV, and energized after July 1, 2015;

(b)	Within 18 months after receiving written notice from ERCOT, a Transmission Facility identified by ERCOT associated with each published generic transmission constraint as deemed necessary by ERCOT; and

(c)	New generating Facilities over 20 MVA aggregated at a single site placed into service after January 1, 2017.

[NOGRR177: Insert item (d) below upon system implementation of NPRR857:] (d) New Direct Current Ties (DC Ties) placed into service after January 1, 2019.