ERCOT Nodal Operating Guide

- Table of Contents

- June 1, 2019

1	Overview	1

1.1	Document Purpose	1

1.2	Document Relationship	2

1.3	Process for Nodal Operating Guide Revision	2

1.3.1 Introduction	2

1.3.2 Submission of a Nodal Operating Guide Revision Request	3

1.3.3 Nodal Operating Guide Revision Procedure	4

1.3.4 Urgent Requests	11

1.3.5 Nodal Operating Guide Revision Implementation	12

1.4	Definitions	12

1.5	Operational Training	20

1.5.1 System Operator Training Objectives	20

1.5.2 System Operator Training Requirements	20

1.5.3 ERCOT Operations Training Seminar	21

1.5.4 ERCOT Severe Weather Drill	21

1.5.5 Training Practices	22

1.5.6 ERCOT Operator Certification Program	22

2	System Operations and Control Requirements	1

2.1	Operational Duties	1

2.2	System Monitoring and Control	3

2.2.1 Overview	3

2.2.2 Security Criteria	4

2.2.3 Response to Transient Voltage Disturbance	5

2.2.4 Load Frequency Control	5

2.2.5 Automatic Voltage Regulators	6

2.2.6 Power System Stabilizers	8

2.2.7 Turbine Speed Governors	10

2.2.8 Performance/Disturbance/Compliance Analysis	11

2.2.9 Time Error and Time Synchronization	12

2.2.10 Generation Resource Response Time Requirements	12

2.3	Ancillary Services	14

2.3.1 Responsive Reserve	17

2.3.2 Non-Spinning Reserve Service	19

2.4	Outage Coordination	20

2.5	Reliability Unit Commitment	20

2.5.1 Criteria for Removing Contingencies from the RUC Analyses	20

2.6	Requirements for Under-Frequency Relaying	20

2.6.1 Automatic Firm Load Shedding	20

2.6.2 Generators	22

2.7	System Voltage Profile and Operational Voltage Control	23

2.7.1 Introduction	23

2.7.2 Maintaining Voltage Profile	23

2.7.3 Real-Time Operational Voltage Control	25

2.7.4 Special Consideration for Nuclear Power Plants	30

2.7.5 Parameters for Standard Reactor and Capacitor Switching Plan	30

2.7.6 Unit Dispatch Beyond the Corrected Unit Reactive Limit or Unit Reactive Limit	31

2.8	Operation of Direct Current Ties	31

2.8.1 Inadvertent Energy Management	32

2.9	Voltage Ride-Through Requirements For Generation Resources	32

2.9.1 Additional Voltage Ride-Through Requirements for Wind-Powered Generation

Resources	34

3 	ERCOT AND MARKET PARTICIPANT RESPONSIBILITIES	1

3.1	System Control Interfaces with ERCOT	1

3.1.1 Introduction	1

3.1.2 Compliance with Dispatch Instructions	1

3.1.3 Dispatch Instructions	1

3.2	Qualified Scheduling Entities	3

3.2.1 Operating Obligations	3

3.2.2 Changes in Resource Status	4

3.2.3 Regulatory Required Incident and Disturbance Reports	4

3.2.4 Ancillary Service Qualification and Testing Program	5

3.3	Resource Entities	6

3.3.1 Unit Capability Requirements	8

3.3.2 Unit Reactive Capability Requirements	8

3.3.3 Resource Entity Responsibilities for Equipment Ratings	11

3.4	Load Resource Testing Requirement	12

3.5	ERCOT Implementation	12

3.6	Transmission Service Providers	13

3.7  	Transmission Operators	13

3.7.1 Transmission Owner Responsibility for a Vegetation Management Program	15

3.7.2 Trasmission Service Provider Responsibilities for Equipment Ratings	16

3.8  	Requirements for Reporting Sabotage Information	16

4	Emergency Operations	2

4.1	Introduction	2

4.2	Communication Under Emergency Conditions	2

4.2.1 Operating Condition Notice	2

4.2.2 Advisory	3

4.2.3 Watch	5

4.2.4 Emergency Notice	6

4.3	Operation to Maintain Transmission System Security	7

4.3.1 Real-Time and Short Term Planning	7

4.4	Block Load Transfers between ERCOT and Non-ERCOT System	7

4.5	Energy Emergency Alert (EEA)	8

4.5.1 General	8

4.5.2 Operating Procedures	8

4.5.3 Implementation	10

4.5.3.1 General Procedures Prior to EEA Operations	 12

4.5.3.2 General Procedures During to EEA Operations	12

4.5.3.3 EEA Levels	13

4.5.3.4 Load Shed Obligation………………………………………………………………..19

4.5.3.5 EEA Termination…………………………………………...……………………….19

4.6	Black Start Service	20

4.6.1 Principles	20

4.6.2 Strategies	21

4.6.3 Priorities	22

4.6.4 Responsibilities	22

4.6.5 Black Start Emergency Back Up Communication Facilities Criteria	26

4.7	Geomagnetic Disturbance Operating Plan	26

4.7.1 Monitoring and Dissemination of Space Weather Information	26

4.7.2 Development and Submission of TO GMD Operating Procedures or Processes	26

4.7.3 ERCOT’s GMD Operating Plan and ERCOT Review of TO GMD Operating Procedures or Processes	27

4.8	Responsive Reserve Service During Scarcity Conditions…………………………………………28

4.8.1 Responsive Reserve Service Manual Deployment…………………………………………..28

4.8.2 Responsive Reserve Service Manual Recall…….……….………….………………………28

5	Network Operations Modeling Requirements	1

5.1	System Modeling Information	1

6	Disturbance Monitoring and System Protection	1

6.1	Disturbance Monitoring Requirements	1

6.1.1 Introduction	1

6.1.2 Fault Recording and Sequence of Events Recording Equipment	1

6.1.3 Phasor Measurement Recording Equipment Including Dynamic Disturbance Recording Equipment	4

6.1.4 Maintenance and Testing Requirements	7

6.1.5 Equipment Reporting Requirements	7

6.1.6 Review Process	8

6.2	System Protective Relaying	8

6.2.1 Introduction	8

6.2.2 Design and Operating Requirements for ERCOT System Facilities	9

6.2.3 Performance Analysis Requirements for ERCOT System Facilities	10

6.2.4 Protective Relay System Failure Response	12

6.2.5 Maintenance and Testing Requirements for ERCOT System Facilities	13

6.2.6 Requirements and Recommendations for ERCOT System Facilities	14

7	Telemetry and Communication	1

7.1  	ERCOT Wide Area Network	2

7.1.1 ERCOT Responsibilities	3

7.1.2 QSE and TSP Responsibilities	3

7.1.3 Joint Responsibilities (Maintenance and Restoration)	10

7.2	ERCOT ICCP Interface	12

7.2.1 Quality Codes	12

7.2.2 Metric of Availability	12

7.3	Telemetry	12

7.3.1 Data from ERCOT to QSEs	14

7.3.2 Data from ERCOT to TSP	14

7.3.3 Data from QSEs and TSPs to ERCOT	14

7.3.4 Resolving Real-Time Data Issues that affect ERCOT Network Security Analysis	16

7.3.5 TSP and QSE Telemetry Restoration	17

7.3.6 General Telemetry Performance Criterion..............................................................................17

7.4	Calibration and Testing of Telemetry Responsibilities	17

7.5	Competitive Renewable Energy Zone Circuits and Stations	17

8	Attachments

8A Black Start Info

8B Protection System Misoperation Report

8C Turbine Governor Speed Tests

8D Seasonal Unit Net Real Power Capability Verification

8E Black Start Plan Template

8F Seasonal Hydro Responsive Reserve Net Capability Verification

8G Load Resource Tests

8H Unit Alternative Fuel Capability

8I Black Start Resource Availabiity Test Form

8J Initial and Sustained Measurements for Primary Frequency Response

8K Remedial Action Scheme (RAS) Template

8L Emergency Operations Plan

8M Selecting Buses for Capturing Sequence of Events Recording and Fault Recording Data

9	Monitoring Programs	1

9.1	QSE and Resource Monitoring Program	1

9.1.1 Testing	1

9.1.2 Reactive Testing for Generation Resources	2

9.1.3 Real-Time Data	2

9.1.4 Compliance with Valid Dispatch Instructions	3

9.1.5 Resource Facilities Network Operations Model Update Implementation Monitor	3

9.1.6 Resource Outage Reporting	4

9.1.7 Backup Control for Resource Energy Deployment	4

9.1.8 Qualified Staffing Requirement	5

9.1.9 Automatic Voltage Regulator (AVR)	5

9.1.10 Current Operating Plan Metrics for QSEs	6

9.2	TSP Monitoring Program	6

9.2.1 Intentionally Left Blank	6

9.2.2 Real-Time Data Monitor	7

9.2.3 Transmission Outage Reporting	7

9.2.4  Transmission Service Provider (TSP) Network Operations Model Update Implementation Monitor	8

9.2.5  Backup Control for TSPs	9

9.3	ERCOT Monitoring Program	9

9.3.1 Transmission Control	9

9.3.2 System and Resource Control	12

9.3.3 Forecasting	13

9.3.4 System Operating Constraints	14

9.3.5 Network Operations Model Update Implementation Statistics	15

9.3.6 Reserved	15

9.3.7 ERCOT Black Start Plan	15

9.3.8 Computer and Communication Systems Real-Time Availability and Systems Security	15

9.3.9 Voltage and Reactive Control Performance Monitoring	16

9.4	Ancillary Services Monitoring Program	16

9.4.1 Hydro Responsive Testing	16

9.4.2 Annual Black Start Plan Receipt Confirmation Report	17

9.4.3 Resource-Specific Responsive Reserve Performance	17

9.4.4 Constant Frequency Control	17

9.4.5 Resource-specific Non-Spinning Reserve	18

10	Market Data Transparency	1

10.1	Direct Current Tie Outage Information	1

11	Constraint Management Plans and Remedial Action Schemes	1

11.1	Introduction	1

11.2	Remedial Action Schemes	1

11.2.1 Reporting of RAS Operations	5

11.3	Automatic Mitigation Plans	6

11.4	Remedial Action Plan	7

11.4.1 Remedial Action Plan Process	9

11.5	Mitigation Plan	9

11.6	Pre-Contingency Action Plans	10

11.6.1 Pre-Contingency Action Plan Process	11

11.7	Temporary Outage Action Plan	11