## Ancillary Services, NERC Standard and Aggregated AS Capability

- Reliability Unit Commitment (RUC) is a backstop mechanism to commit generator if and when market commitment is insufficient.

- RUC will continue to ensure adequate capacity for Real-Time to meet energy and Ancillary Service (AS) needs.  For AS, the RUC engine will check whether or not sufficient AS capability is available for RTC to award in Real-Time.

- The current deferral process under which ERCOT Operators review recommendations from the RUC optimization and make commitment instruction decisions will remain in place.

| ERCOT Ancillary Service | NERC Standard | Quantities (2019 | Notes |
| --- | --- | --- | --- |
| Responsive Reserve (RRS) | NERC BAL-003 | 2,300 MW - 3,016 MW | Plan for sufficient frequency responsive reserve such that instantaneous loss of 2,750 MW will not trigger first stage of UFLS set at 59.30 Hz. |
| Regulation Up Service (Reg-Up) | NERC BAL-001 | 142 MW - 669 MW | CPS1> 100% |
| Regulation Down Service (Reg-Down) | NERC BAL-001 | 148 MW - 604 MW | CPS1> 100% |
| Non-Spinning Reserve (Non-Spin) | NERC BAL-002 | 22 MW- 1,442 MW | Non-Spin reserve can be used to restore contingency reserve service |
| ERCOT Contingency Reserve Service (ECRS) | NERC BAL-002 | 509 MW - 1,353 MW | Restore RRS and recover Frequency within 15 minutes |
| NERC BAL-002 Standard also requires ERCOT to maintain minimum 1,375 MW of Contingency Reserve including ability to restore Contingency Reserve within 90 minutes if deployed. |  |  |  |

Non-Spin quantities reflects implementation of ECRS.

ECRS is a new AS product and is expected to be implemented no earlier than January 1, 2022.