| NPRR Number | 945 | NPRR Title | Net Metering Requirements |
| --- | --- | --- | --- |
| Date of Decision |  | June 13, 2019 |  |
| Action |  | Tabled |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | To be determined |  |
| Priority and Rank Assigned |  | To be determined |  |
| Nodal Protocol Sections Requiring Revision |  | 10.3.2.3, Generation Netting for ERCOT-Polled Settlement Meters |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) clarifies when an All-Inclusive Generation Resource may be netted against Load for Settlement purposes. This NPRR confirms that an All-Inclusive Generation Resource and Load may be netted behind a single Point of Interconnection (POI) as long as the Load is otherwise being lawfully served without use of the ERCOT Transmission Grid. The Public Utility Regulatory Act (PURA) and existing Public Utility Commission of Texas (PUCT) rules and precedent legally determine when and how Load can be served without using the ERCOT Transmission Grid. This NPRR does not change or expand that existing law, but invokes it to limit generation netting behind a common POI. This NPRR also sunsets provisions that previously allowed netting for sites with multiple interconnections, which were meant to address historical interconnection arrangements that are no longer common practice. Sites that are being netted today under these provisions are grandfathered in the NPRR. Finally, this NPRR addresses outdated references to “Generation” or “generation” that should refer to All-Inclusive Generation Resources under today’s Resource definitions. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | This NPRR resolves ambiguity and disagreement between ERCOT and stakeholders regarding metering requests and provides regulatory certainty in metering requirements for netting generation and Load, which will facilitate new generation development and interconnections. |  |
| Credit Work Group Review |  | To be determined |  |
| PRS Decision |  | On 6/13/19, PRS voted unanimously to table NPRR945. All Market Segments were present for the vote. |  |
| Summary of PRS Discussion |  | On 6/13/19, the sponsor requested NPRR945 be tabled to allow time for comments to replace the term “All-Inclusive Generation Resource” due to ERCOT Board approval of NPRR921, RTF-2 Elimination of the Terms All-Inclusive Generation Resource and All-Inclusive Resource. Participants discussed whether NPRR945 should be referred to WMS for review of standby charges, and noted that additional comments to NPRR945 are anticipated. |  |

| Sponsor |  |
| --- | --- |
| Name | Katie Coleman |
| E-mail Address | Katie.Coleman@tklaw.com |
| Company | Thompson & Knight LLP, for Texas Industrial Energy Consumers (TIEC) |
| Phone Number | (512) 404-6705 |
| Cell Number | (512) 773-0394 |
| Market Segment | Not Applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brittney Albracht |
| E-Mail Address | Brittney.Albracht@ercot.com |
| Phone Number | (512) 225-7027 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Market Rules Notes

Please note that the following NPRR(s) also propose revisions to the following section(s):

- NPRR917, Nodal Pricing for Settlement Only Distribution Generators (SODGs) and Settlement Only Transmission Generators (SOTGs)

  - Section 10.3.2.3

Proposed Protocol Language Revision

10.3.2.3	Generation Netting for ERCOT-Polled Settlement Meters

(1)	All-Inclusive Generation Resource(s) may be netted against Load(s) pursuant to the requirements of paragraph (2) below, if the service is otherwise lawful under the Public Utility Regulatory Act (PURA) and applicable Public Utility Commission of Texas (PUCT) rules.  For purposes of netting under this Section, Interval Data Recorders (IDRs) must be installed at the POI(s) to determine generator output and/or Load usage.  In intervals where generation output exceeds Load, the net shall be settled as generation.  In intervals where Load exceeds generation output, the net shall be settled as Load, and subject to any applicable Load shared charges and credits.  ERCOT’s approval of net metering under this Section is not an independent verification that such service complies with PURA or PUCT rules.

(2)	For Settlement purposes, netting an All-Inclusive Generation Resource and Load is not allowed except under one of the following conditions:

(a)	Single POI, including sites with a POI where a single substation connects to multiple Transmission Service Provider (TSP) facilities, with delivered and received metering data channels;

(b)	Multiple POIs where the Loads and All-Inclusive Generation Resource are electrically connected to a common switchyard, as defined in paragraph (6) below.  In addition, there must be sufficient generator capacity to serve all plant Loads for netting to occur, and the POIs must have been netted prior to December 31, 2019;

(c)	A Qualifying Facility (QF) with multiple POIs, where the QF is selling energy to a thermal host from an All-Inclusive Generation Resource, may net the Load meters of the thermal host with the QF’s generation meters when the Load and All-Inclusive Generation Resource are electrically connected to a common switchyard, and where the POIs were netted prior to December 31, 2019.  In instances in which Load is served by new on-site generation through a common switchyard, the TSP or DSP may install monitoring equipment necessary for measuring Load to determine stranded cost charges, if any are applicable, as determined under PURA and applicable PUCT rules.  For purposes of this Section, new on-site generation has the meaning as contained in Public Utility Regulatory Act, Tex. Util. Code Ann. §§ 39.252 and 39.262(k) (Vernon 1998 & Supp. 2007) (PURA); or

(d)	For All-Inclusive Generation Resources and/or Load with flow-through on a private, contiguous transmission system (not included in a TSP’s or DSP’s rate base) and in a configuration existing as of October 1, 2000, the meters at the interconnections with the ERCOT Transmission Grid may be netted for Settlement purposes.  When the net is a Load, the metered interconnection points must be assigned to the same Load Zone and Unaccounted for Energy (UFE) zone.

(3)	For generation sites with EPS Meters that measure Wholesale Storage Load (WSL), each energy storage Load Resource must be separately metered from all other Loads and generation:

(a)	For configurations where the WSL is not at the POI, it must be separately metered behind a single POI metering point; and

(b)	WSL for a compressed air energy storage Load Resource is exempt from the requirement to be electrically connected to a common switchyard, as defined in paragraph (6) below.

(4)	ERCOT shall maintain descriptions of the Metering Facilities of all common switchyards that contain multiple POIs of Loads (ESI IDs) and generation meters (EPS).  The description is limited to identifying the Entities within a common switchyard and a simplified diagram showing the metering configuration of all Supervisory Control and Data Acquisition (SCADA) and Settlement Metering points.

(5)	All Load(s) included in the netting arrangement for an EPS Metering Facility shall only be electrically connected to the ERCOT Transmission Grid through the EPS metering point(s) for such Facility.  Such Loads shall not be electrically connected to the ERCOT Transmission Grid through electrical connections that are not metered by the EPS metering point(s) for the Facility.

(6)	For purposes of this Section, a common switchyard is defined as an electric substation Facility where the POI for Load and an All-Inclusive Generation Resource(s) are located at the same Facility but where the interconnection points are physically not greater than 400 yards apart.  The physical connections of the Load to its POI and the All-Inclusive Generation Resource to its POI cannot be Facilities that have been placed in a TSP’s or DSP’s rate base.