## Slide 1
Dynamic Model Improvement Proposal
Resource Integration Workshop
June 20, 2019

## Slide 2: Background
2019 ROS Goal: Continuously improve dynamic modeling processes
April 25, 2019, Inverter Based Resource Workshop
Previous discussions
  http://www.ercot.com/content/wcm/key_documents_lists/165178/20._Dynamic_Models_Overview_ROS_Meeting_March_2019.pdf
  http://www.ercot.com/content/wcm/key_documents_lists/167487/RIW_Recap_of_IBR_Issues_and_NextSteps.pdf

## Slide 3: Proposal for Dynamic Data and Model Improvement
Goals:
  Identify the model issues as early as possible, even before submission of the model to ERCOT/TSPs
  Reduce/eliminate the iterations of model troubleshooting and updates among REs/developers, TSPs, vendors, and ERCOT
  Allow the study engineers focus more on the studies, not model issues.
Details are described in the following slides.

## Slide 4: Dynamic Data and Model Submittal (Unchanged)
The Facility owner shall provide appropriate dynamics data to ERCOT and the interconnecting TSP including the data for a planned or existing Facility at various stages of the project.
  Full Interconnection (Planning with conceptual technology and vendor)
  QSA (Planning with finalized technology and vendor)
  Commissioning (as built)
  Periodical model validation and update (Operations)
Dynamic data includes a model with parameters that accurately represent the dynamics of the device
  The model shall be compatible with the current version of the model software

## Slide 5: Enhance Requirements for UDM
If a user defined model (UDM) is provided, the data shall also include the following:
  Technical description, including detailed control block diagrams and design logics, of characteristics of the model
  A user manual to describe the procedure of using the model in the software, all parameters of settings and variables, limitations of the model adequacy and usability in the software.
The UDM must be in Dynamic Linked Library (DLL) format
Potential for stricter enforcement of other UDM guidelines developed by Dynamic Model Task Force (DMTF)

## Slide 6: New Requirements to Ensure Submitted Model is Study-Ready
Submitted model must be accompanied by test results that demonstrate acceptable performance of the models in the model software
  Flat Start Test (no disturbance test)
  Voltage Step Change Test
  Frequency Step Change Test
  Voltage Ride Through Test
  Short Circuit Ratio Test
These model quality tests are to be performed by the entity submitting the model

## Slide 7: Model Quality Test – Flat Start
Purpose: to demonstrate the model(s) are compatible with the software and maintain stable response under no disturbance condition

## Slide 8: Model Quality Test – Voltage Step Change Test
Purpose: to demonstrate the model(s) can appropriately respond to voltage step changes, providing voltage support under normal operating conditions

## Slide 9: Model Quality Test – Frequency Step Change Test
Purpose: to demonstrate the model(s) can appropriately respond to frequency step changes, providing frequency support under a normal operating conditions

## Slide 10: Model Quality Test – Voltage Ride Through Test
Purpose: to demonstrate the model(s) can ride through a voltage excursion and respond appropriately to under and over voltage conditions

## Slide 11: Model Quality Test – Short Circuit Ratio Test
Purpose: to demonstrate the model(s) responses under different system strength conditions

## Slide 12: Next Step
Provide your comments to ERCOT by July 5, 2019.
  John Schmall, John.Schmall@ercot.com
Prepare and submit a PGRR