## Slide 1
June 24, 2019
WMWG Meeting
ERCOT Operations
Current Telemetry Validations in Resource Limit Calculator

## Slide 2: RLC Overview
Protocol Section 6.5.7.2 drives the calculations and monitoring built into RLC today.
RLC executes every 4 seconds.
RLC uses telemetry from QSEs to compute limits such as HDL, LDL, HASL and LASL. These limits are then sent to MMS/SCED.
  RLC runs several sanity checks against input telemetry data and weeds out inconsistencies in telemetered data using pre-established business rules.
Resource Limit Calculator
Ancillary Service Calcs.
ex. HASL, LASL
Resource Limit Calcs.
ex. SURAMP, SDRAMP, HDL, LDL
GTBD Calculation
Includes PLDRR, PWRR
Telemetry from QSE via SCADA/ICCP
Dispatch Data from MMS
Operator Initiated Data
SCED BP/LMP Data To QSE via SCADA/ICCP
Calculated and telemetered Data To MMS/SCED
Data For Settlements
Data For Reports and Compliance
Other Calcs.
Ex. SCED Trigger following RRS release

## Slide 3: Telemetry Validations in RLC – SCADA Quality Check
RLC has logic to handle telemetry SCADA data qualities of Good, Suspect, Manual Replaced and Uninitialized. (“intra”-telemetry checks)
If any resource specific telemetry data (excluding ramp rate related telemetries) from QSE has Suspect quality, then RLC retains the last good value which had telemetered quality Good and does not consider the new value of the telemetry that has Suspect data quality
  Thus, if bad data quality is detected for LSL or HSL, the last good value would be used.
If Suspect data quality is detected for resource ramp rates, then effective ramp rate is computed using the resource specific ramp rate curves as submitted in the resource’s Market Manager Generation Resource Parameters or Resource Asset Registration Form (RARF) if there was no Market Manager Submission

## Slide 4: Telemetry Validations in RLC – Data Check
The second layer of validation in RLC are is to ensuring telemetry data consistency across two or more resource specific telemetries. (“inter” telemetry checks)
Following conditions will trigger RLC to set HDL=LDL=MW
  HSL < LSL
  LSL < 0
  HSL <= 0 AND resource status is not one of the offline statuses*
  HSL < Non-Spin Responsibility and resource status is OFFNS
  (HSL – LSL) < Sum of AS Responsibility and resource status is not OFFNS
  Resource Status has invalid value but good SCADA quality
Following conditions will trigger RLC to ramp down a resource per its SCED down ramp rate
  MW > 0.9*LSL and resource status is one of (OFF, OUT, EMR, OFFNS, EMRSWGR)
Alarms are issued in case of most of the telemetry checks outlined above.
* offline statuses = NA, OUT, OFFNA, OFF, EMR, OFFQS, EMRSWGR OR FRRSUP

## Slide 5: Resource Limit Calculator Logic Example 1
- Telemetered HSL = 0
Input Values | MW or #
High Sustainable Limit (HSL) | 0
Power Output (MW) | 500
Normal Down Ramp Rate | 200
Resource Status Code | 3 (ON)
Sum of AS Responsibilities | 0
Low Sustained Limit (LSL) | 0
Calculated Values | MW
High Dispatch Limit (HDL) | 500
Low Dispatch Limit (LDL) | 500
500
- LDL=HDL=BP=500
- Actual Unit Capacity
Output Values | MW or #
Base Point (BP) | 500
Overridden Resource Status Code | 
RLC Logic Applicable:
  Following conditions will trigger RLC to set HDL=LDL=MW
    HSL<=0 AND resource status is not one of the offline statuses*
EMS Alarms triggered:
  Alert: TEL HSL BELOW 0
550

## Slide 6: Resource Limit Calculator Logic Example 2
- Telemetered HSL = 0
Input Values | MW or #
High Sustainable Limit (HSL) | 0
Power Output (MW) | 500
Normal Down Ramp Rate | 200
Resource Status Code | 13 (OFF)
Sum of AS Responsibilities | 0
Low Sustained Limit (LSL) | 0
Calculated Values | MW
High Dispatch Limit (HDL) | 300
Low Dispatch Limit (LDL) | 300
Output Values | MW or #
Base Point (BP) | 300
Overridden Resource Status Code | 0 (NA)
500
- LDL=HDL=BP=300
- Actual Unit Capacity
RLC Logic Applicable:
  Following conditions will trigger RLC to ramp down a resource per its SCED down ramp rate
    MW>0.9*LSL and resource status is one of (OFF, OUT, EMR, OFFNS, EMRSWGR)
EMS Alarms triggered:
  Alert: TEL HSL BELOW 0
  Alert: INCONSIST RST AND MW
550

## Slide 7: Resource Limit Calculator Logic Example 3
- Telemetered HSL = 0
Input Values | MW or #
High Sustainable Limit (HSL) | 0
Power Output (MW) | 500
Normal Down Ramp Rate | 200
Resource Status Code | 0 (NA)
Sum of AS Responsibilities | 0
Low Sustained Limit (LSL) | 0
Calculated Values | MW
High Dispatch Limit (HDL) | 300
Low Dispatch Limit (LDL) | 300
Output Values | MW or #
Base Point (BP) | 300
Overridden Resource Status Code | 
500
- LDL=HDL=BP=300
- Actual Unit Capacity
RLC Logic Applicable:
  HDL formula. No Special logic
EMS Alarms triggered:
  Alert: TEL HSL BELOW 0
  Alert: INCONSIST RST AND MW
550

## Slide 8
Discussion

## Slide 9: Resource Specific Telemetry From/To QSE* - Current
To QSE |  | 
Unit Related |  | A/S Related
Base Point (BP) |  | Non-Spin Deployed (NDPL)
Locational Marginal Price (LMP) |  | RRS Deployed (RDPL) [NCLR]
Curtailment (SBBH) |  | 
SCCT Status (SCCT) |  | 
Updated Desired BP (UDBP) |  | 
From QSE |  |  | 
Unit Related |  |  | A/S Related
High/Low Sustained Limits (HSL, LSL) | AVR Status (AVR) |  | FRRS Up/Down Participation Factor (FUPF, FDPF)
High/Low Emergency Limit (HEL, LEL) | Dynamically Scheduled Resource Schedule (DSRS)[Gen] |  | FRRS Up/Down Responsibility (FURS, FDRS)
Normal Up/Down Ramp Rate (NURR, NDRR) | Lower/Raise Block Status (LBST, RBST) [Gen] |  | Regulation Up/Down Participation Factor (RUPF, RDPF)
Emergency Up/Down Ramp Rates (EURR, EDRR) | PSS Status (PSS) |  | Regulation Up/Down Responsibility (RURS, RDRS)
Net MW/MVAR (MW (aka NPF for CCP), MVAR) | POI kV Measurement/Target (KVM, KVT) |  | Responsive Reserve Responsibility/Schedule (RRRS, RRSC)
Gross MW/MVAR (GMW, GMV) | Scheduled Power Consumption (SPC, SPC2) [CLR] |  | High Set Under Frequency Relay (HSUF) [NCLR]
Resource Status (RST) | Storage Resource Charge/Discharge Data (MXCP, MXDP, MXOD, SOC) |  | Non-Spin Responsibility/Schedule (NSRS, NSSC)
CCP Config No (CCC) | IRR MET Data (DEG, IRAD, MPH, PRES, PTMP, TEMP) |  | 
Non Frequency Responsive Capacity (NFRC) | IRR Turbine/Panel Availability (NTOF, NTON, NTUN) |  | 
Load Resource Breaker Status (LRCB) [NCLR] |  |  | 
Max/Low Power Consumption (MPC, LPC) [CLR, NCLR] |  |  | 
*Refer to the ERCOT Nodal ICCP Communications Handbook
http://www.ercot.com/services/rq/re

## Slide 10: Generation Resource Status Codes
  NA (0)
  OUT (11)
  OFFNS (12)
  OFF (13)
  EMR (14)
  OFFQS (19)
  EMRSWGR (20)
  ONRUC (1)
  ONREG (2)
  ON (3)
  ONDSR (4)
  ONOS (5)
  ONOSREG (6)
  ONDSRREG (7)
  ONTEST (8)
  ONEMR (9)
  ONRR (10)
  SHUTDOWN (15)
  STARTUP (16)
  FRRSUP (17)
  ONOPTOUT (18)
*Refer to the ERCOT Nodal ICCP Communications Handbook Section 4.5.2 for more information on Resource Status Codes: http://www.ercot.com/services/rq/re

## Slide 11: RLC Ancillary Service and Dispatch Calculations
HASL
HDL
LDL
LASL

## Slide 12: Alarms from RLC
RLC issues the followings alarms as a result of its data sanity checks.
  HSL – LSL is < AS RESP
  Alert: TEL HSL BELOW 0
  Alert: TEL LSL BELOW 0
  Alert: INVALID HSL SUM
  Alert: SCEDURR BELOW 0
  Alert: INVALID CC CONFIG
  Alert: SUSPECT TEL HDL=LDL=MW
  Alert: INVALID TEL HSL OR LSL
  Alert: INVALID TEL RST
  Alert: INCONSIST RST AND MW