## Slide 1
SCED/RTC Frequency and Failure Events
ERCOT
July 12, 2019

## Slide 2: SCED/RTC Events
SCED/RTC Re-run sub 5 minute triggers
SCED/RTC Failure
Principle language

## Slide 3: SCED/RTC Re-run sub 5 minute triggers
SCED/RTC automatically re-runs when either of the below events occur
  RRS is deployed for 60 seconds (frequency below 59.91)
  Frequency below 59.95 for 2 consecutive minutes
Operator will continue to have the ability to re-run SCED to control frequency if needed.
We expect the same functionality will remain following RTC implementation

## Slide 4: RTC Failure Process Today vs. Tomorrow
When RTC fails, Emergency Base Points (EBP), specifically EBP offsets will be used to control frequency and recall deployed Regulation.
  A/S Awards prior to the RTC failure will continue to hold till RTC failure is resolved.
Special Conditions
  If a resource carrying A/S trips offline, ERCOT does not seek to replace the A/S.
  If system conditions tighten and PRC reduces, ERCOT may bring additional generation resource(s) online.
  If LFC fails, a QSE may be placed in Constant Frequency Control mode.
When SCED fails, Emergency Base Points (EBP), specifically EBP offsets are used to control frequency and recall deployed Regulation.
Special Conditions
  If a resource carrying A/S trips offline, ERCOT does not seek to replace the A/S.
  If system conditions tighten and PRC reduces, ERCOT may bring additional generation resource(s) online.
  If LFC fails, a QSE may be placed in Constant Frequency Control mode.
Reference: Real-Time Operating Procedure
RTC Failure
SCED Failure

## Slide 5: Impacts of RTC Failure
Current SCED Failure Definition:
  SCED process is not able to reach a solution. (6.5.9.2)
Dispatch Instruction under different scenarios:
ERCOT holds prices (SPPs, Meter prices and MCPCs) from last good SCED run prior to a failure through intervals covering the first 15-minutes of successful SCED process execution following the failure. (NPRR 696)
This does not include the scenarios when ERCOT perform regular system maintenance activities, during which ERCOT intentionally does not run SCED for a short period of time.
These rules will be the same for RTC.
Scenario | Dispatch Instruction
Long SCED interval, EBP flag is not on | QSEs follow the last SCED Base Points
EBP flag is on without offset | QSEs follow the last SCED Base Points received before EBP flag is on.
EBP flag is on with offset | QSEs follow Emergency Base Points

## Slide 6: Principle language 1.5
RTC will continue to have the ability for the Real-Time optimization (i.e., RTC) to be executed off-cycle, manually or automatically, between regularly scheduled 5-minute executions.
The processes and procedures during a SCED/RTC failure will remain the same: emergency base points and held prices (SPPs, Meter prices and MCPCs) through the 15 minute recovery period.