## Slide 1
ROS
May 6, 2019
ERCOT Operations Staff
Update on Unannounced Constant Frequency Control (CFC) Tests

## Slide 2: Operating Guide Section 2.2.4.3(2)
Since January 2018, ERCOT has conducted 5 unannounced CFC tests on 4 different QSEs.
  January 15, 2018
  April 17, 2018
  September 20, 2018
  April 9, 2019
  April 16, 2019
2.2.4.3 ERCOT Loss of AGC
ERCOT shall conduct unannounced testing to verify a QSE’s capability to operate in CFC mode. Only QSEs with at least 350 MW of spinning reserve room will be tested. QSEs shall be tested at least once every three years. At a time determined solely by ERCOT, ERCOT will direct the QSE to operate under CFC mode. Once instructed by ERCOT, the QSE will have five minutes to switch to CFC mode. The duration of this test shall be no more than 15 minutes. ERCOT shall maintain the list of QSEs that have successfully demonstrated their capability to operate in CFC mode.

## Slide 3: Lessons Learned
Through these tests several process changes and display updates were identified and implemented at ERCOT. For Ex.
  Displays were created in Load Frequency Control (LFC) to track QSE level details for purposes of CFC.
  Regulation reset added following completion of CFC test.
Process and Procedural Changes were also identified at the tested QSEs end. For ex.
  In some cases the frequency bias was incorrectly set which caused poor fleet performance during testing.
  In one case the tested QSE missed reassigning Regulation obligation to their fleet on the way out from the test.
Spinning reserve in case of some resources within a QSE’s fleet came from offline power augmentation like duct burners. This offline capacity was unavailable to the QSE for frequency control due to slower start-up time. Additional changes to ERCOT’s procedures may be needed to appropriately account for this offline capacity when evaluating QSE performance.

## Slide 4
Further Discussion