| NOGRR Number | 191 | NOGRR Title | Related to NPRR939, Modification to Load Resources Providing RRS to Maintain Minimum PRC on Generators During Scarcity Conditions |
| --- | --- | --- | --- |
| Date Posted |  | April 30, 2019 |  |
| Requested Resolution |  | Normal |  |
| Nodal Operating Guide Sections Requiring Revision |  | 4.8.1, Responsive Reserve Service Manual Deployment |  |
| Related Documents Requiring Revision/Related Revision Requests |  | Nodal Protocol Revision Request (NPRR) 939, Modification to Load Resources Providing RRS to Maintain Minimum PRC on Generators During Scarcity Conditions |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR), along with NPRR939, allows ERCOT to manually deploy Load Resources other than Controllable Load Resources providing Responsive Reserve (RRS) to maintain a minimum 500 MW of Physical Responsive Capability (PRC) reserves on Generation Resources to continuously balance the Demand with supply while maintaining the stable grid frequency for smaller disturbances. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | The current language dividing Load Resources providing RRS into just two groups may result in much larger manual deployment than needed. Under certain tight conditions, if Load Resources providing RRS were contributing up to 150% of their RRS Ancillary Service Resource Responsibilities towards PRC, then during those conditions there is a potential for ERCOT to have PRC as high as 2,700 MW all on Load Resources. |  |

| Sponsor |  |
| --- | --- |
| Name | Sandip Sharma |
| E-mail Address | sandip.sharma@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4298 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Phillip Bracy |
| E-Mail Address | Phillip.Bracy@ercot.com |
| Phone Number | 512-248-6917 |

Proposed Guide Language Revision

- 4.8.1	Responsive Reserve Service Manual Deployment

(1)	RRS for capacity may be manually deployed (HASL released) when the system approaches scarcity conditions so that the capacity reserved behind HASL will be released to Security-Constrained Economic Dispatch (SCED).

(a)	When HASL – (Gen + 5 minute load ramp) <= 200 MW, ERCOT may deploy the available RRS capacity from Generation Resources and Controllable Load Resources in 500 MW increments after all the available Non-Spinning Reserve (Non-Spin) service has been deployed and Resources have responded to any earlier deployments.

(b)	When HSL – (Gen + 5 minute load ramp) <= 500 MW, ERCOT may deploy Load Resources controlled by high-set under-frequency relays providing RRS.