## Slide 1
ERCOT Frequency Control Report
June 2019
ERCOT
Operations Planning
PDCWG | July 18th, 2019

## Slide 2: Summary of June 2019
CPS1: 174.62%
Current CPS1 12-Month Rolling Average: 174.28%
0 BAAL Exceedances
2 hourly CPS1 scores below 100%
BAAL-003 Events have updated through 2018
2018 BAAL-003 FRM Performance: -843.17
2019 RMS1 Statistics
  Mean: 15.07 mHz
  Min: 13.38 mHz
  Max: 17.94 mHz
Energy Statistics
  Total Energy: 35,157,820 MWh
  Wind Energy: 5,771,138 MWh
  Percent Energy from Wind Generation: 16.41%
Minimum System Inertia
  Mean: 255,097
  Max: 281,561 on Jun 19th
  Min: 195,835 on Jun 14th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Jun-19 CPS1 (%): 174.62
Notes: Outliers:
6/23/2019 13:00 64%
Large expected generation deviation from conventional and wind at the middle of the hour.
6/19/2019 19:00 84.%
Large expected generation deviation from conventional and wind at the beginning and the end of the hour.

## Slide 5: BAAL Exceedances & Violations
There were 0 BAAL exceedances in June

## Slide 6: 15-Minute Average CPS1%
Jun-19 CPS1 (%): 174.62

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 174.28%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes: Mean is 15.07 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 15.07 mHz
Min: 13.38 mHz
Max: 17.94 mHz

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2018 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2018 BAL-003 FRM Performance - Update

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 35,157,820 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 5,771,138 MWh

## Slide 23: % Energy from Wind Generation
Notes: 16.41%

## Slide 24: ERCOT System Inertia

## Slide 25: Daily Minimum System Inertia
Notes: Minimum Inertia = 128,759 MW*s on 11/3/2018.
Previous Minimum was 130,014 MW*s on 10/27/2017. This was also our record wind day.
Data:
Mean: 255,097
Max: 281,561 on Jun 19th
Min: 195,835 on Jun 14th

## Slide 26: Questions?
Thank you!