PRS Report

	NPRR Number
	939
	NPRR Title
	Modification to Load Resources Providing RRS to Maintain Minimum PRC on Generators During Scarcity Conditions

	Date of Decision
	July 17, 2019

	Action
	Recommended Approval

	Requested Resolution 
	Normal 

	Proposed Effective Date
	Upon system implementation

	Priority and Rank Assigned
	Priority – 2019; Rank – 2770 

	Nodal Protocol Sections Requiring Revision 
	6.5.9.4.2, EEA Levels

	Related Documents Requiring Revision/Related Revision Requests
	Nodal Operating Guide Revision Request (NOGRR) 191, Related to NPRR939, Modification to Load Resources Providing RRS to Maintain Minimum PRC on Generators During Scarcity Conditions
Nodal Operating Guide Section 4.5.3.3, EEA Levels

	Revision Description
	This Nodal Protocol Revision Request (NPRR) changes the current practice of ERCOT dividing Load Resources other than Controllable Load Resources providing Responsive Reserve (RRS) into two groups. Instead, ERCOT would create groups of 500 MW each. 

	Reason for Revision
	[image: image1.wmf]

  Addresses current operational issues.

[image: image2.wmf]

  Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board).

[image: image3.wmf]

X

  Market efficiencies or enhancements

[image: image4.wmf]

  Administrative

[image: image5.wmf]

  Regulatory requirements

[image: image6.wmf]

  Other:  (explain)

(please select all that apply)

	Business Case
	This NPRR would allow ERCOT to manually deploy Load Resources other than Controllable Load Resources providing RRS under the provisions of Nodal Operating Guide Section 4.8.1, Responsive Reserve Service Manual Deployment.  Under the current rules, Load Resources other than Controllable Load Resources can provide up to 60% of the total ERCOT RRS requirement and contribute up to 150% of their RRS Ancillary Service Resource Responsibility towards Physical Responsive Capability (PRC).  Dividing them into just two groups may result in much larger manual deployment than needed.  This revision will allow ERCOT to maintain at least 500 MW of PRC from Generation Resources when releasing RRS capacity to Security-Constrained Economic Dispatch (SCED) per Nodal Operating Guide Section 4.8.1.  

	Credit Work Group Review
	ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed NPRR939 and do not believe that it requires changes to credit monitoring activity or the calculation of liability.

	PRS Decision
	On 6/13/19, PRS unanimously voted to recommend approval of NPRR939 as submitted.  All Market Segments were present for the vote.

On 7/17/19, PRS unanimously voted to endorse and forward to TAC the 6/13/19 PRS Report and the Impact Analysis for NPRR939 with a recommended priority of 2019 and rank of 2770.  All Market Segments were present for the vote.

	Summary of PRS Discussion
	On 6/13/19, there was no discussion.
On 7/17/19, participants reviewed the Business Case and Impact Analysis for NPRR939.  ERCOT Staff restated the benefits of maintaining a minimum 500 MW of PRC from Generation Resources.


	Sponsor

	Name
	Sandip Sharma; Mark Patterson

	E-mail Address
	sandip.sharma@ercot.com; mark.patterson@ercot.com

	Company
	ERCOT

	Phone Number
	512-248-4298; 512-248-3912

	Cell Number
	

	Market Segment
	Not applicable


	Market Rules Staff Contact

	Name
	Phillip Bracy

	E-Mail Address
	Phillip.Bracy@ercot.com

	Phone Number
	512-248-6917


	Comments Received

	Comment Author
	Comment Summary

	None
	


	Market Rules Notes


Please note that the following NPRR(s) also propose revisions to the following section(s):

· NPRR937, Distribution Voltage Level Block Load Transfer (BLT) Deployment

· Section 6.5.9.4.2
	Proposed Protocol Language Revision


6.5.9.4.2

EEA Levels

(1)
ERCOT will declare an EEA Level 1 when PRC falls below 2,300 MW and is not projected to be recovered above 2,300 MW within 30 minutes without the use of the following actions that are prescribed for EEA Level 1: 

(a)
ERCOT shall take the following steps to maintain steady state system frequency near 60 Hz and maintain PRC above 1,750 MW:

(i)
Request available Generation Resources that can perform within the expected timeframe of the emergency to come On-Line by initiating manual HRUC or through Dispatch Instructions; 

(ii)
Use available DC Tie import capacity that is not already being used; 

(iii)
Issue a Dispatch Instruction for Resources to remain On-Line which, before start of emergency, were scheduled to come Off-Line; and

(iv)
At ERCOT’s discretion, deploy available contracted ERS-30 via an XML message followed by a VDI to the all-QSE Hotline.  The ERS-30 ramp period shall begin at the completion of the VDI.

(A)
If less than 500 MW of ERS-30 is available for deployment, ERCOT shall deploy it as a single block.  

(B)
If the amount of ERS-30 available for deployment equals or exceeds 500 MW, ERCOT, at its discretion, may deploy ERS-30 as a single block or by group designation.  ERCOT shall develop a random selection methodology for determining how to place ERS Resources in ERS-30 into groups, and shall describe the methodology in a document posted to the MIS Public Area.  Prior to the start of an ERS Contract Period for ERS-30, ERCOT shall notify QSEs representing ERS Resources in ERS-30 of their ERS Resources’ group assignments.

(C)
ERS-30 may be deployed at any time in a Settlement Interval.

(D)
Upon deployment, QSEs shall instruct their ERS Resources in ERS-30 to perform at contracted levels consistent with the criteria described in Section 8.1.3.1.4, Event Performance Criteria for Emergency Response Service Resources, until either ERCOT releases the ERS-30 deployment or the ERS-30 Resources have reached their maximum deployment time.  

(E)
ERCOT shall notify QSEs of the release of ERS-30 via an XML message followed by VDI to the all-QSE Hotline.  The VDI shall represent the official notice of ERS-30 release.  ERCOT may release ERS-30 as a block or by group designation. 

(F)
Upon release, an ERS Resource in ERS-30 shall return to a condition such that it is capable of meeting its ERS performance requirements as soon as practical, but no later than ten hours following the release.

(b)
QSEs shall:

(i)
Ensure COPs and telemetered HSLs are updated and reflect all Resource delays and limitations; and

(ii)
Suspend any ongoing ERCOT required Resource performing testing. 

(2)
ERCOT may declare an EEA Level 2 when the clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes.  ERCOT will declare an EEA Level 2 when PRC falls below 1,750 MW and is not projected to be recovered above 1,750 MW within 30 minutes without the use of the following actions that are prescribed for EEA Level 2: 

(a)
In addition to the measures associated with EEA Level 1, ERCOT shall take the following steps to maintain steady state system frequency at a minimum of 59.91 Hz and maintain PRC above 1,375 MW:

(i)
Instruct TSPs and DSPs or their agents to reduce Customer Load by using distribution voltage reduction measures, if deemed beneficial by the TSP, DSP, or their agents.

(ii)
Instruct TSPs and DSPs to implement any available Load management plans to reduce Customer Load.

(iii)
Instruct QSEs to deploy available contracted ERS-10 Resources, undeployed ERS-30 and/or deploy RRS supplied from Load Resources (controlled by high-set under-frequency relays).  ERCOT may deploy ERS-10, ERS-30, or RRS simultaneously or separately, and in any order.  ERCOT shall issue such Dispatch Instructions in accordance with the deployment methodologies described in paragraphs (iv) and (v) below and, if deploying ERS-30, the methodologies described in paragraph (1)(a)(iv) above. 

	[NPRR863:  Replace item (iii) above with the following upon system implementation:]

(iii)
Instruct QSEs to deploy available contracted ERS-10 Resources, undeployed ERS-30, and/or deploy ECRS or RRS (controlled by high-set under-frequency relays) supplied from Load Resources.  ERCOT may deploy ERS-10, ERS-30, ECRS, or RRS simultaneously or separately, and in any order.  ERCOT shall issue such Dispatch Instructions in accordance with the deployment methodologies described in paragraphs (iv) and (v) below and, if deploying ERS-30, the methodologies described in paragraph (1)(a)(iv) above. 


(iv)
ERCOT shall deploy ERS-10 via an XML message followed by a VDI to the all-QSE Hotline.  The ERS-10 ramp period shall begin at the completion of the VDI.

(A)
If less than 500 MW of ERS-10 is available for deployment, ERCOT shall deploy all ERS-10 Resources as a single block.  

(B)
If the amount of ERS-10 available for deployment equals or exceeds 500 MW, ERCOT, at its discretion, may deploy ERS-10 Resources as a single block or by group designation.  ERCOT shall develop a random selection methodology for determining how to place ERS-10 Resources into groups, and shall describe the methodology in a document posted to the MIS Public Area.  Prior to the start of an ERS-10 Contract Period, ERCOT shall notify QSEs representing ERS-10 Resources of their ERS-10 Resources’ group assignments.

(C)
ERS-10 may be deployed at any time in a Settlement Interval.

(D)
Upon deployment, QSEs shall instruct ERS-10 Resources to perform at contracted levels consistent with the criteria described in Section 8.1.3.1.4 until ERCOT releases the ERS-10 deployment or the ERS-10 Resources have reached their maximum deployment times.  

(E)
ERCOT shall notify QSEs of the release of ERS-10 via an XML message followed by VDI to the all-QSE Hotline.  The VDI shall represent the official notice of ERS-10 release.  ERCOT may release ERS-10 as a block or by group designation.

(F)
Upon release, an ERS-10 Resource shall return to a condition such that it is capable of meeting its ERS performance requirements as soon as practical, but no later than ten hours following the release.

(v)
ERCOT shall deploy RRS capacity supplied by Load Resources (controlled by high-set under-frequency relays) in accordance with the following:

	[NPRR863:  Replace paragraph (v) above with the following upon system implementation:]

(v)
Load Resources providing ECRS that are not controlled by high set under-frequency relays shall be deployed prior to Group 1 deployment.  ERCOT shall deploy ECRS and RRS capacity supplied by Load Resources (controlled by high set under-frequency relays) in accordance with the following:


(A)
Instruct QSEs to deploy RRS that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resource to interrupt based on their group designation from the Day-Ahead.  QSEs shall deploy Load Resources according to the group designation and will be given some discretion to deploy additional Load Resources from any of the groups not designated for deployment if Load Resource operational considerations require such.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;  
	[NPRR863:  Replace paragraph (A) above with the following upon system implementation:]

(A)
Instruct QSEs to deploy RRS with a Group 1 designation and all of the ECRS that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resources to interrupt Group 1 Load Resources providing ECRS and RRS.  QSEs shall deploy Load Resources according to the group designation and will be given some discretion to deploy additional Load Resources from any of the groups not designated for deployment if Load Resource operational considerations require such.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;


(B)
At the discretion of the ERCOT Operator, instruct QSEs to deploy RRS that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resource to interrupt additional Load Resources providing RRS based on their group designation. ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;   

(C)
The ERCOT Operator may deploy all groups of Load Resources providing RRS at the same time.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period; and

	[NPRR863:  Replace paragraph (C) above with the following upon system implementation:]

(C)
The ERCOT Operator may deploy Load Resources providing only ECRS (not controlled by high-set under-frequency relays) and all groups of Load Resources providing RRS and ECRS at the same time.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period; and


(D)
ERCOT shall post a list of Load Resources on the MIS Certified Area immediately following the DRUC for each QSE with a Load Resource obligation which may be deployed to interrupt under paragraph (A) and paragraph (B).  ERCOT shall develop a process for determining which individual Load Resource to place in each group based on a random sampling of individual Load Resources.  At ERCOT’s discretion, ERCOT may deploy all Load Resources at any given time during EEA Level 2. 

(vi)
Unless a media appeal is already in effect, ERCOT shall issue an appeal through the public news media for voluntary energy conservation; and

(vii)
With the approval of the affected non-ERCOT Control Area, TSPs, DSPs, or their agents may implement BLTs, which transfer Load from the ERCOT Control Area to non-ERCOT Control Areas in accordance with BLTs as defined in the Operating Guides.

(b)
Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability.

(3)
ERCOT may declare an EEA Level 3 when the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes.  ERCOT will declare an EEA Level 3 when PRC cannot be maintained above 1,375 MW or when the clock-minute average system frequency falls below 59.91 Hz for 25 consecutive minutes.  Upon declaration of an EEA Level 3, ERCOT will implement any measures associated with EEA Levels 1 and 2 that have not already been implemented.

(a)
When PRC falls below 1,000 MW and is not projected to be recovered above 1,000 MW within 30 minutes, or when the clock-minute average frequency falls below 59.91 Hz for 25 consecutive minutes, ERCOT shall direct all TSPs and DSPs or their agents to shed firm Load, in 100 MW blocks, distributed as documented in the Operating Guides in order to maintain a steady state system frequency at a minimum of 59.91 Hz and to recover 1,000 MW of PRC within 30 minutes. 

(b)
In addition to measures associated with EEA Levels 1 and 2, TSPs and DSPs or their agents will keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens.  Whenever possible, TSPs and DSPs or their agents shall not manually drop Load connected to under-frequency relays during the implementation of the EEA.

�Please note that NPRR937 also proposes revisions to this section.





PRR_Template.doc
Page 2 of 2
PRR_Template.doc
Page 2 of 2
939NPRR-04 PRS Report 071719
Page 2 of 8
PUBLIC

_1624880533.unknown

_1624880534.unknown

_1624880531.unknown

_1624880532.unknown

_1624880530.unknown

_1624880529.unknown

