| NPRR Number | 849 | NPRR Title | Clarification of the Range of Voltage Set Points at a Generation Resource’s POI |
| --- | --- | --- | --- |
| Date |  | July 16, 2019 |  |
| Submitter’s Information |  |  |  |
| Name |  | Woody Rickerson |  |
| E-mail Address |  | wrickerson@ercot.com |  |
| Company |  | ERCOT |  |
| Phone Number |  | 512-248-6501 |  |
| Cell Number |  |  |  |
| Market Segment |  | Not applicable |  |

Comments

ERCOT submits these comments to express its concern that certain language approved by the Reliability and Operations Subcommittee (ROS) on July 10, 2019 may introduce an avoidable ambiguity that could create confusion and disagreement about whether an existing Generation Resource that is undergoing an equipment modification subject to Planning Guide Section 5.1.1, Applicability—commonly referred to as “repowering”—is subject to Reactive Power studies and tests related to the commissioning of the repowered unit.  This is an important issue that should not be left unclear in the Protocols.

As approved by ROS, paragraph (4)(g) of Section 3.15, Voltage Support, provides that “[a] Generation Resource commissioned prior to July 1, 2019 will not be required to submit a new reactive study or conduct pre-commissioning performance testing as described in paragraph (f) above.”  Invenergy and Oncor proposed this language in comments submitted on June 21, 2019, and explained that the language was intended only to clarify that fully commissioned Generation Resources will not somehow be retroactively required to provide new pre-interconnection studies and tests that demonstrate capability to the 0.95 power factor requirement.  ERCOT has no concern with this intended purpose.

However, as ERCOT explained in its July 3, 2019 comments, it does have concerns with the language proposed.  First, because ERCOT plainly cannot require a commissioned Resource to follow procedures that apply only to Resources that have not been commissioned, the clarification is simply unnecessary.  Second, and more problematically, the language introduces an ambiguity about whether existing Generation Resources that are undergoing an equipment modification subject to Planning Guide Section 5.1.1—commonly referred to as “repowering”—may be required to provide reactive studies or tests as part of that commissioning process.  Because the language proposed by Invenergy and Oncor does not make any explicit exception for repowering Generation Resources, one could reasonably conclude that those units are not subject to pre-commissioning studies or tests.  Although ERCOT will interpret the ROS-approved language to require commissioning-related studies and tests for repowering units, there is no compelling reason to leave any room for debate or confusion on this issue when a fairly simple revision to the language will resolve this problem and at the same time provide the clarification on non-retroactivity that Invenergy and Oncor desire.  ERCOT’s July 3, 2019 comments proposed revisions to paragraph (4)(g) that would have resolved this issue in the event stakeholders did not decide to simply strike the language of (4)(g) altogether.

Others at ROS recognized the concern raised by Invenergy’s and Oncor’s language and proposed solutions similar to those proposed by ERCOT. But ROS nevertheless ultimately voted to approve the language in (4)(g) proposed by Invenergy and Oncor without any further clarification.

Invenergy has accurately noted that ERCOT has agreed not to address “the issue of repowering” in this NPRR.  But the “issue of repowering” is not whether repowering Generation Resources are subject to studies and tests in the commissioning process; the issue is what reactive capability must be demonstrated in those studies and tests.  Consistent with this commitment, ERCOT’s proposed language addresses only the former issue; it does not address the latter issue, and looks forward to discussing that language with stakeholders in a separate effort.  Failing to address repowered units in paragraph (4)(g), if it is retained, creates an argument that (4)(g) now operates as an exception to (4)(f), which, along with Planning Guide Section 5.1.1, is the basis for ERCOT’s authority today to require repowering Generation Resources to comply with reactive studies and testing requirements as part of the commissioning process.

ERCOT notes one additional concern with the ROS-approved language in (4)(g): it exempts only those Generation Resources commissioned before July 1, 2019 from having to provide pre-commissioning studies and tests.  This would imply that Generation Resources commissioned after this date are subject to providing pre-commissioning tests after being commissioned, which makes little sense.  ERCOT sees no purpose in having a defined grandfather date for a principle that should apply to all commissioned Generation Resources.

For this reason, ERCOT urges PRS, if it decides not to strike paragraph (4)(g) of Section 3.15, to adopt the following clarifications proposed by ERCOT in its July 3, 2019 comments, which are now reflected in the language below.

Revised Cover Page Language

None

Revised Proposed Protocol Language

- 3.15	Voltage Support

(1)	ERCOT, in coordination with the Transmission Service Providers (TSPs), shall establish and update, as necessary, the ERCOT System Voltage Profile and shall post it on the Market Information System (MIS) Secure Area.  ERCOT, the interconnecting TSP, or that TSP’s agent, may modify the Voltage Set Point described in the Voltage Profile based on current system conditions.

(2)	All Generation Resources (including self-serve generating units) that have a gross generating unit rating greater than 20 MVA or those units connected at the same Point of Interconnection (POI) that have gross generating unit ratings aggregating to greater than 20 MVA, that supply power to the ERCOT Transmission Grid, shall provide Voltage Support Service (VSS).

(3)	Except as reasonably necessary to ensure reliability or operational efficiency, TSPs should utilize available static reactive resources prior to requesting a Voltage Set Point change from a Generation Resource.

(4)	Each Generation Resource required to provide VSS shall comply with the following Reactive Power Requirements in Real-Time operations when issued a Voltage Set Point by a TSP or ERCOT.  Resource testing and study requirements are detailed in paragraphs (f) and (g) below:

(a)	An over-excited (lagging or producing) power factor capability of 0.95 or less determined at the generating unit's maximum net power to be supplied to the ERCOT Transmission Grid and for any Voltage Set Point from 0.95 per unit to 1.04 per unit, as measured at the POI;

(b)	An under-excited (leading or absorbing) power factor capability of 0.95 or less, determined at the generating unit's maximum net power to be supplied to the ERCOT Transmission Grid and for any Voltage Set Point from 1.0 per unit to 1.05 per unit, as measured at the POI;

(c)	For any Voltage Set Point outside of the voltage ranges described in paragraphs (a) and (b) above, the Generation Resource shall supply or absorb the maximum amount of Reactive Power available within its inherent capability and the capability of any Var-capable devices as necessary to achieve the Voltage Set Point;

(d) 	When a Generation Resource required to provide VSS is issued a new Voltage Set Point, that Generation Resource shall make adjustments in response to the new Voltage Set Point, regardless of whether the current voltage is within the tolerances identified in paragraph (4) of Operating Guide Section 2.7.3.5, Resource Entity Responsibilities and Generation Resource Requirements.

(e)	Reactive Power capability shall be available at all MW output levels and may be met through a combination of the Generation Resource’s Unit Reactive Limit (URL), which is the generating unit’s dynamic leading and lagging operating capability, and/or dynamic VAr capable devices.  This Reactive Power profile is depicted graphically as a rectangle.  For Intermittent Renewable Resources (IRRs), the Reactive Power requirements shall be available at all MW output levels at or above 10% of the IRR’s nameplate capacity.  When an IRR is operating below 10% of its nameplate capacity and is unable to support voltage at the POI, ERCOT, the interconnecting TSP, or that TSP’s agent may require an IRR to disconnect from the ERCOT System for purposes of maintaining reliability;

(f)	As part of the technical Resource testing requirements prior to the Resource Commissioning Date, all Generation Resources must conduct an engineering study, and demonstrate through performance testing, the ability to comply with the Reactive Power capability requirements in paragraph (4) above.  Any study and testing results must be accepted by ERCOT prior to the Resource Commissioning Date;

(g)	Except for a Generation Resource subject to Planning Guide Section 5.1.1, Applicability, a Generation Resource that has already been commissioned is not required to submit a new reactive study or conduct commissioning-related reactive testing, as described in paragraph (f) above.  Nothing in this section prohibits ERCOT from conducting reactive testing after a Generation Resource’s Resource Commissioning Date, as otherwise required by NERC Reliability Standards, ERCOT Protocols, and Operating Guides.

(5)	Wind-powered Generation Resources (WGRs) that commenced operation on or after February 17, 2004, and have a signed Standard Generation Interconnection Agreement (SGIA) on or before December 1, 2009 (“Existing Non-Exempt WGRs”), must be capable of producing a defined quantity of Reactive Power to maintain a set point in the Voltage Profile established by ERCOT in accordance with the Reactive Power requirements established in paragraph (4) above, except in the circumstances described in paragraph (a) below.

(a)	Existing Non-Exempt WGRs whose current design does not allow them to meet the Reactive Power requirements established in paragraph (4) above must conduct an engineering study using the Summer/Fall 2010 on-peak/off-peak Voltage Profiles, or conduct performance testing to determine their actual Reactive Power capability.  Any study or testing results must be accepted by ERCOT.  The Reactive Power requirements applicable to these Existing Non-Exempt WGRs will be the greater of: the leading and lagging Reactive Power capabilities established by the Existing Non-Exempt WGR’s engineering study or testing results; or Reactive Power proportional to the real power output of the Existing Non-Exempt WGR (this Reactive Power profile is depicted graphically as a triangle) sufficient to provide an over-excited (lagging) power factor capability of 0.95 or less and an under-excited (leading) power factor capability of 0.95 or less, both determined at the WGR’s set point in the Voltage Profile established by ERCOT, and both measured at the POI.

(i)	Existing Non-Exempt WGRs shall submit the engineering study results or testing results to ERCOT no later than five Business Days after its completion.

(ii)	Existing Non-Exempt WGRs shall update any and all Resource Registration data regarding their Reactive Power capability documented by the engineering study results or testing results.

(iii)	If the Existing Non-Exempt WGR’s engineering study results or testing results indicate that the WGR is not able to provide Reactive Power capability that meets the triangle profile described in paragraph (6)(a) above, then the Existing Non-Exempt WGR will take steps necessary to meet that Reactive Power requirement depicted graphically as a triangle by a date mutually agreed upon by the Existing Non-Exempt WGR and ERCOT.  The Existing Non-Exempt WGR may meet the Reactive Power requirement through a combination of the WGR’s URL and/or automatically switchable static VAr capable devices and/or dynamic VAr capable devices.  No later than five Business Days after completion of the steps to meet that Reactive Power requirement, the Existing Non-Exempt WGR will update any and all Resource Registration data regarding its Reactive Power and provide written notice to ERCOT that it has completed the steps necessary to meet its Reactive Power requirement.

(iv)	For purposes of measuring future compliance with Reactive Power requirements for Existing Non-Exempt WGRs, results from performance testing or the Summer/Fall 2010 on-peak/off-peak Voltage Profiles utilized in the Existing Non-Exempt WGR’s engineering study shall be the basis for measuring compliance, even if the Voltage Profiles provided to the Existing Non-Exempt WGR are revised for other purposes.

(b)	Existing Non-Exempt WGRs whose current design allows them to meet the Reactive Power requirements established in paragraph (4) above (depicted graphically as a rectangle) shall continue to comply with that requirement.  ERCOT, with cause, may request that these Existing Non-Exempt WGRs provide further evidence, including an engineering study, or performance testing, to confirm accuracy of Resource Registration data supporting their Reactive Power capability.

(6)	Qualified Renewable Generation Resources (as described in Section 14, State of Texas Renewable Energy Credit Trading Program) in operation before February 17, 2004, required to provide VSS and all other Generation Resources required to provide VSS that were in operation prior to September 1, 1999, whose current design does not allow them to meet the Reactive Power requirements established in paragraph (4) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the ERCOT Operating Guides.

(7)	New generating units connected before May 17, 2005, whose owners demonstrate to ERCOT’s satisfaction that design and/or equipment procurement decisions were made prior to February 17, 2004, based upon previous standards, whose design does not allow them to meet the Reactive Power requirements established in paragraph (4) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the Operating Guides.

(8)	For purposes of meeting the Reactive Power requirements in paragraphs (4) through (7) above, multiple generation units including IRRs shall, at a Generation Entity’s option, be treated as a single Generation Resource if the units are connected to the same transmission bus.

(9)	Generation Entities may submit to ERCOT specific proposals to meet the Reactive Power requirements established in paragraph (4) above by employing a combination of the URL and added VAr capability, provided that the added VAr capability shall be automatically switchable static and/or dynamic VAr devices.  A Generation Resource and TSP may enter into an agreement in which the proposed static VAr devices can be switchable using Supervisory Control and Data Acquisition (SCADA).  ERCOT may, at its sole discretion, either approve or deny a specific proposal, provided that in either case, ERCOT shall provide the submitter an explanation of its decision.

(10)	A Generation Resource and TSP may enter into an agreement in which the Generation Resource compensates the TSP to provide VSS to meet the Reactive Power requirements of paragraph (4) above in part or in whole.  The TSP shall certify to ERCOT that the agreement complies with the Reactive Power requirements of paragraph (4).

(11)	Unless specifically approved by ERCOT, no unit equipment replacement or modification at a Generation Resource shall reduce the capability of the unit below the Reactive Power requirements that applied prior to the replacement or modification.

(12)	Generation Resources shall not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damage is imminent.

(13)	All WGRs must provide a Real-Time SCADA point that communicates to ERCOT the number of wind turbines that are available for real power and/or Reactive Power injection into the ERCOT Transmission Grid.  WGRs must also provide two other Real-Time SCADA points that communicate to ERCOT the following:

(a)	The number of wind turbines that are not able to communicate and whose status is unknown; and

(b)	The number of wind turbines out of service and not available for operation.

(14)	All PhotoVoltaic Generation Resources (PVGRs) must provide a Real-Time SCADA point that communicates to ERCOT the capacity of PhotoVoltaic (PV) equipment that is available for real power and/or Reactive Power injection into the ERCOT Transmission Grid.  PVGRs must also provide two other Real-Time SCADA points that communicate to ERCOT the following:

(a)	The capacity of PV equipment that is not able to communicate and whose status is unknown; and

(b)	The capacity of PV equipment that is out of service and not available for operation.

(15)	For the purpose of complying with the Reactive Power requirements under this Section 3.15, Reactive Power losses that occur on privately-owned transmission lines behind the POI may be compensated by automatically switchable static VAr capable devices.