## Slide 1
Review of Long SCED Intervals and EBP events
Market Analysis and Validation
WMWG
July 22th, 2019

## Slide 2: Long SCED intervals, EBP Offset and Price Changes
 | Occurrence Count |  |  | Long SCED duration (in minutes) |  |  | System Lambda Changes ($/MWh) | 
Year | Long SCED Count | Price Correction Count due to long SCED | EBP offset count for long SCED | Maximum duration | Average duration | Minimum duration | Largest Increase | Largest Decrease
2010 | 5 |  | 1 | 36.1 | 19.6 | 12.3 | 0.33 | -0.61
2011 | 28 | 12 | 6 | 120.6 | 27.0 | 10.2 | 319.62 | -8.57
2012 | 5 | 3 |  | 44.2 | 24.6 | 11.8 | 1.08 | -1.22
2013 | 3 | 3 | 1 | 47.7 | 38.1 | 29.3 | -0.37 | -3.96
2014 | 9 | 8 | 2 | 83.8 | 30.6 | 10.1 | 47.52 | -737.41
2015 | 10 | 2 | 2 | 79.5 | 19.4 | 7.7 | 709.33 | -17.21
2016 | 14 | 4 | 2 | 82.9 | 16.7 | 7.7 | 18.86 | -1.62
2017 | 5 | 2 |  | 17.0 | 10.5 | 7.9 | 1.37 | -371.62
2018 | 9 | 5 |  | 27.6 | 13.1 | 7.7 | 0.77 | -85.19
2019 | 2 |  |  | 13.5 | 13.4 | 13.3 | -0.26 | -0.29
Total | 90 | 39 | 14 | 120.6 | 22.1 | 7.7 | 709.33 | -737.41
Note:
The long SCED interval threshold was 10 minute before 2015, and 7.5 minute since 2015 due to EMS logic.
3 Instances in 2018 and 2 instances in 2019 were due to unannounced constant frequency control test.
The System Lambda changes were calculated from original system lambda before price correction.

## Slide 3: 10/05/2016
Event: After a scheduled ERCOT EMS/MMS database load, SCED started failing due to a modeling issue in MMS.
Timeline:
  Last good SCED results was run at 00:00
  EBP flag was automatically enabled at 00:07
  During the period when EBP flag was active (00:07-01:25), EBP offsets were entered by the operators multiple times to control the grid frequency.
  The issue was resolved around 01:22, a manual SCED run was run by ERCOT Control room at 01:23.
  After the 01:23 SCED results were verified, emergency base point flag was manually unchecked by ERCOT Control room at 01:25.
  SCED was run manually at 01:25 and again at 01:26, and both SCED results were published successfully.
Price Correction: Price correction was performed, and LMP was hold extra 15 minutes based on NPRR 696.

## Slide 4: 07/07/2016
Event: ERCOT experienced an issue with the EMS. EMS was unavailable first and then was able to run in a degraded state.
Timeline:
  Last good SCED results was run at 11:40
  At 11:41 EMS system became unavailable and LFC went to suspended mode due to very low frequency.
  At 11:42 SCED was triggered due to low frequency and prices went to $9001 due to invalid inputs from EMS
  EBP flag was manually enabled by ERCOT Control room at 11:44
  At 11:59 ERCOT Control room issued operating instruction to NRG QSE for Constant Frequency Control as LFC was still down at this time.
  ERCOT Control room issued operating instruction to NRG QSE to come off of Constant Frequency Control around 12:16, as LFC back to work.
  From 12:16, ERCOT Control room was entering EBP offsets to control the grid frequency as SCED was running with invalid EMS input data.

## Slide 5: 07/07/2016 (Cont.)
  At 13:22, all EMS applications were back in good operating state and the EBP flag were unchecked in EMS.
  SCED was run manually at 13:23 and the results were transferred to the Market.
Price Correction: Price correction was performed. This event was before NPRR 696.

## Slide 6: 03/25/2015
Event: During a scheduled MMS/OS Production cutover, SCED was not running for 80 minutes.
Timeline:
  Last good SCED results was run at 15:35
  EBP flag was automatically enabled at 15:45
  During the period where EBP flag was active, ERCOT Control room entered EBP offsets multiple times in LFC to manually control the frequency.
  After the MMS Database as well as MMS Applications became available, SCED was run manually the first time and it completed at 16:54
  After SCED results were verified and transferred to EMS, EBP flag was unchecked in LFC at 16:55
  First SCED result transferred to Market Participants was the SCED that completed at 16:56
Price Correction: Price correction was performed. This event was before NPRR 696.

## Slide 7: Questions?