## Slide 1
ERCOT Position on Alternative for
KP 1.5 Process for Deploying Ancillary Services
David Maggio
Technical Advisory Committee
ERCOT Public
July 24, 2019

## Slide 2: The manner in which Regulation Service is deployed must change with Real-Time Co-optimization (RTC).
Today, Regulation deployment is at the portfolio level and Qualified Scheduling Entities (QSEs) provide Regulation participation factors which must sum up to “1”.
The Load Frequency Control (LFC) system uses those participation factors to determine the expected output on individual Resources.
The current use of participation factors is predicated on the fact that a QSE’s Ancillary Service (AS) Supply Responsibility for Regulation is known in advance of the period for which it’s in effect (e.g., from the Day-Ahead Market).
This criterion no longer holds under RTC and system changes are needed to address this issue.

## Slide 3: ERCOT is proposing that Regulation deployment become Resource-specific with the instructions being in proportion to a Resource’s Regulation awards.
This system logic is simple and deployments can be sent out immediately after the awards are determined.
This ensures that the system will honor the awards and MW limits of individual Resources.
  Today, use of participation factors can result in Resources being expected to produce at levels that they can’t physically operate at.
The factors for distributing the system-wide deployment will be adjusted following each execution of the optimization (every 5 minutes or less)
QSEs will have flexibility with Resource-specific MW telemetry to affect awards to Resources that have limitations for a given SCED interval.
LFC determines the system-wide deployment amount (e.g., 100/200 MW of Regulation Up)
R1
R2
R3
60 MW Regulation Up Award for the Interval
40 MW Regulation Up Award for the Interval
100 MW Regulation Up Award for the Interval
100/200 MW
30/60 MW
20/40 MW
50/100 MW

## Slide 4: There are concerns with Alternative 2.
While the current design allows use of Regulation participation factors, a fundamental need for that design goes away under RTC. Regulation awards will not be known in advance of Real-Time and are subject to change every time the Real-Time Market clears.
Alternative 2 recognizes this issue and attempts to address it by using a mixture of approaches during the 5-minute interval:
  Use the ERCOT proposed approach for the first part of the 5-minute interval; and
  Use another approach (that is optional) for the latter part of the 5-minute interval where the ERCOT systems determine Regulation instructions at the portfolio level and use participation factors to determine the expected output of individual Resources.
While Alternative 2 may be technically feasible, it is more complex and creates risk around the management and validation of telemetry.
  E.g., determining when QSEs are utilizing this optionality and have updated the values and managing cases when the values don’t look as expected during the latter part of the 5-minute interval.