## Slide 1
Distributed Generation Capacity Forecasting for the CDR
July 31, 2019
Notes: Welcome to

## Slide 2: ERCOT Estimated Total DER Growth 2015-2018 (MW)
Note: This estimate includes informal data reporting by many NOIEs and excludes generation data informally reported by investor-owned utilities for generation that would typically be considered backup or emergency generation.
31%
26%
181%

## Slide 3: Distributed Energy Resources Trends
  Solar PV  Significant growth
    Utility Scale (> 1 MW)
    Residential/Commercial (< 1 MW)
  Internal Combustion Engines
    Diesel  limited growth
    Nat Gas  Significant growth
  Energy Storage  limited growth
    Utility Scale Batteries (> 1 MW)
    Residential/commercial (< 1 MW)
  -- Wind Turbines  very limited growth
    Utility Scale
    Residential(< 20 kW)
  Landfill Gas/Biogas  very limited growth

## Slide 4: Residential Solar Growth Projection
April 12, 2019 SAWG DG Solar Forecast Tool
http://www.ercot.com/content/wcm/key_documents_lists/172703/DGSolar_Forecasting_Tool.xlsm
  Estimates Long-term Growth using S-curve
  Total capacity based on AWS Truepower analysis
  Summer Peak Capacity Factor at 36% based on AWS Truepower analysis.
Chart: S-Curve Penetration Rates
| 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Penetration | 0.041652 | 0.071004 | 0.11273 | 0.15446 | 0.18382 | 0.19974 | 0.20718 | 0.21041 | 0.21177 | 0.21234 | 0.21257

## Slide 5: Utility Scale Solar Growth Projections
No Forecast tool developed yet
Comprised of two primary groups of installations
  NOIE Community Solar (750-998 kW)
  Competitive Choice (typically 5-10 MW)
Proposed methodology would be similar to Rooftop Solar
  Estimate Long-term Growth using S-curve
  Total Capacity estimates
    Suggest hosting solar developer roundtable to help develop/refine?
  Summer Peak Capacity Factor similar to Transmission Connected?

## Slide 6: Natural Gas Growth Projections
Installations started along Gulf Coast for hurricane resiliency
  Starting to spread to other areas of ERCOT
Proposed methodology
  No Forecast tool developed
  Suggest informal Poll of DSP’s to determine short/medium term growth?
  Summer/winter Peak Capacity Factor?
    Self Dispatched
      Price Responsive
      Non-price Responsive

## Slide 7: Price Responsive –Diesel and Nat Gas
2019 - SODGs are mapped to their corresponding Loads in the ERCOT Network model.
Using the Telemetry of those mapped Loads, ERCOT can measure SODG response

## Slide 8: Non-Price Responsive—Diesel and Nat Gas
Multiple price spikes and no change in SCADA MW