## Info
Header Information
TDSP | Operator of the Major Transmission Element.
Major Transmission Element (MTE) | Transmission Element which was, or scheduled to be, on outage and has been associated with one or more high congestion(s).
Equip. Type | Equipment Type of the MTE.
kV | Voltage Level of the MTE. High-side voltage for transformers
Congestion Year/Month | Year and Month the associated congestion occurred.
Contingency | Contingency associated with the MTE.
Overload | Overload associated with the MTE.
Source | Source of the information: RT = Based on historical Real-Time congestion, ST = Based on Outage Coordination Studies. ADD = Addition Requests (both Private and Public)
Outage Type | Outage Type is categorized to be either Planned (PL) and Forced (FR, FE, UE, M1, M2, M3)
Cancel | Outage(s) for the specific MTE was Cancelled, Rejected, or Withdrawn.
Removal Requestor | Stakeholder who is requesting to remove the MTE from the list (Organization)
Addition Requestor | Stakeholder who is requesting to add the MTE from the list (Organization)
Reason for Addition | Justification for adding the MTE to the list. Details of the specific scenarios that the MTE may cause high congestion, including but not limited to: 1. ERCOT Load Level: Peak, Off-Peak (or 35GW, 70GW, etc). 2. Any specific regional load condition: High Houston Load, etc. 3. Wind Generation Level: High, Mid, Low, or N/A. 4. Solar Geneartion Level: High, Mid, Low, or N/A. 5. Any specific abnormal transmission equipment status: i.e. 345 kV line from A to B out-of-service, etc. 6. For Private Submissions, any specific generator output level: i.e. Resource A at 300 MW or above, etc. 7. (Optional) PSSE or PowerWorld case if available.
Reason for Removal | Justification for removing the MTE from the list. Usually entails a Transmission Upgrade Project.
OCITF Consensus | Consensus after OCITF meetings.
Decision | Final (TAC) Decision of the Addition/Removal Request for Non-Consensus items.
Discussion Items | Any other information that stakeholder(s) want to discuss during the OCITF meetings.

## MTE(2019)
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Congestion Year/Month | Contingency | Overload | Source | Outage Type | Cancel | Removal Requestor | Reason for Removal | OCITF Consensus | Decision | Discussion Items | From Acronym | To Acronym | ERCOT Equip Name | ERCOT Contingency ID
AEN | Fayette Plant 2 - Holman Aen | LN | 345 | 18/10, 18/11 | DCKT Lost Pines Aen - Aen Dunlap & Austrop 345 kV | Fayetteville 345/138 kV Auto AT2 | RT | Planned |  | AEN | AEN's line was out at the same time as LCRA's T255 Lytton Spring to Fayette transmission line (also in this spreadsheet). The two outages cause congestion, not the single outage of either transmission line. Fayette Plant2 - Holman AEN was out by itself in both June 2017 and July 2017 and did not cause congestion in those months. |  |  |  | HOLMAN | FPPYD2 | CKT_3122 | SHOLFPP5
AEN | Hamilton Aen CB HM_950 | CB | 138 | 15/4 | DCKT Burleson to Carson Creek 138 kV & Pedernales to Advanced Micro Devices Aen 138 kV | Manesium Plant - Northlan 138 kV | RT | Forced |  | AEN | In April 2015 AEN's HM-950 was out at the same time as AEN's Ckt 949 Burleson - Hicross. AEN's internal N-1-1 analysis has identified both of these transmission elements as possible sources of summer congestion on Ckt 979 Magnesium Plant to-Northlan 138kV but it was the combination of the two outages in April 2015 that caused this congestion. HM-950 was out of service and did not cause congestion in September 2015, January 2016, February 2016, January 2018, February 2018, and March 2018. |  |  |  | HAMILTN |  | HM_950 | N/A
AEP | Air Liquide Ingleside - … - Dupont Switch - Ingleside & Oxychem Ingleside | LN | 138 | 16/4, 17/8, 18/1 | Dupont Pp1 Ingleside to Ingleside Cogen Sw 138 kV (3A), Lon Hill to Coleto Creek 345 kV, Dupont Sw - Ingleside to Ingleside Cogen Sw 138 Kv | Duppont Pp1 Ingleside - Duppont Sw Ingleside 138 kV, Lon Hill - Pawnee Switching Station 345 kV, Dupont Pp1 - Ingleside to Dupont Sw - Ingleside 138 kV | ST, RT | Planned, Forced | [6 empty] | ALIQUING | ALIQUSW | ALIQUI_ALIQUS1 | SALII_D8
AEP | Ajo - … - Rio Hondo | LN | 345 | 16/2, 17/2 | DCKT Lon Hill to North Edinburg 345 kV & Orange Grove Sw 138 kV | Celanese Bishop - Nelson Sharpe 138 kV, Lon Hill - Bessel 138 kV | ST | Planned | [6 empty] | AJO | MAGICVAL | AJO_MAGICV1 | SAJORI25
AEP | Alice (What is the actual MTE? Line? Auto?) | LN | 138/69 | 19/1 | DCKT Lon Hill - North Edinburg 345 kV & Orange Grove Switching Station 138 kV | Falfurrias - Premont 69 kV | RT | Forced | [5 empty] | Need clarification on what the actual MTE is | ALICE |  | 69A1 | XALI89
AEP | Aransas Pass - … - Dupon Swith Ingleside | LN | 138 | 17/4, 17/8 | Rockport to Rincon 138 kV, Lon Hill to Coleto Creek 345 Kv | Gregory - Rincon 69 kV, Lon Hill - Pawnee Switching Station 345 kV | RT, ST | Forced | [6 empty] | ARANSASP | INGLESID | ARANSA_INGLES1 | SHOMI_D8
AEP | Armstrong Aep - … - Raymondville 2 | LN | 138 | 16/3 | Valley Import | N/A | RT | Forced | [6 empty] | ARMSTRON | MV_YUTT | ARMSTR_MV_YUT1 | SARMRA38
AEP | Asherton - Bevo | LN | 138 | 15/11 | Basecase | Low Voltage from Dimmit to DC Eagle Pass | ST | Forced | [6 empty] | BEVO | ASHERTON | 603T603 | SBEVASH8
AEP | Aspermont Aep - Paint Creek | LN | 138 | 16/4 | Scurry Sw to Sun Sw 138 kV | Paint Creek Auto 69-2 138/69 kV | RT | Forced | [6 empty] | ASPM | PAINTCRE | ASPM_PAINTC1 | SASPPAI8
AEP | Barney Davis Bus #1 (CB 6755, etc.) | BUS | 138 | 16/10 | DCKT Barney Davis to Airline Aep 138 kV | Barney Davis - Rodd Field 138 kV | ST | Planned | Y | AEP | Installation of Barney Davis - Naval Base 138 kV line should eleminate this |  |  |  | B_DAVIS |  | 1131 | N/A
AEP | Barney Davis Bus #2 (CB 5200, etc.) | BUS | 138 | 16/10, 17/2, 17/3 | Airline Aep to Barney Davis 138 kV | Rodd Field - Holly 138 kV | ST | Planned, Forced | Y | [5 empty] | B_DAVIS |  | 1132 | N/A
AEP | Big Three - … - Bp Chem Vistron4 | LN | 138 | 17/6 | DCKT Victoria to Victoria Dupont Sw & Victoria Dupont Sw to Victoria 138 kV | Formosa - Lolita 138 kV | RT | Planned, Forced | [6 empty] | BIGTRE | BLCBAYU4 | BIGTRE_BLCBAY1 | SBIGVIS8
AEP | Blessing - Stp Switch | LN | 138 | 18/1 | Lane City to Blessing 138 kV | El_Campo - Lane City Pump 138 kV | RT | Forced | [6 empty] | BLESSING | STP | BLESSI_STPSW1 | SBAYBLE8
AEP | Blessing Auto 1382 138/69 kV | XF | 138 | 17/10, 17/12 | Coleto Creek to Victoria 138 kV, DCKT San Miguel Gen to Elmcreek 345 kV, San Miguel Auto 345_138 kV Switchyards Trx SANMGL8_3_1 | Coleto Creek - Victoria 138 kV, Pawnee Switching Station - Calaveras 345 kV, San Miguel Auto ATAH 345/138 KV | RT | Planned | [6 empty] | BLESSING | 345/138kV | 1382 | XBLE58
AEP | Blessing Auto 69A1 138/69 kV (Typo, believe this should be 345/138 kV auto) | XF | 345 | 18/12 | Lane City - South Lane City 138 kV | Franklins Camp Sub - Sargent Sub 69 kV | RT | Planned, Forced |  | AEP |  |  |  |  | BLESSING |  | 345_1382 | XBLE89
AEP | Brackettville - … - Hamilton Road | LN | 138 | 18/4 | DCKT Big Hill to Kendall 345 kV | Hamilton Road - Maverick 138 kV | RT | Planned | [6 empty] | HAMILTON | PINTCR | 464T464 | SBRAHAM8
AEP | Brady North - … - Eden | LN | 69 | 18/5 | Junction - … - Yellow Jacket 69 kV | Hext - Yellow Jacket 69 kV | RT | Forced |  | AEP | Mason 138/69 auto and Heartland station should be complete end of 2019 |  |  |  | NORTHBRA | EDEN | MELVIN_NORTHB1 | SNORMCL9
AEP | Bruni - Crestonio | LN | 138 | 15/5, 15/6 | Laquinta to Lobo 138 kV | Bruni Auto 69_1 138/69 kV | ST | Planned | Y, N | [5 empty] | BRUNI4 | CRESTONI | BRUNI4_CRESTO1 | SCREBRU8
AEP | Celanese Bishop Bus #1 (CB 6305, 8425) | BUS | 138 | 16/10 | Airline Aep to Barney Davis 138 kV | Rodd Field - Holly 138 kV | ST | Planned | Y | [5 empty] | CELANEBI |  | 1131 | N/A
AEP | Celanese Bishop Bus #2 (CB 6075, 8425) | BUS | 138 | 16/10 | Airline Aep to Barney Davis 138 kV | Rodd Field - Holly 138 kV | ST | Planned | Y | [5 empty] | CELANEBI |  | 1133 | N/A
AEP | Coleto - Lon Hill | LN | 345 | 17/3, 15/3, 16/1, 16/12 | DCKT Whitepoint to Hecker & Dupont Sw Ingleside 138 kV, Coleto Creek to Pawnee Sw 345 kV, Pawnee Sw to Lon Hill 345 kV | Whitepoint - Rincon 138 kV, Kenedy Sw - Coleto Creek 138 kV, Magruder - Victoria 138 kV, Kenedy Sub - Kenedy Sw 69 kV | RT, ST | Planned, Forced | Y, N | [5 empty] | COLETO | LON_HILL | COLETO_LON_HI1 | SCOLLON5
AEP | Del Sol - Pomelo | LN | 345 | 16/10, 17/1 | Valley GTC | N/A | ST | Planned | Y | [5 empty] | DELSOL | POMELO | DELSOL_POMELO1 | SPOMDEL5
AEP | Dupont Switch Ingleside - Hecker (HECKER_I_DUPS2) | LN | 138 | 17/4 | Hecker to WhitePoint 138 kV | Whitepoint - Rincon 138 kV | RT | Planned | [6 empty] | HECKER | I_DUPSW | HECKER_I_DUPS2 | SI_DWHI8
AEP | Fort Stockton Plant - … - Oxy Century Tnp & Rio Pecos | LN | 138 | 18/12, 19/1, 19/2, 19/3 | Moss Switch - Odessa Ehv Switch 345 kV, Lotebush - … - Yucca Drive Switch 138 kV | Rio Pecos - Woodward 2 138 kV, 16th Street Tnp - Woodward 2 138 kV | RT | Planned | [6 empty] | FTST | TOMBSTNE | FTST_TOMBST1 | SWOORI38
AEP | Fort Stockton Plant Auto 69T1 138/69 kV | XF | 138 | 17/12, 18/3, 18/4 | Basecase, Barrilla Auto Trx Fmr1 138/69 Kv, Barilla to Solstice 138 kV, Fort Stockton Plant to Oxy Century Tnp & Rio Pecos & Woodward 1 138 kV | Yucca Drive Sw - Gas Pad 138 Kv, Alamito Creek - Paisano 69 kV, 16Th Street Tnp - Woodward 2 138 kV, Pig Creek - Solstice 138 kV | RT | Planned |  | AEP | 138 kV ring bus and 138/69 kV auto at Saragosa complete end of 2019 |  |  |  | FTST |  | 69T1 | XFTS89
AEP | Fort Stockton Switch - … - Rio Pecos | LN | 69 | 19/3 | Lotebush - … - Yucca Drive Switch 138 kV | Rio Pecos - Woodward 2 138 kV | RT | Planned |  | AEP | This line is keep N/O (radial) for contingencies. 138 kV upgrades at Saragosa also complete end of 2019 |  |  |  | FTSW | RIOPECOS | FTSW_GOMZ1 | SGOMRIO9
AEP | Frontera - … - Key Switch & Palmhurst | LN | 138 | 17/5 | Pharr Magic Valley to North Pharr 138 kV | North McAllen - West McAllen 138 KV | RT | Planned | [6 empty] | FRONTERA | PALMHRTP | FRONTE_PALMHR1 | SPALFRO8
AEP | Ganso - … - Hamilton Road | LN | 138 | 18/3 | North McCamey to Santa Rita 138 kV | Santiago - San Angelo Power Station 138 kV | RT | Planned | [6 empty] | GANSO | MAVERICK | GANSO_MAVERI1 | SEAGHAM8
AEP | Gila - Nueces Bay | LN | 138 | 19/4 | DCKT Whitepoint - Lon Hill & South Texas Project 345 kV | Lon Hill 345/138 kV Auto 382H | RT | Forced | [6 empty] | GILA | NUECES_B | GILA_NBEC8 | SGILNU58
AEP | Haine Drive - La Palma | LN | 138 | 17/4 | DCKT Rio Hondo to North Endinburg 345 kV & Harlingen Sw | Burns Sub - Rio Hondo 138 kV | RT | Planned | [6 empty] | HAINE_DR | LA_PALMA | HAINE__LA_PAL1 | SHAILA_8
AEP | Harlingen #1 - … - La Palma | LN | 69 | 18/1 | Lon Hill to Coleto Creek 345 kV, Dyann to Wharton 138 kV, La Palma to East Harrison 69 kV, North Edinburg Auto Trx 1382 345/138 kV | Warburton Road Switching Station - Victoria 138 kV, El_Campo - Lane City Pump 138 kV, North Edinburg Auto 138H 345/138 kV | RT | Forced | [6 empty] | HARLIN_1 | W_HARLIN | HARLIN_W_HARL1 | SW_HLA_9
AEP | Hecker - Whitepoint (HECKER_WHITE_1) | LN | 138 | 17/3, 18/1, 19/2, 19/3 | DCKT Whitepoint to Hecker & Dupont Sw Ingleside 138 kV, Lon Hill to Coleto Creek 345 kV, McCampbell - … - Whitepoint 138 kV | Whitepoint - Rincon 138 kV, Warburton Road Switching Station - Victoria 138 kV, Whitepoint TRX 138_69A1 138/69 kV | RT | Planned, Forced | [6 empty] | HECKER | WHITE_PT | HECKER_WHITE_1 | SHECWH28
AEP | Hecker - Whitepoint (HECKER_WHITE_2) | LN | 138 | 18/1, 19/2, 19/3 | Lon Hill to Coleto Creek 345 kV, McCampbell - … - Whitepoint 138 kV | Warburton Road Switching Station - Victoria 138 kV, Whitepoint TRX 138_69A1 138/69 kV, Rincon - Whitepoint 138 kV | RT | Planned, Forced | [6 empty] | HECKER | WHITE_PT | HECKER_WHITE_2 | SHECWHI8
AEP | Hiway 9 - Javelina | LN | 138 | 18/10 | DCKT Hecker - Whitepoint 138 kV | Rincon - Whitepoint 138 kV | RT | Planned | [6 empty] | JAVELINA | HIWAY_9 | HIWAY__JAVELI1 | SJAVHIW8
AEP | Hiway 9 Auto 69A2 138/69 kV | XF | 138 | 17/4 | Lon Hill Auto 69A1 138/69 kV | Koch Up River Auto 69A1 138/69 kV | RT | Forced | [6 empty] | HIWAY_9 |  | 69A2 | XHIW89
AEP | Holly - Westside Aep | LN | 138 | 18/11 | Airline Aep - … - Westside Aep 138 kV | Arcadia - Southside 138 kV | RT | Planned, Forced | [6 empty] | HOLLY4 | WESTSIDE | HOLLY4_WESTSI1 | SHOLWES8
AEP | Industrial Aep - Nueces Bay | LN | 69 | 17/4 | Lon Hill Auto 69A1 138/69 kV | Koch Up River Auto 69A1 138/69 kV | RT | Forced | [6 empty] | INDUSTRI | NUECES_B | INDUST_NUECES1 | SINDNUE9
AEP | Jim Treece - Riley | LN | 345 | 16/11 | Panhandle GTC | N/A | ST | Planned | [6 empty] | JIMTREEC | RILEY | JIMTRE_RILEY2 | SJIMRI25
AEP | Jim Treece - Tesla | LN | 345 | 16/11, 17/2 | Panhandle GTC | N/A | ST | Planned | Y, N | [5 empty] | JIMTREEC | TESLA | JIMTRE_TESLA2 | SJIMTE25
AEP | Joslin Bus #1 (CB 8315, etc.) | BUS | 138 | 17/3 | Formosa Unit FORMOSG12, Formosa Unit FORMOSG3 | Formosa - Lolita 138 kV | RT | Planned |  | AEP | The Joslin - Formosa 138 kV line is now double breaker at Joslin, so an outage on the #1 bus will not take this line out. Both the Formosa - Joslin and Formosa - Lolita lines will remain in service in this scenario. |  |  |  | JOSLIN |  | 1131 | N/A
AEP | La Palma - … - Stewart Road | LN | 69 | 18/1 | North Edinburg Auto Trx 1382 345/138 kV | North Edinburg Auto 138H 345/138 kV | RT | Forced | [6 empty] | LA_PALMA | RANGERVL | LA_PAL_RANGER1 | SRANLA_9
AEP | La Palma - Mvec (Rangerville) | LN | 138 | 18/5 | North Pharr - Polk Avenue 138 kV | North McAllen - West McAllen 138 kV | RT | Planned | [6 empty] | LA_PALMA | MVRANGER | LA_PAL_MVRANG1 | SMVRLA_8
AEP | La Palma 138 kV bus #1 (CB 0325, etc.) | BUS | 138 | 18/5 | DCKT Rio Hondo - North Edinburg 345 kV & Harlingen Switch 138 kV | Burns Sub - Rio Hondo 138 kV | RT | Planned | [6 empty] | LA_PALMA |  | 0BB1 | N/A
AEP | La Palma 138 kV bus #2 (CB 2015, etc.) | BUS | 138 | 18/5 | DCKT Rio Hondo - North Edinburg 345 kV & Harlingen Switch 138 kV | Burns Sub - Rio Hondo 138 kV | RT | Planned | [6 empty] | LA_PALMA |  | 8BB2 | N/A
AEP | La Palma Bus #2 (CB 5875, etc.) | BUS | 138 | 17/2 | North Edinburg Auto 1382 345/138 kV | Burns Sub - Rio Hondo 138 kV | RT | Planned | [6 empty] | LA_PALMA |  | 8BB2 | N/A
AEP | Laquinta - Lobo | LN | 138 | 15/5 | Crestonio to Falfurrias 138 kV | Bruni Auto 69_1 138/69 kV | ST | Planned | Y | [5 empty] | LOBO | LAQUINTA | LAQUIN_LOBO1 | SLAQLOB8
AEP | Laredo Vft North - … - Mines Road | LN | 138 | 18/4 | Molina to Wormser Road 138 kV, Lobo to Molina 138 kV | Del_Mar - Laredo Plant 138 kV | RT | Planned | [6 empty] | LARDVNTH | LASCRUCE | LARDVN_LASCRU1 | MNLALAR8
AEP | Las Pulgas - Raymondville 2 | LN | 138 | 16/12, 17/4 | Loyola Sub to Kleberg Aep 138 kV, DCKT Rio Hondo to North Endinburg 345 kV & Harlingen Sw | Loyola Sub Auto 69_1 138/69 kV, Burns Sub - Rio Hondo 138 kV | RT | Planned | [6 empty] | RAYMND2 | LASPULGA | LASPUL_RAYMND1 | SRAYRI38
AEP | Las Pulgas - Rio Hondo | LN | 138 | 16/12, 17/4 | Loyola Sub to Kleberg Aep 138 kV | Loyola Sub Auto 69_1 138/69 kV | ST | Planned | [6 empty] | LASPULGA | RIOHONDO | LASPUL_RIOHON1 | SRAYRI28
AEP | Lon Hill - Nelson Sharpe | LN | 345 | 15/2, 15/10, 16/3, 16/4 | DCKT Lon Hill to North Edinburg 345 kV & Orange Grove Sw 138 kV, Ajo to Rio Hondo 345 kV | Bunsen - Lon Hill 138 kV, Celanese Bishop - Kleberg 138 kV | ST | Planned | Y | [5 empty] | LON_HILL | N_SHARPE | LON_HI_N_SHAR1 | SN_SLON5
AEP | Lon Hill - Whitepoint | LN | 345 | 17/8, 18/2 | Lon Hill to Coleto Creek 345 kV, DCKT San Miguel Gen to Elmcreek 345 kV, DCKT Kendall to Cagnon 345 kV & Menger Creek to Ranchtwn 138 kV | Lon Hill - Pawnee Switching Station 345 kV, Pawnee Switching Station - Calaveras 345 kV, Marion Auto AT2H 345/138 kV | RT | Forced | [6 empty] | LON_HILL | WHITE_PT | LON_HI_WHITE_1 | SWHILON5
AEP | Lon Hill Auto 381 345/138 kV | XF | 345 | 19/3, 19/4 | Whitepoint TRX 345A 345/138 kV | Lon Hill TRX 382H 345/138 kV | RT | Planned, Forced | [6 empty] | LON_HILL |  | LON_HILL XFMR 381 | XLON58
AEP | Lon Hill Auto 69A2 138/69 kV | XF | 138 | 17/4 | Hecker to WhitePoint 138 kV, Lon Hill Auto 69A1 138/69 kV | Whitepoint - Rincon 138 kV, Koch Up River Auto 69A1 138/69 kV | RT | Planned | [6 empty] | LON_HILL |  | 69A2 | XLON489
AEP | Lon Hill Bus #1 (CB 6005, etc.) | BUS | 138 | 15/5 | Lobo Auto A2 345/138 kV | Asherton - Catarina 138 kV | ST | Planned |  | AEP | MTE and contingency are not in same area. Remote from each other. |  |  |  | LON_HILL |  | 1131 | N/A
AEP | McCampbell - … - Whitepoint | LN | 138 | 18/10 | DCKT Hecker - Whitepoint 138 kV | Dupont Switch Ingleside - Rincon 138 kV | RT | Planned, Forced | [6 empty] | MCCAMPBE | PORTLAND | MCCAMP_PORTLA1 | SPORWH28
AEP | Melon Creek - Refugio | LN | 138 | 18/10 | DCKT Hecker - Whitepoint 138 kV | Rincon - Whitepoint 138 kV | RT | Planned | [6 empty] | MELONCRE | REFUGIO | MELONC_REFUGI1 | SMELREF8
AEP | Melon Creek - Rincon | LN | 138 | 18/10, 18/11 | DCKT Hecker - Whitepoint 138 kV, Airline Aep - … - Westside Aep 138 kV | Dupont Switch Ingleside - Rincon 138 kV, Arcadia - Southside 138 kV | RT | Planned, Forced | [6 empty] | RINCON | MELONCRE | MELONC_RINCON1 | SMELRIN8
AEP | Musquiz - Pig Creek | LN | 138 | 17/9 | Yucca Drive Sw to Wolf Switching Station 138 kV | Andrews County South - Amoco Three Bar Tap 138 kV, No Trees Sw - Cheyenne Tap 138 kV | RT | Planned | [6 empty] | PIGCREEK | MUSQUIZ | MUSQUI_PIGCRE1 | MLOTPIG8
AEP | Mvec (Rangerville) - … - Wesmer | LN | 138 | 18/2 | Polk Avenue to North Pharr 138 kV | North McAllen - West McAllen 138 KV | RT | Planned | [6 empty] | MVRANGER | MESQUITE | MESQUI_MVRANG1 | SMVRWES8
AEP | North Edinburg - … - North Pharr | LN | 138 | 18/9 | DCKT North Edinburt - West Edinburg Sub & Palmhurst Sub 138kV | North Edinburg - North McAllen 138 kV | RT | Planned | [6 empty] | NEDIN | MCOLL_RD | MCOLL__NEDIN1 | SN_ANED8
AEP | North Edinburg - Lon Hill | LN | 345 | 17/3, 15/3, 16/3 | Nelson Sharpe to Ajo 345 kV, Nelso Sharpe to Ajo 345 kV, DCKT Rio Hondo to North Edinburg 345 kV & Harlingen Sw 138 kV, Valley GTC | Raymondville 2 - Yturria Sub 138 kV, Celanese Bishop - Nelson Sharpe 138 kV, Burns Sub - Rio Hondo 138 kV, N/A | RT, ST | Planned, Forced | [6 empty] | NEDIN | LON_HILL | LON_HI_NEDIN1 | SNEDLON5
AEP | North Edinburg - Pomelo | LN | 345 | 16/10, 17/1 | Valley GTC | N/A | ST | Planned | Y | [5 empty] | NEDIN | POMELO | NEDIN_POMELO1 | SPOMNED5
AEP | North Edinburg - Rio Hondo | LN | 345 | 16/3 | North Edinburg to Lon Hill 345 kV | Burns Sub - Rio Hondo 138 kV | ST | Planned | [6 empty] | NEDIN | RIOHONDO | NEDIN_RIOHON1 | SNEDRIO5
AEP | North Edinburg Auto 138 345/138 kV | XF | 345 | 17/2, 19/4 | North Edinburg Auto 1382 345/138 kV | Burns Sub - Rio Hondo 138 kV, Haine Drive - La Palma 138 kV | RT | Planned, Forced | [6 empty] | NEDIN |  | 138H | XNED358
AEP | North Edinburg Bus #1 (CB 5010, etc.) | BUS | 138 | 16/9 | North McAllen to North Edinburg 138 kV | North Edinburg - McColl Road 138 kV | ST | Planned | [6 empty] | NEDIN |  | 8BB2 | N/A
AEP | North McAllen - North Pharr | LN | 138 | 17/5 | Pharr Magic Valley to North Pharr 138 kV | North McAllen - West McAllen 138 KV | RT | Planned | [6 empty] | N_MCALLN | PHARR | N_MCAL_PHARR1 | SPHAN_M8
AEP | Paint Creek Bus #1 (CB 4135, etc.) | BUS | 138 | 16/5, 16/6, 17/1 | Scurry Sw to Sun Sw 138 kV, Salt Creek Bepc to Salt Creek Reactor 138 kV | Eskota Sw - Longworth 69 kV, Aspermont Auto 69T1 138/69 kV | ST | Planned | [6 empty] | PAINTCRE |  | 8BB1 | N/A
AEP | Pig Creek - Solstice | LN | 138 | 17/9 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV | RT | Planned |  | AEP | AEP will be open ending the overloaded element, BARL - FTSW 69 kV due to this. Also 138 kV upgrades at Saragosa should relieve congestion |  |  |  | PIGCREEK | SOLSTICE | PIGCRE_SOLSTI1 | SPIGSOL8
AEP | Port Aransas - Seawall Aep | LN | 69 | 17/3, 18/1 | DCKT Whitepoint to McCambell & Dupons Sw Ingleside 138 kV, DCKT Whitepoint to Hecker & Dupont Sw Ingleside 138 Kv, Barney Davis to Nelson Sharpe 138 kV, Nelson Sharpe Auto Trx Xf1 345/138 kV | Whitepoint - Rincon 138 kV, Rodd Field - Holly 138 kV | RT | Planned, Forced | [6 empty] | PORT_A | SEAWALL | PORT_A_SEAWAL1 | SSEAPO29
AEP | Rincon - Whitepoint | LN | 138 | 19/2 | McCampbell - … - Whitepoint 138 kV | Whitepoint TRX 138_69A1 138/69 kV | RT | Planned | [6 empty] | WHITE_PT | RINCON | RINCON_WHITE_2 | SRINWHI8
AEP | Rusthill - San Angelo Concho | LN | 138 | 15/6 | San Angelo College Hills Auto 69T1 138/69 kV | San Angelo Power Station Auto 69T1 138/69 kV | RT | Forced | [6 empty] | CONCHO | RUSTHILL | CONCHO_RUSTHI1 | SRUSCON8
AEP | San Angelo Red Creek Auto T2 345/138 kV | XF | 345 | 16/10 | San Angelo Red Creek Auto T1 345/138 kV | Nicole - Orient 138 kV | RT | Planned | [6 empty] | REDCREEK |  | T2H | XSA3R58
AEP | Sonora Auto 69-1 138/69 kV | XF | 138 | 18/3 | North McCamey to Santa Rita 138 kV | Santiago - San Angelo Power Station 138 kV | RT | Planned |  | AEP | MTE is remote to overloaded element. Not close to each other. |  |  |  | SONR |  | 69-1 | XSON89
AEP | Stewart Road Auto ST1 138/69 kV | LN | 138 | 18/9 | DCKT North Edinburt - West Edinburg Sub & Palmhurst Sub 138kV | North Edinburg - North McAllen 138 kV | RT | Planned | [6 empty] | STEWART |  | ST1 | XSTE89
AEP | Weil Tract - Westside Aep | LN | 138 | 18/11 | DCKT Citgo N Oak Park 0 Hiway 9 138 kV & Hiway 9 - Industrial Aep 69 kV | Morris Street - Nueces Bay 138 kV | RT | Planned | [6 empty] | SEIL_TRC | WESTSIDE | WEIL_T_WESTSI1 | SWEIWES8
AEP | West Batesville Bus #1 (CB 1005, etc.) | BUS | 138 | 15/4 | Lobo to San Miguel 345 kV | Hamilton Road - Maverick 138 kV | ST | Planned | [6 empty] | W_BATESV |  | 1381 | N/A
AEP | Whitepoint Auto 345A 345/138 kV | XF | 345 | 18/3 | Lon Hill Auto Trx Lon_Hill_3_2 345/138 kV | Lon Hill Auto 381H 345/138 kV | RT | Forced | [6 empty] | WHITE_PT |  | 345A | XWHI58
AEP, BRAZOS | Scurry Switch - … - Spur | LN | 138 | 16/3, 16/10 | Aspermont Aep to Spur 138 kV | Spur Auto 69_1 138/69 kV | ST | Planned | Y, N | [5 empty] | SCURRYSW | SCK | SLTCRK_SCRYSW | SSPUMW18
AEP, CNP | South Texas Project - Whitepoint | LN | 345 | 17/9, 17/11, 17/12, 18/1, 18/3 | Lon Hill to Coleto Creek 345 kV, DCKT San Miguel Gen to Elmcreek 345 kV, DCKT Haisley to Warburton Road Switching Station 138 kV & Lon Hill to Coleto Creek 345 kV, San Miguel Auto 345_138 kV Switchyards Trx SANMGL8_3_1 345/138 kV, Dyann to Wharton 138 kV, Danevang Switching Station to Blessing 138 kV | Lon Hill - Pawnee Switching Station 345 kV, Pawnee Switching Station - Calaveras 345 kV, Blessing Auto 69A1 138/69 kV, El_Campo - Lane City Pump 138 kV | RT | Forced | [6 empty] | WHITE_PT | STP | STPZWP39 | SWHISTP5
AEP, CROSS | Gray - Tesla (GRAY_TESLA_1) | LN | 345 | 17/1 | Panhandle GTC | N/A | RT | Forced | [6 empty] | CTT_GRAY | TESLA | GRAY_TESLA_1 | SCTTTES5
AEP, CROSS, SHARYLAND Oncor | Tesla - … - Tule Canyon (1) | LN | 345 | 16/5, 16/11, 16/12 | Panhandle GTC | N/A | RT, ST | Planned, Forced | [6 empty] | TESLA | CTT_CROS | CROSS_TESLA_1 | SCTTTE45
AEP, CROSS, SHARYLAND Oncor | Tesla - … - Tule Canyon (2) | LN | 345 | 16/5, 16/11, 16/12 | Panhandle GTC | N/A | RT, ST | Planned, Forced | [6 empty] | TESLA | CTT_CROS | CROSS_TESLA_2 | SCTTTE55
AEP, ETT | Cenizo - … - Del Sol | LN | 345 | 18/5, 19/1 | Basecase, Lobo - San Miguel Gen 345 kV | Valley Import, North Laredo Switch - Piloncillo 138 kV | RT | Forced | [6 empty] | CENIZO | CABEZNTP | CABEZN_CENIZO1 | SCE2DEL5
AEP, ETT | Clear Crossing - … - Edith Clarke (CLEARC_GAUSS2) | LN | 345 | 17/7, 17/8, 17/9 | Basecase | Panhandle GTC | RT | Planned | [6 empty] | CLEARCRO | GAUSS | CLEARC_GAUSS2 | SGAUED35
AEP, ETT | Edith Clarke - Riley (Edithc_Riley1) | LN | 345 | 17/10, 17/11, 17/12, 18/1, 18/2, 18/3 | Panhandle GTC | N/A | RT | Planned | [6 empty] | EDITHCLA | RILEY | EDITHC_RILEY1 | SRILED15
AEP, ETT | Edith Clarke - Riley (Edithc_Riley2) | LN | 345 | 17/10, 17/11, 17/12, 18/1, 18/2, 18/3 | Panhandle GTC | N/A | RT | Planned | [6 empty] | EDITHCLA | RILEY | EDITHC_RILEY2 | SRILED25
AEP, LCRA | Mesa View Switch - … - Tunas Creek | LN | 138 | 18/3 | North McCamey to Santa Rita 138 kV | Santiago - San Angelo Power Station 138 kV | RT | Planned |  | AEP | LCRA installing Tippet station. |  |  |  | INDNENR | MEVISW | 33T620 | SINDRIO8
AEP, LCRA | Naval Base - … - Port Aransas | LN | 69 | 17/4, 18/10, 18/11 | Hecker to WhitePoint 138 kV, Airline Aep - … - Westside Aep 138 kV, DCKT Citgo N Oak Park 0 Hiway 9 138 kV & Hiway 9 - Industrial Aep 69 kV, DCKT Hecker - Whitepoint 138 kV | Whitepoint - Rincon 138 kV, Arcadia - Southside 138 kV, Morris Street - Nueces Bay 138 kV, Dupont Switch Ingleside - Rincon 138 kV | RT | Planned | [6 empty] | NVLBASE | N_PADRE | NVLBAS_N_PADR1 | SSEAPO19
AEP, ONCOR | Clear Crossing - … - Dermott Switch (DMTSW_KIRCHH1) | LN | 345 | 18/4, 18/5, 18/6, 18/7, 18/8, 18/9, 18/11, 18/12 | DCKT Dermott Sw to Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | [6 empty] | CLEARCRO | KIRCHHOF | CLEARC_KIRCHH1 | SKIRDMT5
AEP, ONCOR | Clear Crossing - … - Dermott Switch (DMTSW_KIRCHH2) | LN | 345 | 18/4, 18/5 | DCKT Dermott Switch to Scurry County South Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | [6 empty] | CLEARCRO | KIRCHHOF | CLEARC_KIRCHH2 | SKIRDM35
AEP, ONCOR, TNMP | Lotebush - … - Yucca Drive Switch | LN | 138 | 18/5 | Fort Stockton Plant - Rio Pecos 138 kV | 16th Street Tnp - Woodward 2 138 kV, Rio Pecos - Woodward 2 138 kV | RT | Forced | [6 empty] | YUCSW | LOTEBUSH | 6332_A | SHACPB38
AEP, SHARYLAND Oncor | Frontera - … - Railroad | LN | 138 | 18/3 | Polk Avenue to North Pharr 138 kV (This item was added to the list because of buildings located within the possible sag of the line at certain loads. This issue has been resolved by removing or lowering the buildings in question.) | North McAllen - West McAllen 138 KV | RT | Planned |  | Sharyland (Jesse Merriweather) | The obstruction has been removed and the line conditions have been returned to normal |  |  |  | FRONTERA | S_MISSIN | BENTS_FRTER_1B | SS_MRAI8
AEP, SHARYLAND Oncor | North Edinburg - Palmito | LN | 345 | 18/1 | Basecase | Valley Import | RT | Forced | [6 empty] | NEDIN | PALMITO | NEDIN_PALMIT1 | SPALNED5
AEP, STEC | Blessing - Danevang Switching Station | LN | 138 | 17/5 | DCKT Victoria to Victoria Dupont Sw & Victoria Dupont Sw to Victoria 138 kV | Formosa - Lolita 138 kV | RT | Planned | [6 empty] | DANEVA | BLESSING | DANEVANG | SDANBLE8
AEP, STEC | Calallen Sub - … - Stadium Aep | LN | 69 | 18/3 | Lon Hill Auto 382H 345/138 kV | Lon Hill Auto 381H 345/138 kV | RT | Planned |  | AEP | Believe this is an error. 69 kV line should not cause overload on 345 kV auto. |  |  |  | CALALS | BANQUETE | 3023 | MGILSTA9
AEP, STEC | George West Switching Station - Orange Grove Switching Station | LN | 138 | 18/1 | San Miguel Auto 345_138 kV Switchyards Trx Sanmgl8_3_2 345/138 kV | San Miguel Gen Auto ATBH 345/138 kV | RT | Forced | [6 empty] | GEORGWST | ORNGROV | GEW_ORN | SGEOORN8
AEP, STEC | Lobo - San Miguel | LN | 345 | 15/11, 16/4 | Rio Bravo to Zapata 138 kV, Javalina Tap to Rio Bravo 138 kV | Freer - San Diego 69 kV, Voltage Collapse | ST | Planned | [6 empty] | LOBO | SANMIGL | LOBO_SANMGS1 | SLOBSA25
AEP, STEC | Lon Hill - Orange Grove Switching Station | LN | 138 | 18/1 | San Miguel Auto 345_138 kV Switchyards Trx Sanmgl8_3_2 345/138 kV | San Miguel Gen Auto ATBH 345/138 kV | RT | Forced | [6 empty] | ORNGROV | LON_HILL | LON_HI_ORNGR0 | SORNLON8
AEP, WET | Edith Clarke - Wett_Cottonwood (COTTON_EDITHC3) | LN | 345 | 16/11, 16/12, 17/1, 17/2, 17/3, 17/4, 17/5, 17/6 | Panhandle GTC | N/A | RT, ST | Planned, Forced | [6 empty] | EDITHCLA | W_CW_345 | COTTON_EDITHC3 | SW_CED55
AEP, WET | Edith Clarke - Wett_Cottonwood (COTTON_EDITHC4) | LN | 345 | 16/11, 16/12, 17/1, 17/2, 17/3, 17/4, 17/5, 17/6 | Panhandle GTC | N/A | RT, ST | Planned, Forced | [6 empty] | EDITHCLA | W_CW_345 | COTTON_EDITHC4 | SW_CED45
AEP/STEC (This should be shared with STEC) | Hwy 511 Sub - South Carbide | LN | 138 | 16/6 | South Carbide to Loma Alta Sub 138 kV | La Palma - Villa Cavazos 138 kV | ST | Planned | [6 empty] | SCARBIDE | MV_HW511 | HWY511_SCARBID | SMV_SCA8
BPUB | Loma Alta Substation - Waterport Substation | LN | 138 | 16/5, 18/1 | South Carbide to Loma Alta Sub 138 kV, Loma Alta Sub T1 138/69 kV, La Palma to East Harrison 69 kV | La Palma - Villa Cavazos 138 kV, Haine Drive - La Palma 138 kV | RT | Planned, Forced | [6 empty] | WATERPRT | LOMA_ALT | WP_LA | SWATLO28
BPUB | Palo Alto Sub - Titan Sub | LN | 138 | 16/5 | South Carbide to Loma Alta Sub 138 kV, Loma Alta Sub T1 138/69 kV | La Palma - Villa Cavazos 138 kV | RT | Planned | [6 empty] | PALOALTO | TITAN_SU | PALOAL_TITAN_1 | SPALSCA8
BPUB | Power Plant Substation - Sixth Street Substation | LN | 138 | 18/3, 18/4 | DCKT San Miguel Gen to Elmcreek 345 kV, Kendall to Cagnon 345 kV | Pawnee Switching Station - Calaveras 345 kV, CICO - Comfort 138 kV | RT | Planned | [6 empty] | SILASRAY | SIXTH_ST | PP_6ST | SSIXSIL8
BPUB | Sixth Street Substation - South Plant Substation | LN | 138 | 18/3, 18/4 | DCKT San Miguel Gen to Elmcreek 345 kV, Kendall to Cagnon 345 kV; | Pawnee Switching Station - Calaveras 345 kV, CICO - Comfort 138 kV | RT | Planned | [6 empty] | SOUTH_PL | SIXTH_ST | 6ST_SP | SSIXSOU8
BPUB | Southmost Sub - Waterport Sub | LN | 138 | 18/1 | Lon Hill to Coleto Creek 345 kV, La Palma to East Harrison 69 kV, DCKT Jewett to Singleton 345 kV | Warburton Road Switching Station - Victoria 138 kV, Btu Jack Creek - Twin Oak Sw 345 kV | RT | Forced | [6 empty] | WATERPRT | SOUTHMOS | WP_SM | SSOUWAT8
BPUB, TMPA | Btu_Jack_Creek - Gibbons Creek | LN | 345 | 17/4, 16/1 | DCKT Jewett to Singleton 345 kV | Gibbons Creek - Twin Oak Sw 345 kV, BTU_Jack_Creek Auto XF1 345/138 kV | RT, ST | Planned | Y | [5 empty] | GIBCRK | JK_CK | GC_JK | SJK_GIB5
BRAZON, ONCOR | Carrollton Northwest - … - Collin Ses & Legacy | LN | 138 | 18/11 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Arco - Cooper Creek Substation 138 kV | RT | Planned | [6 empty] | CRLFR | CRLNW | 815_H | SHBRCR48
BRAZOS | Hasse Auto Xfm1 138/69 kV | XF | 138 | 17/11 | Brownwood Sw to Mercers Gap Sw 138 kV, Comanche Sw (Oncor) to Mercers Gap Sw | Has Auto XFM2 138/69 kV | RT | Forced | [6 empty] | HAS |  | XFM1 | XHA2S89
BRAZOS | Hilltop Lakes - Watson Chapel | LN | 138 | 17/8 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned | [6 empty] | HLK | WATSONCP | WAT_HLK | SHLKJEW8
BRAZOS | Jaybird - Rw Miller | LN | 138 | 16/11 | Mineral Wells to Mineral Wells West 138 kV | Bunker - RW Miller 138 kV | ST | Planned | [6 empty] | MIL | JAYBIRD | JYBRD_MIL | SSTVMIL8
BRAZOS | Jaybird - Stephenville Bepc | LN | 138 | 16/11 | Mineral Wells to Mineral Wells West 138 kV | Bunker - RW Miller 138 kV | ST | Planned | [6 empty] | JAYBIRD | STV | JYBRD_STV | SJAYSTV8
BRAZOS | Krugerville - … - Navo | LN | 138 | 15/10 | Jim Christal Sub to West Denton 138 kV | Pockrus Sub - Teasely Sub 138 kV | ST | Forced | [6 empty] | NAVO | OKPNTSS | NAVO_OKPNTS1 | SCNSARC8
BRAZOS | Lewisville Switch Auto FMR2 345/138 kV | XF | 345 | 17/4 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned | [6 empty] | LWSSW |  | FMR2 | XLWS158
BRAZOS ONCOR, BPUB (Changed operatorship to Oncor and BPUB) | Loma Alta - Palmito | LN | 138 | 18/9 | DCKT North Edinburt - West Edinburg Sub & Palmhurst Sub 138kV | North Edinburg - North McAllen 138 kV | RT | Planned | [6 empty] | LOMA_ALT | PALMITO | LOMA_PAL | SWATLO18
BRAZOS | Stephenville Bepc Auto FMR1 138/69 kV | XF | 138 | 15/3 | Oran Sub to Mineral Wells & RW Miller 138 kV | Bunker - RW Miller 138 kV | ST | Planned | [6 empty] | STV |  | FMR1 | XSTV289
BRAZOS | Whitney Bus 1525 (CB 5075, etc.) | BUS | 138 | 16/12 | Bosque Sw to Elm Mott 345 kV | Bosque Sw - Rogers Hill Bepc 138 kV | ST | Forced | [6 empty] | WHTNY |  | 1525 | N/A
BRAZOS | Whitney Bus BB1 (CB 210, etc.) | BUS | 69 | 16/12 | Bosque Sw to Elm Mott 345 kV | Bosque Sw - Rogers Hill Bepc 138 kV | ST | Forced | [6 empty] | WHTNY |  | BB1 | N/A
BRAZOS, ONCOR (Removed Brazos as operator) | Allen Switch- … - Anna Switch | LN | 138 | 19/2 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Arco - Cooper Creek Substation 138 kV | RT | Planned | [6 empty] | ALNSW | ALLEN | 535_A | SMCWANA8
BRAZOS, ONCOR | Carrollton Northwest - Lewisville Switch (105_A) | LN | 345 | 2018 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | ADD | [7 empty] | CRLNW | LWSSW | 105_A | SLWSCRL5
BRAZOS, ONCOR | Carrollton Northwest - Lewisville Switch (83) | LN | 345 | 17/3 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned | [6 empty] | CRLNW | LWSSW | 83 | SKRWCR25
BRAZOS, TMPA | Gibbons Creek - Keith Switch 138 kV | LN | 138 | 16/10 | Gibbons Creek to Btu_East 138 kV | Gibbons Creek - Btu_Greens_Prairie 138 kV | RT | Planned | [6 empty] | GIBCRK | KEITHSW | GIBC_KEISW | SKEIGIB8
BTU | Btu_Atkins - Btu_Dansby | LN | 138 | 17/3 | Btu_Industrial_Park to Btu_North 69 kV | Btu_East - Btu_Shady_Lane 69 kV | RT | Planned | [6 empty] | DANSBY | ATKINS | DANSBY_ATKINS | SATKDAN8
BTU | Btu_Dowling - Btu_Enterprise | LN | 138 | 18/3 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Forced | [6 empty] | DOWLNG | ENTERPR | DOWL_ENT | SDOWENT8
BTU | Btu_East - Btu_Shady_Lane 69 | LN | 69 | 16/6 | Btu_Atkins Auto FMR1 138/69 kV | Btu_Briarcrest - Btu_Nall_Lane 69 kV | RT | Forced | [6 empty] | EAST | SHADY_LN | SHA_EAST | SSHAEAS9
CNP | Alta Loma - Ph Robinson | LN | 138 | 18/5 | DCKT Sr Bertron - Dowlap & Quanab 138 kV | Angleton - Liverpool 138 kV | RT | Forced |  | CNP | Congestion caused by multiple forced outages related to the failure of PHR A4. Reconfiguration and replacement projects have since been completed to relieve this congestion. TPIT: 6312B & 43531 |  |  |  | PHR | AL | AL_PHR93 | SALPHR8
CNP | Baytown - … - Haney | LN | 138 | 18/5 | DCKT Cedar Bayou Plant - Quanum & Strang 138 kV | Diamond Battleground - Moment 138 kV | RT | Planned |  | CNP | Congestion caused by multiple forced outages related to the failure of PHR A4. Reconfiguration and replacement projects have since been completed to relieve this congestion. TPIT: 6312B & 43531 |  |  |  | BT | HL | BT_HL_66 | SHNYBT8
CNP | Bellaire - … - Britmoore | LN | 138 | 19/4 | Meadow - PH Robinson 345 kV | Alvin Tnp - Mainland Tnp 138 kV | RT | Planned |  | CNP | The cause of congestion is unlikely and we are unable to recreate. The outage in question is a 138kV line on the west side of our system, and is one of many parallel paths between major substations. A 345kV contignency on the East side of our system should not cause congestion on our Eastern 138kV ties when paired with this outage. |  |  |  | BI | BM | BI_UL_24 | SULBI8
CNP | Bellaire - Wa Parish | LN | 345 | 16/10 | DCKT Wa Parish to Jeanetta 345 kV | Bellaire - Smithers 345 kV | ST | Planned | [6 empty] | BI | WAP | BI_WAP50 | SBIWAP5
CNP | Blessing - South Texas Project | LN | 345 | 18/12 | DCKT Wa Parish - Bailey & Hillje 345 kV | Jones Creek - South Texas Project 345 kV | RT | Planned, Forced | [6 empty] | STP | BLESSING | BLESSING | SBLESTP5
CNP | Bunker - H O Clarke | LN | 138 | 18/11 | Meadow - North Alvin Tap 138 kV | Grant - Teco 138 kV | RT | Planned |  | CNP | Project to increase rating of line 37 Teco to Grant Completed TPIT: 5767 |  |  |  | BUN | HOC | BUNHOC08 | SBUNHO28
CNP | Camden - Surfsi | LN | 138 | 18/12 | DCKT Wa Parish - Bailey & Hillje 345 kV | Dow Chemical - South Texas Project 345 kV | RT | Planned, Forced |  | CNP | Line does not exist. |  |  |  | SRF | VL | SRFVL_59 | SSRFV2L8
CNP | Chambers - King | LN | 345 | 17/9, 17/10, 18/3 | Meadow to Oasis 345 kV, Ph Robinson to Center 345 kV, DCKT Crown to Tanker & Davson to Greens Bayou 138 KV | Angleton - Liverpool 138 kV, Channelview - Lynch 138 kV, Exxon - Lynch 138 kV, Bigvue - Power Systems - Arco Cogen 138 kV | RT | Planned, Forced |  | CNP | Congestion caused by multiple forced outages related to the events of Harvey. Multiple 345kV lines were taken out to repair errosion, which coincided with multiple planned 138kV outages to create congestion. |  |  |  | CHB | KG | CHBKG_97 | SCHBKG5
CNP | Crosby - Power Systems Arco Cogen | LN | 138 | 19/3 | DCKT Chambers - King & Jordan - North Belt 345 kV | Bigvue - Power Systems Arco Cogen 138 kV | RT | Planned, Forced | [6 empty] | CS | HNY | CS_HL_08 | SHLC6S8
CNP | Derick - South Channel | LN | 138 | 18/5 | DCKT Cedar Bayou Plant - Quanum & Strang 138 kV, DCKT Sr Bertron - Dowlap & Quanab | Diamond Battleground - Moment 138 kV, Angleton - Liverpool 138 kV | RT | Planned |  | CNP | Congestion caused by multiple forced outages related to the failure of PHR A4. Reconfiguration and replacement projects have since been completed to relieve this congestion. TPIT: 6312B & 43531 |  |  |  | DER | SC | DERSC_85 | SDERSC8
CNP | Dow Chemical - South Texas Project | LN | 345 | 18/12, 19/1, 19/3 | DCKT Wa Parish - Bailey & Hillje 345 kV | Jones Creek - South Texas Project 345 kV | RT | Planned | [6 empty] | STP | DOW | DOWSTP27 | SSTPDOW5
CNP | Freeport - Surfsi | LN | 138 | 18/12 | DCKT Wa Parish - Bailey & Hillje 345 kV | Dow Chemical - South Texas Project 345 kV | RT | Planned, Forced | [6 empty] | FP | SRF | FP_SRF59 | SFPSRF8
CNP | Garrott - Kirby (GT_KB_37) | LN | 138 | 17/9 | Meadow to Oasis 345 kV | Angleton - Liverpool 138 kV | RT | Planned |  | CNP | Congestion caused by multiple forced outages related to the events of Harvey. Multiple 345kV lines were taken out to repair errosion, which coincided with multiple planned 138kV outages to create congestion. |  |  |  | GT | KB | GT_KB_37 | SGTKB8
CNP | Greens Bayou - … - Lychem | LN | 138 | 18/5 | DCKT Cedar Bayou Plant - Quanum & Strang 138 kV | Diamond Battleground - Moment 138 kV | RT | Planned, Forced |  | CNP | Congestion caused by multiple forced outages related to the failure of PHR A4. Reconfiguration and replacement projects have since been completed to relieve this congestion. TPIT: 6312B & 43531 |  |  |  | UV | GBY | GBYUV_08 | SLHMGB28
CNP | Greens Bayou Auto AT2 | XF | 345 | 16/2 | DCKT Greens Bayou to King 345 kV | Greens Bayou Auto AT1 345/138 kV | ST | Planned | [6 empty] | GBY |  | AT2 | XGB2Y58
CNP | H O Clarke - … - Southwyck | LN | 138 | 18/3 | DCKT Crown to Tanker & Davson to Greens Bayou 138 KV | Bigvue - Power Systems - Arco Cogen 138 kV | RT | Planned |  | CNP | HOC-SO 05 has been reconfigured and is currently a radial and the congestion has not occurred since. |  |  |  | HOC | IR | HOCIR_05 | SIRSO8
CNP | Hillje - Wa Parish (HLJWAP64) | LN | 345 | 16/3 | DCKT South Texas Project to Dow Chemial & Jones Creek 345 kV | South Texas Project - Wa Parish 345 kV | RT | Planned | [6 empty] | HLJ | WAP | HLJWAP64 | SHLJWA25
CNP, TNMP | Hidden Lakes Tnp - PH Robinson | LN | 138 | 18/12 | Lane City - South Lane City 138 kV | Franklins Camp Sub - Sargent Sub 69 kV | RT | Planned, Forced |  | CNP | Congestion was likely due to other outages. The outage, contingency, and overload are ties to separate islands. It is unlikely the three are related. |  |  |  | HDNLAKES | PHR | G138_8A | SPHRHDN8
CNP | Jones Creek - South Texas Project | LN | 345 | 18/12, 19/1, 19/4 | DCKT Wa Parish - Bailey & Hillje 345 kV, DCKT Hillje - Wa Parish & Bailey 345 kV | Dow Chemical - South Texas Project 345 kV | RT | Planned | [6 empty] | JCK | STP | JCKSTP18 | SJCKSTP5
CNP | Jewett - Limestone (225) | LN | 345 | 15/3 | DCKT Limestone to Twin Oak Sw 345 kV | Big Brown Ses - Jewet (50) | ST | Planned |  | CNP | Houston Import Project system upgrades completed in 2018 allievates congenstion. TPIT: 3937 |  |  |  | JEWET | LEG | 225 | SLEGJE35
CNP | Jordan - North Belt | LN | 345 | 17/9, 17/10 | Meadow to Oasis 345 kV, Ph Robinson to Center 345 kV | Angleton - Liverpool 138 kV, Channelview - Lynch 138 kV, Exxon - Lynch 138 kV | RT | Forced |  | CNP | Congestion caused by multiple forced outages related to the events of Harvey. Multiple 345kV lines were taken out to repair errosion, which coincided with multiple planned 138kV outages to create congestion. |  |  |  | JOR | NB | JORNB_99 | SCBYNB5
CNP | New Gulf - South Lane City | LN | 138 | 15/12 | DCKT Wharton to East Bernard & Dyann 138 kV (UNSOLVED) | N/A | ST | Planned |  | CNP | Has not occurred again. No issues with internal case solving |  |  |  | LC | NEW | LC_NEW60 | STGFLC8
CNP | Ph Robinson - Webster | LN | 138 | 18/5 | DCKT Sr Bertron - Dowlap & Quanab 138 kV | Angleton - Liverpool 138 kV | RT | Forced |  | CNP | Congestion caused by multiple forced outages related to the failure of PHR A4. Reconfiguration and replacement projects have since been completed to relieve this congestion. TPIT: 6312B & 43531 |  |  |  | PHR | WEB | PHRWEB93 | SWEBPHR8
CNP, CPS | Elm Creek - South Texas Project (STPELM18) | LN | 345 | 16/4 | DCKT Marion to Clear Springs & Zorn 345 kV | Comal - Henne 138 kV | ST | Planned | [6 empty] | STP | ELMCREEK | STPELM18 | SELMST25
CNP, CPS | Elm Creek - South Texas Project (STPELM27) | LN | 345 | 16/4 | DCKT Marion to Clear Springs & Zorn 345 kV | Comal - Henne 138 kV | ST | Planned | [6 empty] | STP | ELMCREEK | STPELM27 | SELMSTP5
CNP, TNMP | Gaf Tnp - Ph Robinson | LN | 138 | 18/1 | Caddo Sw Sta Tnp to Greenbelt Tnp 138 kV | Tejas Tnp - Comanche Sw Tnp 138 kV | RT | Planned | [6 empty] | PHR | GAF | GAF_PHR | SGAFPHR8
CNP | White Oak Auto AT3 345/138 kV | XF | 345 | 16/6 | DCKT Britmoore to Sauer 138 kV | Bellaire - San Felipe 138 kV | RT | Planned |  | CNP | Project to increase rating of line 09 Bellaire to San Felipe Completed TPIT:4703A |  |  |  | WO |  | AT3H | XW2O58
CPS | Cagnon - Calaveras | LN | 345 | 17/8 | DCKT Calaveras to Skyline 345 kV | Braunig - Cagnon 345 kV | RT | Forced | [6 empty] | CALAVERS | CAGNON | N5_R5 | SCAGCA25
CPS | Calaveras - Skyline (N5_P4) | LN | 345 | 17/5, 17/12 | DCKT Cagnon to Braunig & Calaveras to Cagnon 345 kV, DCKT Hill Country to Marion 345 kV | Skyline - Calaveras 345 kV, Pawnee Switching Station - Calaveras 345 kV, Skyline - Elmcreek 345 kV | RT | Planned, Forced | [6 empty] | CALAVERS | SKYLINE | N5_P4 | SSKYCA25
CPS | Calaveras - Skyline (N5_P4_2) | LN | 345 | 17/12 | DCKT Cagnon to Braunig & Calaveras to Cagnon 345 kV, DCKT Hill Country to Marion 345 kV | Pawnee Switching Station - Calaveras 345 kV, Pawnee Switching Station Auto XF1 345/138 kV, Skyline - Elmcreek 345 kV | RT | Planned | [6 empty] | CALAVERS | SKYLINE | N5_P4_2 | SSKYCAL5
CPS | Howard - Somerset | LN | 138 | 17/12, 18/1 | DCKT Castrvll to Razorbac & Txresrch 138kV | Hondo Creek Switching Station - Moore Switching Station 138 kV | RT | Planned | [6 empty] | S1 | E3 | E3_S1 | SE3S18
CPS | Randolph - Weiderstein | LN | 138 | 15/9 | DCKT Skyline to Harmony & Nachches 138 kV | Fratt - Parkway Lcra 138 kV | ST | Planned | Y | [5 empty] | WEIDER | W2 | WEIDER_RAND | SW2WEI8
CPS, STEC | Calaveras - Pawnee Switching Station | LN | 345 | 17/8, 19/2 | DCKT Calaveras to Skyline 345 kV, DCKT Elmcreek - Skyline 345 kV | Braunig - Cagnon 345 kV, Hill Country - Marion 345 kV | RT | Planned, Forced | [6 empty] | PAWNEE | CALAVERS | PAWNEE_SPRUCE | SPAWCAL5
CROSS | Gray - Railhead | LN | 345 | 16/3, 16/5 | Panhandle GTC, Panhandle GTC, DCKT Alibates to Tule Canyon 345 kV | N/A, N/A, Low Voltage in Panhandle area | RT, ST | Planned | Y | [5 empty] | RAILHEAD | CTT_GRAY | RAILHD_GRAY | SRAICTT5
CROSS | Gray South Bus (CB GY_BKR_G130, etc.) | BUS | 345 | 16/5 | DCKT Alibates to Tule Canyon 345 kV | Low Voltage in Panhandle area | ST | Planned | Y | [5 empty] | GTT_GRAY |  | 1002 | N/A
CROSS, SHARYLAND Oncor | Alibates - Gray | LN | 345 | 16/3, 16/5 | Panhandle GTC, DCKT Alibates to Tule Canyon 345 kV | N/A, Low Voltage in Panhandle area | ST | Planned | Y | [5 empty] | ALIBATES | CTT_GRAY | ALIBATE_GRAY_1 | SCTTAL15
DME | Cooper Creek Sub - Industrial Sub | LN | 138 | 15/7 | Lewisville Sw Auto FMR2 345/138 kV | Pockrus Sub - Teasely Sub 138 kV | ST | Planned |  | DME | Remove - Line Rebuild; Line Rating 700 MVA on Pockrus to Teasley 138 kV Line |  |  |  | COOPERCK | INDUSTRL | COOPERCK_IND | SINDCOO8
DME | Forth Worth - Teasley | LN | 138 | 15/10 | Denton Arco to North Denton Interchange 138 kV | Hickory - Locust 69 kV | ST | Planned |  | DME | Remove - Hickory to Locust 69 kV is on a radial feed; No overload issue due to line loading |  |  |  | TEASLEY | FTWORTH | TSL_FTW | SFTWTEA8
DME | McKinney - Woodrow Sub | LN | 138 | 19/1 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Arco - Cooper Creek Substation 138 kV | RT | Planned | [6 empty] | WOODROW | MCKINNEY | MCKINNEY_WDRW | SWOOMCK8
DME, GAR | Denton Steam Auto AT1 138/69 kV | XF | 138 | 18/4 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned |  | DME | Remove - Denton Steam is on a Radial feed |  |  |  | DENTON |  | AT1 | SSPNDEN9
DME, TMPA | Arco - North Denton | LN | 138 | 15/7, 16/4, 16/5 | DCKT Lewisville Sw to Krum West Sw & Roanoke Sw 345 kV, DCKT Roanoke Sw to West Denton & Lewisville Sw to Krum West Sw 345 kV | Teasley Sub - Pockrus Sub 138 k, Fort Worth Sub - West Denton 138 kV | RT | Planned, Forced |  | DME | Remove - Line rebuild; Upgrade Line to 700MVA from West Denton to Ft Worth to Teasley to Pockrus 198 kV Lines |  |  |  | N_DENT | ARCO | 180001_D | SDENN_D8
DME, TMPA | Arco To - Cooper Creek Sub | LN | 138 | 18/2 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned | [6 empty] | COOPERCK | ARCO | COOPERCK_ARCO | SDENCOO8
DME, TMPA | Denton Steam - … - Locust Sub & Woodrow Sub | LN | 138 | 18/3, 18/4, 19/1 | DCKT Carrollton Northwest to Lewisville Sw 345 kV, Jones Street Tnp to Lewisville Sw 138 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Ti Tnp - West Tnp 138 kV, Arco - Cooper Creek Substation 138 kV | RT | Planned | [6 empty] | DENTON | DMENODE | SPI_NODE | SWOOLOC8
DME, TMPA | Fort Worth Sub - West Denton | LN | 138 | 16/10 | DCKT Lewisville Sw to Krum West Sw & Roanoke Sw 345 kV | Jim Christal Sub - West Denton 138 kV | ST | Planned | Y | DME | Remove - MLE Switch DNWD 8051 was Replaced |  |  |  | FTWORTH | W_DENT | FTW_W_DE | SFTWW_D8
DME, TMPA | Jimchristal - West Denton | LN | 138 | 18/1 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest to Lakepointe Tnp 138 kV | RT | Planned |  | DME | Remove - West Denton to RD Wells and West Denton to Ft Worth lines are in service |  |  |  | W_DENT | JCHRSTL | AIR_W_DE | SJMCW_D8
ETT | Castrvll - … - Razorback | LN | 138 | 19/2 | DCKT Elmcreek - Skyline 345 kV | Hill Country - Marion 345 kV | RT | Planned |  | AEP | MTE and contingency are not in same area. Remote from each other. |  |  |  | QUIHI | D1 | D1_QUIHI1 | SRA2D18
ETT | Clear Crossing - West Shackelford (CLEARC_WSHACK1) | LN | 345 | 19/1, 19/2, 19/3 | DCKT Dermott Switch - Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | [6 empty] | CLEARCRO | WSHACK | CLEARC_WSHACK1 | SCLEWS15
ETT | Clear Crossing - West Shackelford (CLEARC_WSHACK2) | LN | 345 | 19/1, 19/2, 19/3 | DCKT Dermott Switch - Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | [6 empty] | CLEARCRO | WSHACK | CLEARC_WSHACK2 | SCLEWS25
GAR | Elmgrove - Wylie Switch | LN | 138 | 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned | [6 empty] | ELMGROVE | WYLIESW | WYL_ELMG | SWYLELM8
GAR | Olinger - Wylie Switch (WYL_OLI1) | LN | 138 | 16/4 | Greenville Steam to Shelby 138 kV | Shelby Auto BT1 138/69 kV | ST | Forced | [6 empty] | WYLIESW | OLINGR | WYL_OLI1 | SFIRWY18
GAR | Olinger - Wylie Switch (WYL_OLI2) | LN | 138 | 15/9, 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned | [6 empty] | WYLIESW | OLINGR | WYL_OLI2 | SOLIWY18
GAR | Olinger - Wylie Switch (WYL_OLI3) | LN | 138 | 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned | [6 empty] | WYLIESW | OLINGR | WYL_OLI3 | SOLIEL28
GEUS, TMPA | Diesel - Greenville Steam | LN | 69 | 15/7 | Shelby Auto BT1 138/69 kV | Greenville Steam Auto XT1 138/69 kV | ST | Planned | [6 empty] | DIESEL | GN_S_I | DIE_GNS | SDIEGN_9
LCRA | Andice - Bertram | LN | 69 | 19/3 | DCKT Ferguson - Granite Mountain & Wirtz - Starcke 138 kV | Flat Rock Lcra - Wirtz 138 kV | RT | Planned |  | LCRA | There were several extended LCRA outages in the area: T414 Fairland-Lago Vista 138 kV; T448 Gillespie-Horseshoe Bay 138 kV; T192 Gillespie-Ferguson 138 kV. Also, now there is a bypass at Marshall Ford with T323 Marshall Ford-Paleface and T179 Marshall Ford-Lakeway AEN that mitigates overload on T365 Flat Rock LCRA-Wirtz 138 kV |  |  |  | BERTRA | ANDICE | 427T427 | SBERAND9
LCRA | Bergheim - Kendall | LN | 345 | 19/1 | Cagnon - Kendall 345 kV | Cico - Comfort 138 kV | RT | Forced | [6 empty] | BERGHE | KENDAL | 656T656 | SHAYKE25
LCRA | Bevo Auto BEVO | XF | 138 | 15/6 | Bevo Sub to Asherton 138 kV | Hamilton Road - Maverick 138 kV | RT | Planned | [6 empty] | BEVO |  | BEVO | XBEV89
LCRA | Blanco - Devils Hill | LN | 69 | 18/11 | DCKT Ferguson - Granite Mountain & Wirtz - Starcke 138 kV | Flat Rock Lcra - Wirtz 138 kV | RT | Planned, Forced |  | LCRA | There were several extended LCRA outages in the area: T414 Fairland-Lago Vista 138 kV; T448 Gillespie-Horseshoe Bay 138 kV; T192 Gillespie-Ferguson 138 kV. Also, now there is a bypass at Marshall Ford with T323 Marshall Ford-Paleface and T179 Marshall Ford-Lakeway AEN that mitigates overload on T365 Flat Rock LCRA-Wirtz 138 kV |  |  |  | BLANCO | DEVIHI | 345T318 | SBLADEV9
LCRA | Burnet - … - Lampasas | LN | 138 | 18/09 | Ferguson - Sherwood Shores 138 kV | Cedar Valley - Trimmier 138 kV | RT | Planned |  | LCRA | There were several extended LCRA outages in the area: T414 Fairland-Lago Vista 138 kV; T448 Gillespie-Horseshoe Bay 138 kV; T192 Gillespie-Ferguson 138 kV. |  |  |  | BURNET | EBABES | 13T219 | SEBALAM8
LCRA | Clear Springs - Marion | LN | 345 | 18/2, 18/4 | DCKT Kendall to Cagnon 345 kV & Menger Creek to Ranchtwn 138 kV, Kendall to Cagnon 345 kV | CICO - Comfort 138 kV, Marion Auto AT2H 345/138 kV | RT | Planned | [6 empty] | CLEASP | MARION | 419T419 | SCLEMAR5
LCRA | Comfort - … - Raymond F Barker | LN | 138 | 18/5, 18/12 | DCKT Cagnon - Kendall 345 kV & Cico - Comfort 138 kV, DCKT Carrollton Northwest - Lewisville Switch 345 kV | Comfort - Raymond F Barker 138 kV, Arco - Cooper Creek Substation 138 kV | RT | Planned, Forced | [6 empty] | COMFOR | CYPRCR | 77T121 | SCYPCOM8
LCRA | Coronado - … - Sherwood Shores | LN | 138 | 17/11 | DCKT Granite Mountain to Ferguson & Starcke to Wirtz 138 kV | Burnet Auto AT3L 138/69 kV | RT | Planned | [6 empty] | CORONA | BUBORA | 27T635 | SBUBCOR8
LCRA | Coronado - Fairland | LN | 138 | 19/3 | DCKT Wirtz - Burnet & Starcke 138 kV | Flat Rock Lcra - Wirtz 138 kV | RT | Planned, Forced |  | LCRA | There were several extended LCRA outages in the area: T448 Gillespie-Horseshoe Bay 138 kV; T192 Gillespie-Ferguson 138 kV. Also, now there is a bypass at Marshall Ford with T323 Marshall Ford-Paleface and T179 Marshall Ford-Lakeway AEN that mitigates overload on T365 Flat Rock LCRA-Wirtz 138 kV |  |  |  | CORONA | FAIRLA | 28T110 | SFAICOR8
LCRA | Ctec Buchanan - … - Kingsland 1 | LN | 69 | 17/11 | DCKT Granite Mountain to Ferguson & Starcke to Wirtz 138 kV | Burnet Auto AT3L 138/69 kV | RT | Planned | [6 empty] | CTECBU | KING_2 | 35T291 | SKINCTE9
LCRA | Ctec Buchanan - … - Pitsburg | LN | 69 | 17/11 | DCKT Granite Mountain to Ferguson & Starcke to Wirtz 138 kV | Burnet Auto AT3L 138/69 kV | RT | Planned | [6 empty] | CTECBU | PITSBU | 34T267 | SSANPIT9
LCRA | Fairland - Lago Vista | LN | 138 | 18/09, 18/11, 19/3 | Ferguson - Sherwood Shores 138 kV, DCKT Ferguson - Granite Mountain & Wirtz - Starcke 138 kV | Cedar Valley - Trimmier 138 kV, Flat Rock Lcra - Wirtz 138 kV | RT | Planned, Forced |  | LCRA | There were several extended LCRA outages in the area: T414 Fairland-Lago Vista 138 kV; T448 Gillespie-Horseshoe Bay 138 kV; T192 Gillespie-Ferguson 138 kV. |  |  |  | FAIRLA | LAGOVI | 414T414 | SFAILAG8
LCRA | Fayette Plant 1 - Salem Lcra | LN | 345 | 17/4 | DCKT Lost Pines Aen to Austrop & Aen Dunlap 345 kV | Fayetteville Auto AT2 345/138 kV | ST | Planned | [6 empty] | FPPYD1 | SALEM | 10T211 | SSALFPP5
LCRA | Fayette Plant 138 - Fayetteville | LN | 138 | 18/5 | Piney Creek - Plum 138 kV | Fayetteville - Freisburg 138 kV | RT | Planned, Forced | [6 empty] | FAYETT | FPP138 | 171T253 | SFPPFAY8
LCRA | Fayette Plant 2 - Lytton Springs | LN | 345 | 18/10, 18/11 | DCKT Lost Pines Aen - Aen Dunlap & Austrop 345 kV | Fayetteville 345/138 kV Auto AT2 | RT | Planned |  | LCRA | AEN's Fayette Plant 2-Lytton Ckt_3122 line was out at the same time as LCRA's T255 Lytton Spring to Fayette transmission line. The two outages cause congestion, not the single outage of either transmission line. |  |  |  | LYTTON_S | FPPYD2 | 355T255 | SFPPLYT5
LCRA | Ferguson - Gillespie | LN | 138 | 18/11 | DCKT Ferguson - Granite Mountain & Wirtz - Starcke 138 kV | Flat Rock Lcra - Wirtz 138 kV | RT | Planned |  | LCRA | There were several extended LCRA outages in the area: T414 Fairland-Lago Vista 138 kV; T448 Gillespie-Horseshoe Bay 138 kV; T192 Gillespie-Ferguson 138 kV. Also, now there is a bypass at Marshall Ford with T323 Marshall Ford-Paleface and T179 Marshall Ford-Lakeway AEN that mitigates overload on T365 Flat Rock LCRA-Wirtz 138 kV |  |  |  | GILLES | FERGUS | 50T192 | SGILFER8
LCRA | Fredericksburg - … - Kendall | LN | 138 | 18/5 | DCKT Cagnon - Kendall 345 kV & Cico - Menger Creek 138 kV, DCKT Cagnon - Kendall 345 kV & Cico - Comfort 138 kV, Fredericksburg - Gillespie 138 kV | Turtle Creek - Verde Creek 138 kV, Comfort - Raymond F Barker 138 kV, Gilles TRX AT1L 138/69 kV | RT | Planned | [6 empty] | FREDER | HOLLMI | 73T120 | SFREKEN8
LCRA | Heines - Naval Base | LN | 69 | 19/4 | DCKT Whitepoint - Lon Hill & South Texas Project 345 kV | Lon Hill 345/138 kV Auto 382H | RT | Planned | [6 empty] | NVLBASE | HEINES | 685T685 | SNVLHEI9
LCRA | Hill Country - Marion | LN | 345 | 19/2 | DCKT Elmcreek - Skyline 345 kV | Hill Country - Marion 345 kV | RT | Planned | [6 empty] | MARION | HILLCTRY | HILL_MAR_1 | SHILMAR5
LCRA | Kendall - Kendall Ctec | LN | 138 | 18/5 | DCKT Cagnon - Kendall 345 kV & Cico - Comfort 138 kV | Comfort - Raymond F Barker 138 kV | RT | Planned | [6 empty] | KENDCT | KENDAL | 675T675 | SKENKEN8
LCRA | Kerrville Stadium - Verde Creek | LN | 138 | 18/5 | DCKT Cagnon - Kendall 345 kV & Cico - Menger Creek 138 kV | Turtle Creek - Verde Creek 138 kV | RT | Planned | [6 empty] | VERDCR | KERRST | 60t225 | SVERKER8
LCRA | Lakeway - Marble Falls | LN | 138 | 19/3 | DCKT Wirtz - Burnet & Starcke 138 kV | Flat Rock Lcra - Wirtz 138 kV | RT | Planned |  | LCRA | There were several extended LCRA outages in the area: T414 Fairland-Lago Vista 138 kV; T448 Gillespie-Horseshoe Bay 138 kV; T192 Gillespie-Ferguson 138 kV. |  |  |  | MARBFA | LAKEWY | 497T497 | SLAKMA28
LCRA | Lampasas - … - San Saba | LN | 138 | 17/5 | Comanche Sw (Oncor) to Mercers Gap Sw | Holder Auto FMR1 138/69 kV | RT | Planned | [6 empty] | LAMPAS | LOMETA | 25T138 | SLOMLAM8
LCRA | Marion - Zorn | LN | 345 | 16/3, 18/2, 18/4 | DCKT South Texas Project Unit 1 & 2, DCKT Kendall to Cagnon 345 kV & Menger Creek to Ranchtwn 138 kV, Kendall to Cagnon 345 kV | Marion - Clear Springs 345 kV, Marion Auto AT2H 345/138 kV, CICO to Comfort 138 kV | RT | Planned | [6 empty] | MARION | ZORN | 5T248 | SMARZOR5
LCRA | Moore Lcra DSC MOS_13021 | DSC | 138 | 16/5 | Sweetwater Downtown to Haynes Sub 138 kV | Eskota Sw - Trent 69 kV | ST | Planned | [6 empty] | MOORE_ |  | MOS_13021 | N/A
LCRA | Odlaw Switch - … - Uvalde Aep | LN | 138 | 19/2 | Bighill - Kendal 345 kV | Hamilton Road - Maverick 138kV | RT | Planned, Forced | [6 empty] | ODLASW | BLEWET | 570T570 | SBRAUVA8
LCRA | Paleface - … - Wirtz | LN | 138 | 18/5 | DCKT Cagnon - Kendall 345 kV & Cico - Menger Creek 138 kV | Turtle Creek - Verde Creek 138 kV | RT | Planned, Forced | [6 empty] | FLATRO | PALEPE | 43T365 | SPALWIR8
LCRA | Seguin - York Creek | LN | 138 | 15/9 | DCKT Zorn to Marion & Clear Springs 345 kV | Comal - Henne 138 kV | ST | Forced | [6 empty] | YORKCR | SEGUIN | 209T203 | SYORZOR8
LCRA, ONCOR | North McCamey - Odessa Ehv Switch | LN | 345 | 2018 | McCamey GTC | N/A | ADD | Planned | [6 empty] | NORTMC | ODEHV | MCCAMEY_ODESSA | SNORODE5
LCRA, STEC | Big Hill - Schneeman Draw | LN | 345 | 2018 | McCamey GTC | N/A | ADD | Planned | [6 empty] | SCHNDR | BIGHIL | SCHNDR_BIGHIL | SBAKBIG5
ONCOR | Airco Tap 2 - ... - Blackland | LN | 138 | 18/5 | Farmersville Switch - Royse Switch (381) | Farmersville Switch - Royse Switch (400) | RT | Planned, Forced | [6 empty] | ACTP2 | WMFPI | 1700_J | STRNNWT8
ONCOR | Allen Switch- Plano Tennyson | LN | 345 | 18/5 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Jones Street Tnp - Lewisville Switch 138 kV, Carrollton Northwest - Lakepointe Tnp 138kV | RT | Planned, Forced | [6 empty] | ALNSW | PTENN | 80 | SPTEALN5
ONCOR | Alliance - Hicks Switch (106) | LN | 345 | 16/4 | Rosen Heights to Eagle Mountain Compressor 138 kV, Eagle Mountain Ses Auto MR1 345/138 kV, DCKT Eagle Mountain Ses to Saginaw Sw 138 kV | Rosen Heights Tap 2 - Morris Dido 138 kV, Eagle Mountain Ses Auto AX2 345/138 kV, Eagle Mountain Ses - Morris Dido 138 kV | RT, ST | Planned | Y | [5 empty] | HCKSW | ALLNC | 106_A | SALLHCK5
ONCOR | Austrop - Sandow Switch (440) | LN | 345 | 2017 | DCKT Sandow Sw to Bell County East Sw | Taylor - Taylor West 138 kV | ADD | [7 empty] | SNDSW | AUSTRO | 440 | SSNDAU15
ONCOR | Austrop - Sandow Switch (450) | LN | 345 | 2017 | DCKT Sandow Sw to Bell County East Sw | Taylor - Taylor West 138 kV | ADD | [7 empty] | SNDSW | AUSTRO | 450 | SSNDAU35
ONCOR | Bell County East Switch - Sandow Switch (421) | LN | 345 | 17/2, 17/4 | DCKT Sandow Sw to Austrop 345 kV | Hutto Sw - Taylor West 138 kV | RT, ST | Planned, Forced | [6 empty] | SNDSW | BCESW | 421 | SBCESN35
ONCOR | Bell County East Switch - Sandow Switch (431) | LN | 345 | 17/2 | DCKT Sandow Sw to Austrop 345 kV | Hutto Sw - Taylor West 138 kV | RT | Forced | [6 empty] | SNDSW | BCESW | 431 | SBCESND5
ONCOR | Benbrook Switch- Sycamore Creek | LN | 345 | 17/2, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV | RT | Forced | [6 empty] | BNBSW | SYCRK | 6000_A | SSYCEV25
ONCOR | Brownwood - … - Brownwood Switch | LN | 138 | 17/2, 17/3, 17/4, 17/5 | Mercers Gap Sw to Comanche Sw (Oncor) 138 kV | Holder Auto FMR1 138/69 kV, Holder Auto FMR1 138/69 kV | RT, ST | Planned | [6 empty] | BRNSO | BRNWD | 670_A | SBRNCMP8
ONCOR | Brownwood Switch - Goldthwaite | LN | 138 | 18/09 | Ferguson - Sherwood Shores 138 kV | Cedar Valley - Trimmier 138 kV | RT | Planned | [6 empty] | BRNSW | GOLDTH | 680 | SGOLBRN8
ONCOR | Calmont Switch- … - Eagle Mountain Ses & White Settlement Switch (6185) | LN | 138 | 17/4, 18/2, 19/4 | DCKT Eagle Mountain to Saginaw Sw 138 Kv, DCKT Hicks Switch - Saginaw Switch 138 kV | Eagle Mountain Ses - Morris Dido 138 kV (6265), Eagle Mountain Compressor Station - Eagle Mountain Poi 138 kV | RT | Planned | [6 empty] | CMTSW | WSTHL | 6185_A | SMRSEMS8
ONCOR | Calmont Switch- … - Eagle Mountain Ses (6190_A) | LN | 138 | 15/6, 15/7, 17/4 | DCKT Eagle Mountain SES to Parker Sw & Hicks Sw 345 kV, DCKT Eagle Mountain SES to Parker Sw & Hicks Sw 345 kv, DCKT Eagle Mountain to Saginaw Sw 138 kV | Calmont Sw - … - Eagle Mountain Ses (6185), Calmont Sw - … - Eagle Mountain Ses (6190), Eagle Mountain Ses - Morris Dido 138 kV (6265) | RT | Planned, Forced | [6 empty] | CMTSW | WSTHL | 6190_A | SWSTWSM8
ONCOR | Carrollton East - ... - Preston North | LN | 138 | 19/4 | Argyl - … - Lewisville Switch 138 kV | Argyle - Highlands Tap 138 kV | RT | Planned | [6 empty] | CRLES | PRSTN | 1500_J | SMDWREN8
ONCOR | Carrollton Northwest - … - Plano Tennyson (840_A) | LN | 138 | 16/1, 16/6 | Lewisville Sw Auto FMR2 345/138kV | Fort Worth Sub - West Denton 138 kV | RT | Planned | [6 empty] | CRLNW | CRLFR | 840_A | SSPRCR28
ONCOR | Carrollton Northwest - Lakepointe Tnp | LN | 138 | 19/1, 19/2 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Arco - Cooper Creek Substation 138 kV | RT | Planned, Forced | [6 empty] | CRLNW | LKPNT | 591 | SLKPCRL8
ONCOR | Carrollton Northwest - Plano Tennyson | LN | 345 | 18/12 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Arco - Cooper Creek Substation 138 kV | RT | Planned | [6 empty] | CRLNW | PTENN | 81 | SPTECRL5
ONCOR | Cedar Crest Switch - … - Industrial Blvd | LN | 138 | 18/5, 19/3 | DCKT Westmoreland - Cedar Hill Switch 138 kV & Mountain Creek Ses - Fish Creek Switch 69 kV, DCKT Carrollton Northwest - Lewisville Switch 345 kV, Lewisville Switch - Jonesville Tnp 138 kV | Saint Augustine Tap 2 - Sargent Road 138 kV, Carrollton Northwest - Lakepointe Tnp 138kV, Ti Tnp - West Tnp 138 kV | RT | Planned | [6 empty] | CMPST | CDCSW | 3130_A | SCMPIND8
ONCOR | Cedar Crest Switch- … - Sargent Road 138 kV | LN | 138 | 16/9 | Mountain Creek Ses Unit Unit8 | Industrial Blvd - Compton Street 138 kV | RT | Planned, Forced | [6 empty] | CDCSW | SATP2 | 3140_A | SLKJSAR8
ONCOR | Cedar Crest Switch- … - Wall Street | LN | 69 | 18/5 | DCKT Westmoreland - Cedar Hill Switch 138 kV & Mountain Creek Ses - Fish Creek Switch 69 kV | Saint Augustine Tap 2 - Sargent Road 138 kV | RT | Planned | [6 empty] | CDCSW | CMPST | 3890_A | SWALCDC9
ONCOR | Cedar Crest Switch- … - West Levee Switch | LN | 138 | 18/5 | DCKT Westmoreland - Cedar Hill Switch 138 kV & Mountain Creek Ses - Fish Creek Switch 69 kV | Saint Augustine Tap 2 - Sargent Road 138 kV | RT | Planned, Forced | [6 empty] | CDCSW | DEALY | 3120_A | SDEAWLV8
ONCOR | Cedar Hill Switch- Courtland | LN | 345 | 18/9 | DCKT Navarro - Watermill Switch 345 kV | Britten Road - Venus Switch 345 kV | RT | Planned | [6 empty] | CRTLD | CDHSW | 6020_A | SCRTCDH5
ONCOR | Cedar Hill Switch- Mountain Creek Ses (3200) | LN | 138 | 15/9, 16/10, 16/11, 16/9 | Polk Street to Oak Cliff South 138 KV, Mountain Creek Ses Auto MR1 138/69 kV, DCKT Mountain Creek Ses to Cedar Crest Sw 138 kV, West Levee Sw Auto MR1 345/138 kV, Spur - … - Salt Creek Bepc, Polk Street to Oak Cliff South 138 kV | Cedar Crest Sw - Oak Cliff South 138 kV, Industrial Blvd - Compton Street 138 kV, Cedar Crest Sw - Oak Cliff South 138 kV | RT, ST | Planned, Forced | [6 empty] | CDHSW | MCSES | 3200 | SMCSCDH8
ONCOR | Cedar Hill Switch- Mountain Creek Ses (3210) | LN | 138 | 15/9, 16/10, 16/11, 16/9 | Polk Street to Oak Cliff South 138 KV, Mountain Creek Ses Auto MR1 138/69 kV, DCKT Mountain Creek Ses to Cedar Crest Sw 138 kV, West Levee Sw Auto MR1 345/138 kV, Polk Street to Oak Cliff South 138 kV | Cedar Crest Sw - Oak Cliff South 138 kV, Industrial Blvd - Compton Street 138 kV, Cedar Crest Sw - Oak Cliff South 138 kV | RT, ST | Planned, Forced | [6 empty] | CDHSW | MCSES | 3210_A | SWMRCDH8
ONCOR | Centerville Road Switch- … - Judd Court & Kirkland Park | LN | 138 | 19/3 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Lakepointe Tnp - Jones Street Tnp 138 kV | RT | Planned | [6 empty] | CNRSW | GRLRD | 3250_A | SLKHCNR8
ONCOR | Centerville Road Switch- Forney Switch | LN | 345 | 2017 | Forney - Royse DCKT | Forney 345/138 auto | ADD | [7 empty] | CNRSW | FORSW | 110 | SCNRFOR5
ONCOR | Comanche Peak Ses - Comanche Switch | LN | 345 | 18/11 | DCKT Brown Switch - Killen Switch 345 kV | Comanche Tap - Comanche Switch 138 kV | RT | Forced | [6 empty] | CMNSW | CPSES | 662 | SCMNCPS5
ONCOR | Comanche Peak Ses - Everman Switch | LN | 345 | 2017 | Comanch Peak Ses to Mitchell Bend 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD | [7 empty] | CPSES | EVRSW | 6063 | SCPSEVR5
ONCOR | Comanche Peak Ses - Johnson Switch (Oncor) | LN | 345 | 17/5, 17/9, 18/4 | Comanche Peak Ses to Mitchell Bend Sw 345 kV | Wolf Hollow 345 Sw - Comanche Peak Ses 345 kV | RT | Planned | [6 empty] | JONSW | CPSES | 140 | SJONCPS5
ONCOR | Comanche Peak Ses - Parker Switch (6016) | LN | 345 | 2017 | Comanch Peak Ses to Johnson Sw & Everman Sw 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD | [7 empty] | CPSES | PKRSW | 6016 | SCPSPKR5
ONCOR | Comanche Peak Ses - Parker Switch (6062) | LN | 345 | 2017 | Comanch Peak Ses to Johnson Sw & Everman Sw 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD | [7 empty] | CPSES | PKRSW | 6062 | SPKREVR5
ONCOR | Courtland - Everman Switch | LN | 345 | 18/5 | DCKT Navarro - Watermill Switch 345 kV | Britten Road - Venus Switch 345 kV | RT | Planned, Forced | [6 empty] | EVRSW | CRTLD | 6020_D | SCRTEVR5
ONCOR | Culberson Switch - … - Horseshoe Spring Switch & Riverton Switch (6140) | LN | 138 | 18/12, 19/4 | Moss Switch - Odessa Ehv Switch 345 kV, Fort Stockton Plant - Solstice 138 kV | Rio Pecos - Woodward 2 138 kV, Barilla - Fort Stockton Switch 69 kV | RT | Planned, Forced | [6 empty] | CULSW | CHILL | 6140_E | SRVRCUL8
ONCOR | Culberson Switch - … - Yucca Drive Switch | LN | 138 | 18/5 | Moss Switch - Yucca Drive Switch 138 kV, North McCamey - Odessa Ehv Switch 345 kV, Odessa Ehv Switch - … - Wolf Switching Station 138 kV | General Tire Switch - Southwestern Portland Tnp 138 kV, Pigcreek - Solstice 138 kV, General Tire Switch - Southwestern Portland Tnp 138 kV | RT | Planned | [6 empty] | CULSW | MVRCK | 6575_D | SCULCDP8
ONCOR | Decordova Ses - Everman Switch | LN | 345 | 19/3 | DCKT Comanche Peak Ses - Everman Switch & Johnson Switch 345 kV | Decordova Dam - Hood 13 8 kV | RT | Forced | [6 empty] | EVRSW | DCSES | 161 | SDCSEVR5
ONCOR | Denton Drive - … - Empire Central & Norwood Switch | LN | 138 | 18/5 | DCKT Carrollton Northwest - Lewisville Switch 345 kV, DCKT Navarro - Watermill Switch 345 kV | Jones Street Tnp - Lewisville Switch 138 kV, Carrollton Northwest - Lakepointe Tnp 138kV, Britten Road - Venus Switch 345 kV | RT | Planned, Forced | [6 empty] | DENDR | ECTP1 | 3360_A | SEMPNO28
ONCOR | Eagle Mountain Ses - … - Saginaw Switch (6265) | LN | 138 | 19/4 | DCKT Hicks Switch - Saginaw Switch 138 kV | Eagle Mountain Compressor Station - Eagle Mountain Poi 138 kV | RT | Planned | [6 empty] | EMSES | MRSDO | 6265_A | SRSNEM38
ONCOR | East Levee Switch - … - Industrial Blvd | LN | 138 | 15/5, 15/6 | DCKT West Levee Sw to 800/900 Network 138 kV | East Levee Sw - Reagan Street 138 kV (3410_A) | RT | Planned | [6 empty] | ELVSW | WNTWK | 3570_A | SWNTEL28
ONCOR | East Levee Switch - West Levee Switch | LN | 138 | 18/5 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Jones Street Tnp - Lewisville Switch 138 kV, Carrollton Northwest - Lakepointe Tnp 138kV | RT | Planned | [6 empty] | WLVEE | ELVSW | 4090 | SELVWL28
ONCOR | Elkton - … - Forney Switch | LN | 345 | 2017, 17/11, 18/11, 18/12 | Trinidad - Enterprise and - Stryker DCKT, DCKT Martin Lake Ses - Stryker Creek Ses & Mt Enterprise 345 kV | Elkton 345/138 kV auto, Lufkin Switch - Nacogdoches South Tap 138 kV | ADD, RT | Planned | [6 empty] | ELKTN | TRCNR | 170 | SELKFOR5
ONCOR | Elkton - Martin Lake Ses | LN | 345 | 2017 | Martin Lake - Styker and - Enterprise DCKT | Martin Lake - Shamburger | ADD | [7 empty] | ELKTN | MLSES | 180 | SELKMLS5
ONCOR | Euless - … - Hackberry (745) | LN | 138 | 16/12, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Lewisville Sw - Jones Street Tnp 138 kV | RT | Planned | [6 empty] | EULES | GRHWY | 745_H | SCPLHKB8
ONCOR | Euless - … - McKamy Road & Roanoke Switch (1065) | LN | 138 | 16/10, 16/12, 17/1, 17/2, 17/3, 17/4, 17/5, 17/10 | DCKT Carrollton Northwest to Lewisville Sw 345 kV, DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV, DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Blue Mound - Wagley Robertson 138 kV, Lewisville Sw - Jones Street Tnp 138 kV, Tyler Northwest - Shamburger Sw 138 kV | RT, ST | Planned | [6 empty] | EULES | GRHWY | 1065_L | SKIMRN48
ONCOR | Executive Parkway - … - Handley Ses | LN | 138 | 18/5 | DCKT Eagle Mountain Ses - Saginaw Switch 138 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned, Forced | [6 empty] | BRHT2 | EXPKY | 6435_B | SWHIHL38
ONCOR | Forney Switch - Royse Switch (200) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney 345/138 kV Auto MR3 | ADD | [7 empty] | FORSW | RYSSW | 200 | SFORRYS5
ONCOR | Forney Switch - Royse Switch (210) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney 345/138 kV Auto MR3 | ADD | [7 empty] | FORSW | RYSSW | 210 | SFORRY25
ONCOR | Forney Switch - Seagoville Switch | LN | 345 | 19/4 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Carrollton Northwest - Lakepointe Tnp 138kV | RT | Planned | [6 empty] | FORSW | SGVSW | 220_A | SSGVFOR5
ONCOR | Forney West - … - Royse Switch | LN | 138 | 18/5 | Farmersville Switch - Royse Switch (381) | Farmersville Switch - Royse Switch (400) | RT | Planned | [6 empty] | FORWE | RYSSW | 1090_E | SRWARY28
ONCOR | Gresham Road Switch - … - Nacogdoches Se | LN | 138 | 17/12, 18/7, 18/8, 18/10, 18/12, 19/1 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV, DCKT Mt Enterprise - Trinidad Ses & Martin Lake Ses - Stryker Creek Ses | Herty North Switch - Nacogdoches Se 138 kV, Lufkin Switch - Nacogdoches South Tap 138 kV | RT | Planned | [6 empty] | CSHNG | GRDSW | 1450_F | SNCDCMI8
ONCOR | Gresham Road Switch - Stryker Creek Ses | LN | 138 | 18/6 | DCKT Mt Enterprise - Trinidad Ses & Martin Lake Ses - Stryker Creek Ses | Herty North Switch - Nacogdoches Se 138 kV | RT | Planned | [6 empty] | SCSES | GRDSW | 11010 | SGRDSCS8
ONCOR | Hackberry - … - Irving Beltine Road & Ligget Switch | LN | 138 | 19/4 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Carrollton Northwest - Lakepointe Tnp 138kV | RT | Planned | [6 empty] | HKBRY | DFWBE | 1150_A | SIRVLIG8
ONCOR | Hackberry - … - Liggett Switch | LN | 138 | 19/4 | DCKT Carrollton Northwest - Lewisville Switch 345 kV, Argyle - … - Lewisville Switch 138 kV | Carrollton Northwest - Lakepointe Tnp 138kV, Argyle - Highlands Tap 138 kV | RT | Planned | [6 empty] | HKBRY | DFWBE | 1140_E | SDFWLI18
ONCOR | Hackberry - … - Norwood Switch (100) | LN | 345 | 16/3, 16/7, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Lewisville Sw - Jones Street Tnp 138 kV | RT | Planned | [6 empty] | HKBRY | VLYRN | 100_A | SNORVLY5
ONCOR | Herty North Switch - Nacogdoches Se | LN | 138 | 18/12 | DCKT Mt Enterprise - Trinidad Ses & Martin Lake Ses - Stryker Creek Ses | Lufkin Switch - Nacogdoches South Tap 138 kV | RT | Planned | [6 empty] | HNRSW | NCDSE | 1170 | SHNRNCD8
ONCOR | Hicks Switch - … - Saginaw Switch (6270) | LN | 138 | 16/2, 16/3, 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV, Rosen Heights to Eagle Mountain Compressor 138 kV | Eagle Mountain Ses - Morris Dido 138 kV, Rosen Heights Tap 2 - Morris Dido 138 kV | RT, ST | Planned, Forced | [6 empty] | HCKSW | WGROB | 6270_D | SBLMHCK8
ONCOR | Hicks Switch - … - Saginaw Switch (6271) | LN | 138 | 16/2, 16/3, 16/12, 17/1, 16/1, 16/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV, Rosen Heights to Eagle Mountain Compressor 138 kV, Rosen Heights to Eagle Mountain Compressor, DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Eagle Mountain Ses - Morris Dido 138 kV, Rosen Heights Tap 2 - Morris Dido 138 kV, Eagle Mountain Ses - Morris Dido 138 kV | RT, ST | Planned, Forced | [6 empty] | HCKSW | WGROB | 6271_A | SFSCHC28
ONCOR | Hicks Switch - Roanoke Switch | LN | 345 | 16/4 | Rosen Heights to Eagle Mountain Compressor 138 kV, Eagle Mountain Ses Auto MR1 345/138 kV, DCKT Eagle Mountain Ses to Saginaw Sw 138 kV, Rosen Heights to Rosen Heights Tap 2 | Rosen Heights Tap 2 - Morris Dido 138 kV, Eagle Mountain Ses Auto AX2 345/138 kV, Eagle Mountain Ses - Morris Dido 138 kV | RT, ST | Planned | Y | [5 empty] | RNKSW | HCKSW | 107 | SHCKRNK5
ONCOR | Holt Switch - … - Yucca Drive Switch | LN | 138 | 18/4 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV, Pig Creek - Solstice 138 kV | RT | Planned | [6 empty] | HLTSW | YUCSW | 6425_A | SGSMPB28
ONCOR | Hutto Switch - … - Taylor (Oncor) | LN | 138 | 18/12 | Killeen Switch TRX KLNSW_3_2 345/138 | Killen Switch TRX MR1H 345/138 kV | RT | Planned | [6 empty] | HUTTO | TLRWT | 1665_A | STRLHUT8
ONCOR | Irving Norwood - Norwood Switch | LN | 138 | 18/9 | DCKT Hicks Switch - Alliance & Roanoke Switch 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned | [6 empty] | NORSW | IRVND | NORSW_IRVND | SIRVNO28
ONCOR | Jewett - Singleton (260_A) | LN | 345 | 2018 | DCKT Gibbons Creek to Singleton 345 kV | Jewett - Singleton 345 kV (240) | ADD | Planned | [6 empty] | JEWET | SNG | 260_A | SSNGJE25
ONCOR | Killeen Switch - Salado Switch (271) | LN | 345 | 18/12 | Killeen Switch TRX KLNSW_3_2 345/138 | Killen Switch TRX MR1H 345/138 kV | RT | Planned | [6 empty] | KLNSW | SALSW | 271 | SKLNSA25
ONCOR | Killeen Switch - Salado Switch (272) | LN | 345 | 18/12 | Killeen Switch TRX KLNSW_3_2 345/138 | Killen Switch TRX MR1H 345/138 kV | RT | Planned | [6 empty] | KLNSW | SALSW | 272 | SKLNSAL5
ONCOR | Lake Creek Ses Bus #1 (CB 2840, etc.) | BUS | 138 | 15/9 | Waco Mm Mars 2 to Robinson 138 KV, Valley South to Anna Sw & Farmersville Sw 345 kV | Elm Mott - Northcrest Tap 138 kV, Pink Hills Pod - Payne Sw 138 kV | RT, ST | Planned | [6 empty] | LCSES |  | 4BB1 | N/A
ONCOR | Lewisville Switch - Roanoke Switch | LN | 345 | 19/3, 19/4 | DCKT Carrollton Northwest - Lewisville Switch 345 kV, Argyle - … - Lewisville Switch 138 kV | Ti Tnp - West Tnp 138 kV, Argyle - Highlands Tap 138 kV | RT | Planned, Forced | [6 empty] | LWSSW | RNKSW | 105_B | SLWSRNK5
ONCOR | Lindley Ranch Pecos Express - … - Riverton Switch | LN | 138 | 18/5 | Clearfork - Telephone Road 345 kV, Moss Switch - Yucca Drive Switch 138 kV, Odessa Ehv Switch - … - Wolf Switching Station 138 kV | Pigcreek - Solstice 138 kV, Amoco Three Bar Tap - Andrews County South 138 kV, Cheyenne Tap - No Trees Switch 138 kV, General Tire Switch - Southwestern Portland Tnp 138 kV | RT | Planned, Forced | [6 empty] | LDYPD | RVRSW | 6142_G | SRVRLDY8
ONCOR | Lufkin Switch - … - Nacogdoches Se | LN | 138 | 17/12 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV | Herty North Sw - Nacogdoches Se 138 kV | RT | Planned | [6 empty] | LFKSW | NCSTP | 1350_E | SNCDNCD8
ONCOR | Martin Lake Ses - Mt Enterprise | LN | 345 | 2017 | Martin Lake - Elktion and Tyler Grande DCKT | Martin Lake - Shamburger | ADD | [7 empty] | MLSES | ENTPR | 360 | SENTMLS5
ONCOR | Martin Lake Ses - Styker Creek Ses | LN | 345 | 2017 | DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD | [7 empty] | MLSES | SCSES | 370 | SMLSSCS5
ONCOR | Martin Lake Ses - Tyler Grande | LN | 345 | 2017 | DCKT Martin Lake Ses to Styker Creek Ses & Mt Enterprise 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD | [7 empty] | MLSES | TYGND | 340 | STYGMLS5
ONCOR | Midland County Northwest Switch -… - Moss Switch | LN | 138 | 19/4 | DCKT Odessa - Midessa South Sw & Odessa Ehv Switch 138 kV | Big Three Odessa Tap - Odessa Ehv Switch 138 kV | RT | Planned, Forced | [6 empty] | MCNSW | HISKY | 6463_A | SMOSMCN8
ONCOR | Monticello Ses - Paris Switch | LN | 345 | 2017 | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Paris Sw 345/138 kV Auto MR1 | ADD | [7 empty] | PRSSW | MNSES | 390 | SMNSPRS5
ONCOR | Morrison Lane Switch - … - Northaven Switch | LN | 138 | 19/3 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Lakepointe Tnp - Jones Street Tnp 138 kV | RT | Planned | [6 empty] | MSLSW | MSHLN | 3850_A | SMSHNH28
ONCOR | Moss Switch - … - Wolf Switching Station | LN | 138 | 18/5 | Clearfork - Telephone Road 345 kV, Moss Switch - Yucca Drive Switch 138 kV | General Tire Switch - Southwestern Portland Tnp 138 kV, Amoco Three Bar Tap - Andrews County South 138 kV | RT | Planned, Forced | [6 empty] | MOSSW | WLFSW | 6480_A | SWLFECT8
ONCOR | Moss Switch - Odessa Ehv Switch | LN | 345 | 19/4 | DCKT Odessa - Midessa South Sw & Odessa Ehv Switch 138 kV | Big Three Odessa Tap - Odessa Ehv Switch 138 kV | RT | Planned, Forced | [6 empty] | MOSSW | ODEHV | 34600 | SMDLODE5
ONCOR | Moss Switch - Yukon Switch | LN | 138 | 17/9 | Yucca Drive Sw to Wolf Switching Station 138 kV | Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned | [6 empty] | MOSSW | YKNSW | 14075 | SECNMO28
ONCOR | Mt Enterprise - Trinidad Ses | LN | 345 | 2017 | DCKT Elkton to Forney & Tyler Grande to Tri Corner 345 kV | Elkton 345/138 kV Auto MR3 | ADD | [7 empty] | ENTPR | TRSES | 361 | SENTTR25
ONCOR | Northaven Switch - … - Renner Switch | LN | 138 | 19/3 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Lakepointe Tnp - Jones Street Tnp 138 kV | RT | Planned | [6 empty] | NHNSW | ALPHA | 3700_B | SBNDKRK8
ONCOR | Odessa Ehv Switch TRX MR1 345/138 kV | XF | 345 | 18/11 | Moss Switch - Odessa Ehv Switch 345 kV | 16th Street Tnp - Woodward 2 138 kV, Odessa Ehv Switch TRX MR2H 345/138 kV | RT | Planned, Forced | [6 empty] | ODEHV |  | ODEHV MR1 345/138 KV XFMR | XOD2E58
ONCOR | Paris Switch CB_8635 | CB | 345 | 2017 | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Paris Sw 345/138 kV Auto MR1 | ADD | [7 empty] | PRSSW |  | 8635 | N/A
ONCOR | Parkdale Switch - … - Prairie Creek Switch | LN | 138 | 18/11 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Arco - Cooper Creek Substation 138 kV | RT | Planned | [6 empty] | PRCRK | PDSES | 3655_A | SPRCPDS8
ONCOR | Riverton Switch - Three Mile Draw Switch | LN | 138 | 18/5 | Clearfork - Telephone Road 345 kV, Moss Switch - Yucca Drive Switch 138 kV | Pigcreek - Solstice 138 kV, Amoco Three Bar Tap - Andrews County South 138 kV, Cheyenne Tap - No Trees Switch 138 kV | RT | Planned, Forced | [6 empty] | RVRSW | TMDSW | 6143 | SRVRTMD8
ONCOR | Royse Switch Auto #1 | XF | 345 | 15/9 | Royse Sw Auto FMR3 345/138 KV | Forney Sw - Forney West 138 kV | RT | Planned | [6 empty] | RYSSW |  | FMR1 | SFORRYS5
ONCOR | Saginaw Switch - … - Springdale | LN | 138 | 18/6, 18/9, 19/4 | DCKT Eagle Mountain Ses - Saginaw Switch 138 kV, DCKT Hicks Switch - Alliance & Roanoke Switch 345 kV | Blue Mound - Wagley Robertson 138 kV, Eagle Mountain Compressor Station - Eagle Mountain Poi 138 kV | RT | Planned | [6 empty] | AMFTP | SAGNA | 6495_C | SSAGAMF8
ONCOR | Sargent Road - West Levee Switch 345 kV | LN | 345 | 16/9, 18/11, 18/12 | Mountain Creek Ses Unit Unit8, DCKT Carrollton Northwest - Lewisville Switch 345 kV | Industrial Blvd - Compton Street 138 kV, Arco - Cooper Creek Substation 138 kV | RT | Planned | [6 empty] | SARRD | WLVEE | 217 | SSARWLV5
ONCOR | Sargent Road 345 kV Bus North (CB 7770, etc.) | BUS | 345 | 18/12 | DCKT Venus Switch - Everman Switch 345 kV | Everman Switch 345/138 kV Auto MR2h | RT | Planned | [6 empty] | SAARD |  | BB1N | N/A
ONCOR | Sargent Road 345 kV Bus South (CB 7780, etc.) | BUS | 345 | 18/12 | DCKT Venus Switch - Everman Switch 345 kV | Everman Switch 345/138 kV Auto MR2h | RT | Planned | [6 empty] | SAARD |  | BB1S | N/A
ONCOR | Stryker Creek Ses - Trinidad Ses | LN | 345 | 2017 | DCKT Elkton to Forney & Tyler Grande to Tri Corner 345 kV | Elkton 345/138 kV Auto MR3 | ADD | [7 empty] | SCSES | TRSES | 480 | STRSSCS5
ONCOR | Tri Corner - Tyler Grande | LN | 345 | 2017 | DCKT Trinidad Ses to Stryker Creek Ses & Mt Enterprise 345 kV | Elkton 345/138 kV Auto MR3 | ADD | [7 empty] | TRCNR | TYGND | 341 | STYGTRC5
ONCOR | Tri Corner - Watermill Switch | LN | 345 | 18/9 | DCKT Navarro - Watermill Switch 345 kV | Britten Road - Venus Switch 345 kV | RT | Planned | [6 empty] | TRCNR | WTRML | 215 | STRCWTR5
ONCOR | Ward Gulf Tap - Wolf Switching Station | LN | 138 | 18/4 | Yucca Drive Sw to Wink Sub 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV, Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned | [6 empty] | WLFSW | WGLFT | 6545_I | SHSAPB38
ONCOR | Wink Sub - Yucca Drive Switch | LN | 138 | 18/3 | Chevron Has to Wickett & Wink Sub & Wolf Switching Station 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV | RT | Planned | [6 empty] | WINKS | YUCSW | 6571 | SWINYUC8
ONCOR | Wink Sub Auto Fmr1 138/69 kV | XF | 138 | 17/6 | Wink Sub to Wink Tnp 138 kV | Wink Sub Auto MR2L 138/69 kV | RT | Planned | [6 empty] | WINKS |  | FMR1 | XWIN389
SHARYLAND Oncor | Alibates - Aj Swope Sharyland Utilities (AJSWOP_ALIBA) | LN | 345 | 17/4 | Panhandle GTC | N/A | ST | Planned | [6 empty] | ALIBATES | AJ_SWOPE | AJSWOP_ALIBA | SWINALI5
SHARYLAND Oncor | Alibates - Aj Swope Sharyland Utilities (AJSWOP_ALIBA2) | LN | 345 | 17/4 | Panhandle GTC | N/A | ST | Planned | [6 empty] | ALIBATES | AJ_SWOPE | AJSWOP_ALIBA2 | SALIAJ_5
SHARYLAND Oncor | Alibates - Grandview Wind Farm | LN | 345 | 15/5 | Isolates Generation | N/A | ST | Planned | [6 empty] | GRANDVW1 | ALIBATES | GV1_LINE | SGRAALI5
SHARYLAND Oncor | Alibates - Tule Canyon (ALIB_TULE_2) | LN | 345 | 17/1 | Panhandle GTC | N/A | RT | Forced | [6 empty] | ALIBATES | TULECNYN | ALIB_TULE_2 | SALITU25
SHARYLAND Oncor | Bulldog Su - Elbow | LN | 138 | 16/9 | Moss Sw to Odessa Ehv Sw 345 kV | Trigas Odessa Tap - Odessa Ehv Sw | ST | Planned | Y | [5 empty] | ELBOW | BULLDOG | ELBOW_BULLDOG | SELBBUL8
SHARYLAND Oncor | Tule Canyon - White River (TULEC_WHIT_R1) | LN | 345 | 15/11 | Panhandle GTC | N/A | ST | Planned | Y | [5 empty] | TULECNYN | WHIT_RVR | TULEC_WHIT_R1 | SW_CTUL5
SHARYLAND Oncor | Tule Canyon - White River (TULEC_WHIT_R2) | LN | 345 | 15/11 | Panhandle GTC | N/A | ST | Planned | Y | [5 empty] | TULECNYN | WHIT_RVR | TULEC_WHIT_R2 | SW_CTU35
SHARYLAND Oncor | Tule Canyon Bus #1 (CB TCN7100, etc.) | BUS | 345 | 15/6 | Panhandle GTC | N/A | ST | Planned | [6 empty] | TULECNYN |  | BUS1_NORTH | N/A
SHARYLAND Oncor | Tule Canyon Bus #2 (CB TCN7102, etc.) | BUS | 345 | 15/6 | Panhandle GTC | N/A | ST | Planned | [6 empty] | TULECNYN |  | BUS2_SOUTH | N/A
SHARYLAND Oncor | White River - Wett_Cottonwood (WHIT_RV_W_CW1) | LN | 345 | 15/12 | Panhandle GTC | N/A | RT | Planned | [6 empty] | WHIT_RVR | W_CW_345 | WHIT_RV_W_CW1 | SWHIW_15
SHARYLAND Oncor | White River - Wett_Cottonwood (WHIT_RV_W_CW2) | LN | 345 | 15/12 | Panhandle GTC | N/A | RT | Planned | [6 empty] | WHIT_RVR | W_CW_345 | WHIT_RV_W_CW2 | SWHIW_25
SHARYLAND Oncor | Windmill Entire Station | ST | 345 | 16/8 | Basecase | Resource Isolation | ST | Planned | Y | [5 empty] | WINDMILL |  |  | N/A
STEC | Fowlerton - Tilden 138 Sub | LN | 138 | 18/1 | San Miguel Auto 345_138 kV Switchyards Trx Sanmgl8_3_2 345/138 kV | San Miguel Gen Auto ATBH 345/138 kV | RT | Forced | [6 empty] | FOWLRTON | TILDEN | FWLRTN_TILDEN | SFOWTIL8
STEC | Oaks Sub - Poteet Sub | LN | 69 | 17/12, 18/1 | DCKT Castrvll to Razorbac & Txresrch 138kV | Hondo Creek Switching Station - Moore Switching Station 138 Kv | RT | Planned | [6 empty] | POTEETS | OAKS9 | POT_OAKS | SPOTOAK9
STEC | Sam Rayburn Switch - Vanderbilt Switch | LN | 138 | 15/10 | Loop 463 to Sam Rayburn 138 kV | Sam Rayurn Swithcing Station Auto 69_2 138/69 kV | ST | Planned | [6 empty] | RAYBURN | VANBLTSS | RAY_VANB | SVANRAY8
STEC | San Miguel Auto ATA | XF | 345 | 15/3, 16/2 | DCKT Lon Hill to North Edinburg 345 kV & Orange Grove Sw 138 kV, Pawnee Sw to San Miguel 345 kV | Fannin Sub - Victoria 69 kV, San Miguel Auto ATB 345/138 kV | ST | Planned | Y | [5 empty] | SANMIGL |  | ATAH | XSAN58
STEC | San Miguel Auto ATB | XF | 345 | 15/10 | Lobo Auto AT2 345/138 kV | San Miguel Auto ATA 345/138 kV | ST | Planned | [6 empty] | SANMIGL |  | ATBH | XSA2N58
TNMP | Amoco Oil Cogen - Greenbelt (G138_23) | LN | 138 | 16/2 | Greenbelt to Caddo Sw 138 kV | Greenbelt - Tejas 138 kV | ST | Planned | [6 empty] | GRNBELT | AMOCOOIL | G138_23 | SAMOGR38
TNMP | Amoco Tnp - Grant Avenue Tnp | LN | 69 | 17/10, 17/11 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, Caddo Sw Sta Tnp to Apache Tnp 138 kV | Singleton - Zenith 345 kV, Choctaw Tap Tnp - Choctaw Tnp | RT | Planned, Forced | [6 empty] | GRANTAVE | AMOCOTN | G69_B | SGRAAMO9
TNMP | Choctaw Tnp - … - Terminal Tnp | LN | 69 | 17/11 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned | [6 empty] | CHOCTAW | MARTHNOL | G69_BB2 | SCHOTER9
TNMP | Dickinson Tnp - Freeway Park Tnp | LN | 138 | 15/8 | North Alvin Tnp to Meadow 138 KV | PH Robinson - Southshore TNP 138 kV | RT | Forced | [6 empty] | DICKNSON | FRWYPARK | G138_14 | SDICFR28
TNMP | Freeway Park Tnp - Mainland Tnp | LN | 138 | 17/11 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV | Singleton - Zenith 345 kV | RT | Planned | [6 empty] | MAINLAND | FRWYPARK | 138_FWP_MNL | SFRWMAI8
TNMP | Friendswood Tnp - Seminole Tnp | LN | 138 | 19/4 | Meadow - PH Robinson 345 kV | Alvin Tnp - Mainland Tnp 138 kV | RT | Planned, Forced | [6 empty] | FRDSWOOD | SEMINOLE | G138_10C | SFRDSEM8
TNMP | Gaf - Greenbelt Tnp | LN | 138 | 16/2 | Freeway Park Tnp to Heights Tnp 138 kV | Heights Tnp - Ph Robinson 138 kV | ST | Planned | [6 empty] | GAF | GRNBELT | G138_1B | SGAFGRN8
TNMP | Grant Avenue Tnp - Praxair Tap Tnp | LN | 69 | 17/10 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV | Singleton - Zenith 345 kV | RT | Planned | [6 empty] | TNPRXTAP | GRANTAVE | G69_A2 | STNPTNP9
TNMP | Greenbelt Tnp - Tejas Tnp | LN | 138 | 17/11 | Caddo Sw Sta Tnp to Apache Tnp 138 kV | Choctaw Tap Tnp to Choctaw Tnp | RT | Planned | [6 empty] | GRNBELT | TEJAS | G138_1BB | STEJGR38
TNMP | Ih 20 Tnp Auto Iht1 138/69 kV | XF | 138 | 18/3, 18/4 | Chevron Has to Wickett & Wink Sub & Wolf Switching Station 138 kV, Yucca Drive Sw to Wink Sub 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV, Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned, Forced | [6 empty] | IH20 |  | 1HT1 | XIH289
TNMP | Jones Street Tnp - Lakepointe Tnp | LN | 138 | 17/11, 17/12, 19/3 | DCKT Carrollton Northwest to Lewisville Switch 345 kV | Ti Tnp - West Tnp 138 kV, Carrollton Northwest - Lakepointe Tnp 138kV | RT | Planned | [6 empty] | LWVJS | LKPNT | 590_B | SLWVLKP8
AEP | Coleto - Victoria 1 | LN | 138 |  | Coleto Creek to Pawnee Switching Station 345 KV | Coleto - Victoria 2 |  |  |  | AEP | The addition of the new Euler 138 kV station, Euler – Coleto and Euler – Tuleta 138 kV lines should relieve this congestion at Coleto Creek. The Euler station and both 138 kV lines is scheduled to be completed by the end of August 2019. |  |  | Congestion is limiting Coleto Coal gen output. The limiting MW varied, will get worse when there are high south wind.
AEP | Coleto - Victoria 2 | LN | 138 |  | Coleto Creek to Pawnee Switching Station 345 KV | Coleto - Victoria 1 |  |  |  | AEP | The addition of the new Euler 138 kV station, Euler – Coleto and Euler – Tuleta 138 kV lines should relieve this congestion at Coleto Creek. The Euler station and both 138 kV lines is scheduled to be completed by the end of August 2019. |  |  | Congestion is limiting Coleto Coal gen output. The limiting MW varied, will get worse when there are high south wind.
AEP | Coleto - Rosata | LN | 138 |  | Coleto Creek to Pawnee Switching Station 345 KV | Coleto - Victoria 1 |  |  |  | AEP | The addition of the new Euler 138 kV station, Euler – Coleto and Euler – Tuleta 138 kV lines should relieve this congestion at Coleto Creek. The Euler station and both 138 kV lines is scheduled to be completed by the end of August 2019. |  |  | Congestion is limiting Coleto Coal gen output. The limiting MW varied, will get worse when there are high south wind.

## Form - Request for Addition
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Contingency | Overload | Addition Requestor | Reason for Addition
Oncor | Ennis - Wahaxhachie - Sterret | LN | 138 | ENNIS SWITCH to ENNIS WEST SWITCH LIN _C | ENNIS WEST SWITCH - ENNIS SWITCH 138 kV |  | Any of the outage from Ennis Sw station will cause Ennis Gen have 100% post contingency shift fatcor. The unit output will limit to the rating of the remain line, which is approximately around 234MVA
Oncor | Ennis West -Ennis Switch - Trumbull | LN | 138 | ENNIS SWITCH to ENNIS WEST SWITCH LIN _A | Ennis - Wahaxhachie - Sterret |  | Any of the outage from Ennis Sw station will cause Ennis Gen have 100% post contingency shift fatcor. The unit output will limit to the rating of the remain line, which is approximately around 234MVA
Oncor | Ennis West -Ennis South | LN | 138 | WXHCH-WXOCF_69kV & ENWSW-STERT_138kV | Ennis West -Ennis Switch - Trumbull |  | Any of the outage from Ennis Sw station will cause Ennis Gen have 100% post contingency shift fatcor. The unit output will limit to the rating of the remain line, which is approximately around 234MVA
LCRA | Kendall - BERGHEIM | LN | 345 | ZORN - HAYSEN 345KV | BERGHEIM Auto |  | Entire Hays Genration (1010MW) will be push into Bergheim Auto with 100% shift factor, limiting the gen output to be 370MW, that is the ratinf of the auto.
AEP | Coleto - Victoria 1 | LN | 138 | Coleto Creek to Pawnee Switching Station 345 KV | Coleto - Victoria 2 |  | Congestion is limiting Coleto Coal gen output. The limiting MW varied, will get worse when there are high south wind.
AEP | Coleto - Victoria 2 | LN | 138 | Coleto Creek to Pawnee Switching Station 345 KV | Coleto - Victoria 1 |  | Congestion is limiting Coleto Coal gen output. The limiting MW varied, will get worse when there are high south wind.
AEP | Coleto - Rosata | LN | 138 | Coleto Creek to Pawnee Switching Station 345 KV | Coleto - Victoria 1 |  | Congestion is limiting Coleto Coal gen output. The limiting MW varied, will get worse when there are high south wind.